## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:December 2021
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2021-12-01 |  | 2021-11-01 |  | 2020-12-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 9588 | 2021-12-02 | 10389 | 2021-11-03 | 9098 | 2020-12-05 | 13792 | 2021-04-27
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 20:00
2 | Minimum Generation (MW) | 5167 | 2021-12-17 | 5609 | 2021-11-27 | 4945 | 19/12/20 | - | -
|  |  | 6:00 |  | 6:00 |  | 5:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 9588 | 2021-12-02 | 10389 | 2021-11-03 | 9098 | 2020-12-05 | 13792 | 2021-04-27
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 20:00
4 | Maximum Day Peak Generation (MW) | 8400 | 2021-12-02 | 9044 | 2021-11-01 | 7608 | 2020-12-01 | 11773 | 2021-04-27
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 9588 | 2021-12-02 | 10389 | 2021-11-03 | 9098 | 2020-12-05 | 14097 | 2021-04-27
|  |  | 12:00 |  | 12:00 |  | 19:00 |  | 19:00
6 | Average Generation (MW) at Evening Peak | 9041.1935 |  | 9579.6333 |  | 8691.6 |  | 12676.7 | 2021-04-27
7 | Average Generation (MW) at Day Peak | 7577.4194 |  | 8132.4 |  | 6979.68 |  | 10379.6667 | 2021-04-27
8 | Maximum Power Import from India, BIPTC (MW) | 736 | 2021-12-20 | 747 | 2021-11-09 | 821 | 31/12/2020 | 956 | 27/3/2019
|  |  | 17:30 |  | 3:00 |  | 19:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 112 | 2021-12-11 | 138 | 2021-11-11 | 120 | 03/12/2020 | 194 | 12/06/19
|  |  | 18:00 |  | 11:30 |  | 19:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 04/05/2010
|  |  | - |  | - |  |  |  | 20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 13792 | 2021-04-27
|  | - | - | - | - | - | - |  | 20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 1148.0976 |  | 1073.0634 |  | 2669.46 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 97.7685 |  | 70.8056 |  | 69.63
22 | Net Generation of BPDB (MKWH) | 1050.329 |  | 1002.2577 |  | 2599.84
23 | Net Generation of IPP (MKWH) | 3411.0841 |  | 3794.4574 |  | 1680.44
24 | Net Generation of REB (MKWH) | 126.8797 |  | 137.7806 |  | 124.31
24 | Net Generation of Rental Power Plant (MKWH) | 390.0595 |  | 293.2499 |  | 305.49
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 4978.3523 |  | 5227.7456 |  | 4710.08 |  | 7072.7704 | April'21
26 | Energy Generation by Gas (MKWH) | 3368.8362 |  | 3922.3382 |  | 3403.35 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 189.0553 |  | 176.6325 |  | 102.76 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1014.2984 |  | 802.3956 |  | 857.01 |  | 1679.4648 | Sep-20
29 | Energy Generation by Hydro (MKWH) | 52.2948 |  | 65.2371 |  | 39.36 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 23.3093 |  | 19.3572 |  | 4.67 |  | 22.56 | 2019-09-16
31 | Energy Generation by Coal (MKWH) | 428.3268 |  | 312.5907 |  | 372.56 |  | 627.4399 | April'21
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 450.7438 |  | 537.3749 |  | 430.72 |  | 775.9511 | August-20
33 | Monthly Load Factor (%) | 77.488 |  | 75.5028 |  | 79.54 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:December 2021
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 9588 | 2021-12-02 | 19:00
Generation Period
| Dhaka | MW | 3546
| Chattogram | MW | 1078
| Cumilla | MW | 751
| Mymensingh | MW | 706
| Sylhet | MW | 331
a) | Total supply in East zone | MW | 6412
| Khulna | MW | 1049
| Barisal | MW | 248
| Rajshahi | MW | 873
| Rangpur | MW | 593
b) | Total supply in West zone | MW | 2763
c) | Total supply in both zone ( a+b) | MW | 9175
Ref: | 27.21.0000.603.16.087.20.470 | Date: 19/01/2022
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:December 2021
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 480 | 2021-12-31 | 12:00
| b) Ishurdi end | MW | 336 | 2021-12-18 | 11:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 1280 | 2021-12-01 | 9:00
| b) Ishurdi end | MW | 100 | 2021-12-02 | 8:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 0.775
| b) Ishurdi end | MKWH | 94.52
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 91.69
| b) Ishurdi end | MKWH | 0.75
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 220 | 2021-12-18 | 6:00
| b)Serajganj end | MW | 430 | 2021-12-08 | 15:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 380 | 2021-12-19 | 17:00
| b)Sirajganj end | MW | 120 | 2021-12-28 | 18:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 4.764 | 2021-12-22
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 1.38
| b)Sirajganj end | MKWH | 108.28
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 104.94
| b)Sirajganj end | MKWH | 1.4
30 | Transmission loss of EWI /NO-2 | % | 3.028
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.
Ist East-West Interconnector Loss:
| Ghorasal End (KWH): | 109882206.4 | 1000000 | 109.8822 | 836363.65
| Ishurdi End (KWH): | 106928443.1 | 1000000 | 106.9284 | 811272.74
| Difference (-) : | 2953763.3 |  |  | 25090.91
| Loss : | 2.688% |  |  | 3%
2nd East-West Interconnector Loss:
| Ashuganj End (KWH) | 245578000 | 1000000 | 245.578
| Sirajganj End (KWH) | 242062000 | 1000000 | 242.062
| Difference (-) : | 3516000
| Loss : | 1.432%

## QF-LDC-23
QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: December2021
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Manikganj | 132/33 kV transformer GT-4 | 2021-12-23 13:47 | 2021-12-23 15:05 | 1:18 | T | Due to red-hot maint | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-1 | 2021-12-26 13:54 | 2021-12-26 14:10 | 0:16 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
|  |  | Total : | 1:34 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Rampura | 230/132 kV transformer T-01 | 2021-12-13 15:58 | 2021-12-13 16:32 | 0:34 | T | Tripped showing buchholz relay | 40 | 22.6667 | Power interruption
Madanganj | 132/33 kV transformer T-1 | 2021-12-16 18:03 | 2021-12-16 18:18 | 0:15 | T | Tripped showing main prot. relay. | 0 | 0 | No interruption
Manikganj | 132/33 kV transformer T-4 | 2021-12-19 18:36 | 2021-12-19 19:22 | 0:46 | T | Due to red-hot maint | 0 | 0 | No interruption
Hasnabad | 132/33 kV transformer T-1 | 2021-12-21 17:44 | 2021-12-21 18:31 | 0:47 | T | Due to red-hot maint | 0 | 0 | No interruption
Haripur | 230 kV Bus-1 | 2021-12-22 07:26 | 2021-12-22 09:37 | 2:11 | T | Tripped lockout relay. | 0 | 0 | No interruption
Bhulta | 400/230 kV transformer T-1 | 2021-12-22 07:26 | 2021-12-22 07:57 | 0:31 | T | Tripped showing Diff. relay. | 0 | 0 | No interruption
Keraniganj | 132/33 kV transformers T-1 & T2 | 2021-12-26 00:03 | 2021-12-26 00:26 | 0:23 | T | Tripped showing Dist. Z1 relay | 32 | 12.2667 | Power interruption
Sreenagar | 132/33 kV transformer T-1 | 2021-12-29 15:01 | 2021-12-29 16:04 | 1:03 | T | Due to red-hot maint | 0 | 0 | No interruption
|  |  | Total : | 0:34 |  | Unserved Energy: |  | 34.9333
Chattogram Grid Circle :
Cox,sbazar | 132/33 kV transformer T-3 | 2021-12-24 13:22 | 2021-12-24 17:03 | 3:41 | T | Due to 33 kV feeder fault | 22 | 81.0333 | Power interruption
| 132/33 kV transformer T-3 | 2021-12-28 14:40 | 2021-12-28 15:04 | 0:24 | T | Due to 33 kV feeder fault | 25 | 10 | Power interruption
|  |  | Total : | 4:05 |  | Unserved Energy: |  | 91.0333
Cumilla Grid Circle :
Kachua | 132/33 kV transformer T2 | 2021-12-08 07:56 | 2021-12-08 09:21 | 1:25 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV transformer T2 | 2021-12-21 17:00 | 2021-12-21 17:19 | 0:19 | T | Tripped showing O/C relay | 0 | 0 | No interruption
| 132/33 kV transformer T4 | 2021-12-21 18:23 | 2021-12-21 19:18 | 0:55 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Feni | 132/33 kV transformer T2 | 2021-12-23 11:32 | 2021-12-23 14:09 | 2:37 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Baroierhat | 132/33 kV transformer T1 | 2021-12-28 09:31 | 2021-12-28 10:29 | 0:58 | E/O | Due to red-hot maint | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2021-12-29 10:21 | 2021-12-29 10:21 | 0:00 | T | Tripped showing buchholz relay | 0 | 0 | No interruption
|  |  | Total : | 6:14 |  |  |  | 0
Khulna Grid Circle :
Khulna© | 132/33 kV transformer T-3 | 2021-12-12 05:47 | 2021-12-12 12:59 | 7:12 | E/O | Tripped showing Diff. relay | 0 | 0 | No interruption
| 132/33 kV transformer T3 | 2021-12-14 01:15 | 2021-12-14 13:25 | 12:10 | T | Tripped showing 87T fault | 0 | 0 | No interruption
Baisal(N) | 230/33 kV transformer T01 | 2021-12-14 13:03 | 2021-12-14 13:35 | 0:32 | T | Tripped showing winding temperature high | 0 | 0 | No interruption
Khulna© | 132/33 kV transformer T3 | 2021-12-16 05:08 | 2021-12-16 10:13 | 5:05 | T | Tripped showing Diff.relay at 33 kV side | 0 | 0 | No interruption
Faridpur | 132/33 kV transformers T-1 & T2 | 2021-12-17 17:50 | 2021-12-17 18:05 | 0:15 | E/O | Due to bursting of 11/33 kV transformer | 0 | 0 | No interruption
Gallamari | 132/33 kV transformers T-1 & T2 | 2021-12-19 10:29 | 2021-12-19 10:35 | 0:06 | T | Due to 33 kV feeder fault | 36 | 3.6 | Power interruption
Magura | 132/33 kV transformer T1 | 2021-12-21 04:59 | 2021-12-21 05:21 | 0:22 | T | Tripped showing O/V relay | 0 | 0 | No interruption
Mongla | 132/33 kV transformer T2 | 2021-12-21 03:15 | 2021-12-21 03:46 | 0:31 | T |  | 0 | 0 | No interruption
|  |  | Total : | 26:13 |  | Unserved Energy: |  | 3.6
HVDC Grid Circle :
Banapole | 132/33 kV transformers T-1 & T2 | 2021-12-11 18:20 | 2021-12-11 18:40 | 0:20 | T | Tripped showing O/C & E/F relay at 33 kV side | 38 | 12.6667 | Power interruption
| 132/33 kV transformer T1 | 2021-12-12 07:42 | 2021-12-12 08:16 | 0:34 | E/O | Due to red-hot maint | 10 | 5.6667 | Power interruption
|  |  | Total : | 0:54 |  |  |  | 18.3333
Bogura Grid Circle:
Purbasadipur | 132/33 kV transformer T1 | 2021-12-29 23:30 | 2021-12-29 23:50 | 0:20 | E/O | Due to 33 kV feeder fault | 25 | 8.3333 | Power interruption
Naogaon | 132/33 kV transformers T-1 & T2 | 2021-12-30 02:25 | 2021-12-30 23:50 | 21:25 | E/O |  | 24 | 514 | Power interruption
|  |  | Total : | 21:45 |  |  |  | 522.3333
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 61:19 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: December2021
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kallyanpur | Kallyanpur-Lalbagh 132 kV Ckt-1 | 2021-12-01 08:26 | 2021-12-01 09:25 | 0:59 | T | Tripped showing O/C relay. | 0 | 0 | No interruption
Rajendrapur | Rajendrapur-Kodda 132 kV Ckt-2 | 2021-12-05 11:55 | 2021-12-05 13:50 | 1:55 | T | Tripped showing basbar protection relay. | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 3rd phase 132 kV Ckt | 2021-12-08 15:46 | 2021-12-08 15:54 | 0:08 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Lalbagh | Lalbagh-Kallyanpur 132 kV Ckt-1 | 2021-12-25 08:55 | 2021-12-25 09:16 | 0:21 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-1 | 2021-12-25 13:29 | 2021-12-25 14:02 | 0:33 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
| Tongi-Uttra 3rd phase 132 kV Ckt | 2021-12-30 20:27 | 2021-12-30 20:50 | 0:23 | T | Tripped showing Diff. relay | 0 | 0 | Power interruption
|  |  | Total : | 3:20 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Haripur | Haripur-Haripur 230 KV Ckt-1 & 2 | 2021-12-22 07:27 | 2021-12-22 17:47 | 8:02 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
| Haripur-Bhulta 230 KV Ckt-1 & 2 | 2021-12-22 07:27 | 2021-12-22 07:57 | 0:30 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Siddhirganj S/S | Siddhirganj S/S-Siddhirganj peaking 132 kV Ckt | 2021-12-22 08:13 | 2021-12-22 08:36 | 0:23 | T | Tripped showing line overload | 0 | 0 | No interruption
| Siddhirganj S/S-Matuail 132 kV Ckt | 2021-12-22 08:13 | 2021-12-22 08:32 | 0:19 | T | Tripped showing O/C relay. | 0 | 0 | No interruption
Hasnabad | Hasnabad-Sitalakhya 132 kV Ckt | 2021-12-23 14:10 | 2021-12-23 15:31 | 1:21 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Haripur | Haripur-Ullon 132 kV Ckt | 2021-12-29 09:00 | 2021-12-29 10:14 | 1:14 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV Ckt-1 | 2021-12-31 09:01 | 2021-12-31 15:59 | 6:58 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
|  |  | Total : | 18:47 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Hathazari | Hathazari-Abul Khair 230 kV Ckt | 2021-12-03 14:07 | 2021-12-03 20:28 | 6:21 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Juldah | Juldah-Shahmirpur 132 kV Ckt-1 | 2021-12-06 10:36 | 2021-12-06 11:01 | 0:25 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Juldah-Shahmirpur 132 kV Ckt-2 | 2021-12-06 10:36 | 2021-12-06 11:02 | 0:26 | T |  | 0 | 0 | No interruption
Khulshi | Khulshi-AKS 132 kV Ckt | 2021-12-06 10:36 | 2021-12-06 11:12 | 0:36 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| Khulshi-Bakulia 132 kV Ckt | 2021-12-06 10:36 | 2021-12-06 11:00 | 0:24 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| Khulshi-Modern Steel 132 kV Ckt | 2021-12-06 10:36 | 2021-12-06 10:53 | 0:17 | T | Tripped showing Dist. relay. | 466 | 132.0333 | Power interruption
Rangamati | Rangamati-Chanraghona 132 kV Ckt-2 | 2021-12-11 13:08 | 2021-12-11 13:31 | 0:23 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV Ckt | 2021-12-12 06:01 | 2021-12-12 06:13 | 0:12 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Halishahar | Halishahar-Kulshi 132 kV Ckt-2 | 2021-12-12 16:41 | 2021-12-12 17:17 | 0:36 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Sikalbaha(O) | Sikalbaha(O) S/S-132 kV all lines | 2021-12-18 10:35 | 2021-12-18 12:30 | 1:55 | E/O | Due to bursting of L/A | 64 | 122.6667 | Power interruption
|  |  | Total : | 11:35 |  | Unserved Energy: |  | 254.7
Cumilla Grid Circle :
Sylhet | Sylhet-Fenchuganj 132 kV Ckt | 2021-12-09 04:44 | 2021-12-09 05:05 | 0:21 | T | Tripped showing Dist. relay | 20 | 7 | Power interruption
| Sylhet-Fenchuganj -Bibyanibazar 132 kV Ckt | 2021-12-10 02:12 | 2021-12-10 02:25 | 0:13 | T | Tripped showing Dist. relay | 24 | 5.2 | Power interruption
| Sylhet-Fenchuganj -Bibyanibazar 132 kV Ckt | 2021-12-10 05:02 | 2021-12-10 05:13 | 0:11 | T | Tripped showing Dist. relay
Chowmuhani | Chowmuhani-Ramganj 132 kV Ckt-2 | 2021-12-10 06:27 | 2021-12-10 06:34 | 0:07 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Kachua 132 kV Ckt-2 | 2021-12-10 06:16 | 2021-12-10 06:31 | 0:15 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ashuganj (S) 230 kV Ckt-1 | 2021-12-12 15:02 | 2021-12-12 15:02 | 0:00 | T | Due to abnormal sound at Ashuganj Ckt-1. | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj 132 kV Ckt | 2021-12-13 04:25 | 2021-12-13 04:41 | 0:16 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Sylhet-Fenchuganj 132 kV Ckt | 2021-12-17 01:44 | 2021-12-17 01:57 | 0:13 | T | Tripped showing Dist. relay | 22 | 4.7667 | Power interruption
Chandpur Desh | Chandpur Desh P/P-Ramganj 132 kV Ckt-1 & 2 | 2021-12-29 06:35 | 2021-12-29 07:10 | 0:35 | T | Tripped showing O/V. relay | 0 | 0 | No interruption
Chandpur S/S | Chandpur S/S-Chandpur Desh P/P 132 kV Ckt-1 & 2 | 2021-12-29 06:35 | 2021-12-29 07:20 | 0:45 | T | Tripped showing backup protection relay | 0 | 0 | No interruption
Chandpur Desh | Chandpur Desh P/P-Ramganj 132 kV Ckt-1 & 2 | 2021-12-31 00:28 | 2021-12-31 02:05 | 1:37 | T | Tripped showing O/V. relay | 0 | 0 | No interruption
|  |  | Total : | 4:33 |  | Unserved Energy: |  | 16.9667
Khulna Grid Circle :
Khulna(S) | Khulna(S)-Satkhira 132 kV Ckt-1 | 2021-12-15 04:01 | 2021-12-15 04:01 | 0:00 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Mongla | Mongla-Bagerhat 132 kV Ckt-2 | 2021-12-22 07:12 | 2021-12-22 08:30 | 1:18 | E/O | Due to Breaker replacement | 0 | 0 | No interruption
|  |  | Total : | 1:18 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Jhenaidah(O) | Jhenaidah(O)-Jhenaidah(N) 132 kV Ckt-2 | 2021-12-21 16:35 | 2021-12-21 16:56 | 0:21 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 0:21 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-2 | 2021-12-29 10:54 | 2021-12-29 12:53 | 1:59 | E/O | Due to red-hot maint | 0 | 0 | No interruption
|  |  | Total : | 1:59 |  | Unserved Energy: |  | 0
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 41:53 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: December2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Cantonment | 132/33 kV transformer T-1 | 2021-12-01 11:26 | 2021-12-01 11:53 | 0:27 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2021-12-01 09:16 | 2021-12-01 11:19 | 2:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV transformer T-3 | 2021-12-01 08:13 | 2021-12-01 18:40 | 10:27 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2021-12-02 08:17 | 2021-12-02 14:52 | 6:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 230/132 kV transformer T-01 | 2021-12-02 10:09 | 2021-12-02 16:25 | 6:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Cantonment | 132/33 kV transformer T-1 | 2021-12-03 08:10 | 2021-12-03 16:01 | 7:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 132/33 kV transformers T-3 & T4 | 2021-12-03 08:45 | 2021-12-03 16:52 | 8:07 | S/O | Due to C/M work | 85 | 689.9167 | Power interruption
Tongi | 132/33 kV transformer T-2 | 2021-12-03 09:10 | 2021-12-03 10:38 | 1:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-1 with 33 kV Bus | 2021-12-04 09:38 | 2021-12-04 10:05 | 0:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 132/33 kV transformers T-1 & T2 with 33 kV Bus | 2021-12-04 08:49 | 2021-12-04 17:17 | 8:28 | S/O | Due to PBS work | 40 | 338.6667 | Power interruption
Mymensing | 132/33 kV transformer T-1 | 2021-12-04 09:38 | 2021-12-04 16:28 | 6:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV transformer T-1 with 33 kV Bus | 2021-12-04 10:03 | 2021-12-04 11:21 | 1:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 230/132 kV transformer T-02 | 2021-12-04 09:55 | 2021-12-04 15:46 | 5:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer T-01 | 2021-12-05 10:29 | 2021-12-05 18:45 | 8:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Lalbagh | 132/33 kV transformer T-1 | 2021-12-05 10:07 | 2021-12-06 00:33 | 14:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensing | 132/33 kV transformer T-1 | 2021-12-05 09:26 | 2021-12-05 16:50 | 7:24 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230 kV Bus coupler | 2021-12-06 13:07 | 2021-12-06 13:08 | 0:01 | S/O | Due to SCADA test | 0 | 0 | No interruption
Mymensing | 132/33 kV transformer T-1 | 2021-12-06 10:01 | 2021-12-06 15:40 | 5:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Satmosjid | 132/33 kV transformer T-1 | 2021-12-06 10:05 | 2021-12-06 14:51 | 4:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensing | 132/33 kV transformer T-1 | 2021-12-07 10:15 | 2021-12-07 15:15 | 5:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2021-12-08 09:28 | 2021-12-08 16:35 | 7:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV transformer T-2 with 33 kV Bus | 2021-12-08 09:44 | 2021-12-08 15:42 | 5:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Satmosjid | 132/33 kV transformer T-2 | 2021-12-08 15:10 | 2021-12-08 16:44 | 1:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV transformer T-2 | 2021-12-09 09:36 | 2021-12-09 14:21 | 4:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV transformer T-2 | 2021-12-09 09:45 | 2021-12-09 16:38 | 6:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 132/33 kV transformer T-3 | 2021-12-09 10:18 | 2021-12-09 16:14 | 5:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Uttara | 132/33 kV transformer T-3 | 2021-12-09 10:25 | 2021-12-09 14:52 | 4:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | 132/33 kV transformer GT-2 | 2021-12-11 08:41 | 2021-12-11 16:47 | 8:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-2 | 2021-12-11 09:21 | 2021-12-11 16:07 | 6:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV transformer T-1 | 2021-12-11 10:08 | 2021-12-11 16:32 | 6:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV transformer T-2 with 33 kV Bus-2 | 2021-12-11 09:00 | 2021-12-11 12:56 | 3:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 230/132 kV transformer T-03 | 2021-12-11 09:27 | 2021-12-11 09:27 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 132/33 kV transformer T-3 | 2021-12-11 11:35 | 2021-12-11 17:30 | 5:55 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV transformer T-01 | 2021-12-12 09:27 | 2021-12-12 15:45 | 6:18 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer Tr-02 | 2021-12-12 16:10 | 2021-12-12 16:20 | 0:10 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer Tr-03 | 2021-12-12 16:22 | 2021-12-12 17:17 | 0:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV transformer T-01 | 2021-12-13 08:38 | 2021-12-13 12:36 | 3:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV transformer T-1 | 2021-12-14 07:20 | 2021-12-14 08:15 | 0:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV transformer T-1 | 2021-12-14 09:30 | 2021-12-14 10:47 | 1:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 132/33 kV transformer T-2 | 2021-12-14 09:08 | 2021-12-14 17:01 | 7:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132 kV Bus | 2021-12-14 09:20 | 2021-12-14 16:20 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV transformer T-1 | 2021-12-14 09:45 | 2021-12-14 17:06 | 7:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 132/33 kV transformer T-2 | 2021-12-14 09:19 | 2021-12-14 17:01 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV transformer T-3 | 2021-12-15 09:52 | 2021-12-15 15:46 | 5:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 132/33 kV transformer T-2 | 2021-12-15 09:08 | 2021-12-15 17:01 | 7:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-2 | 2021-12-18 09:09 | 2021-12-18 15:53 | 6:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV transformer TR-2 | 2021-12-18 08:45 | 2021-12-18 15:45 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-2 | 2021-12-19 09:05 | 2021-12-19 16:18 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV transformer TR-2 | 2021-12-19 08:32 | 2021-12-19 14:34 | 6:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Manikganj | 132/33 kV transformer T-4 | 2021-12-19 09:52 | 2021-12-19 11:45 | 1:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajendrapur | 132 kV Bus-1 | 2021-12-19 10:35 | 2021-12-19 10:35 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Joydevpur | 132/33 kV transformer T-2 | 2021-12-19 13:14 | 2021-12-20 02:30 | 13:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhaluka | 132/33 kV transformer T-1 | 2021-12-20 11:57 | 2021-12-20 13:17 | 1:20 | S/O | Due to D/W work | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-2 | 2021-12-20 09:21 | 2021-12-20 15:48 | 6:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-2 | 2021-12-20 09:22 | 2021-12-20 12:30 | 3:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Kodda | 132/33 kV transformer T-1 | 2021-12-21 07:48 | 2021-12-21 07:48 | 0:00 | S/O | Due to relay test | 0 | 0 | No interruption
Joydevpur | 132/33 kV transformer T-4 | 2021-12-21 09:37 | 2021-12-21 10:56 | 1:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-1 | 2021-12-21 10:18 | 2021-12-21 16:42 | 6:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Joydevpur | 132/33 kV transformer T3 | 2021-12-21 11:23 | 2021-12-21 22:56 | 11:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 132/33 kV transformer T-3 | 2021-12-22 09:05 | 2021-12-22 17:05 | 8:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV transformer T-1 | 2021-12-22 08:55 | 2021-12-22 13:56 | 5:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Satmosjid | 132 kV Bus-2 | 2021-12-22 09:29 | 2021-12-22 12:31 | 3:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 33 kV capacitor bank | 2021-12-22 09:15 | 2021-12-22 16:05 | 6:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 132/33 kV transformer T-1 | 2021-12-22 13:54 | 2021-12-22 15:09 | 1:15 | S/O | Due to protection work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2021-12-22 15:25 | 2021-12-22 16:28 | 1:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 33 kV capacitor bank | 2021-12-23 08:50 | 2021-12-23 16:40 | 7:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer T02 | 2021-12-23 09:42 | 2021-12-23 14:27 | 4:45 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer T02 | 2021-12-26 10:09 | 2021-12-26 16:02 | 5:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 132/33 kV transformer T-4 | 2021-12-26 09:18 | 2021-12-26 17:06 | 7:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer T02 | 2021-12-27 10:10 | 2021-12-27 14:07 | 3:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | 132/33 kV transformer T-1 | 2021-12-27 08:38 | 2021-12-27 15:37 | 6:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV transformer T-4 | 2021-12-27 10:31 | 2021-12-27 13:40 | 3:09 | S/O | Due to D/W work | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-1 | 2021-12-28 09:18 | 2021-12-28 16:43 | 7:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | 400/230 kV transformer T-01 | 2021-12-28 09:24 | 2021-12-28 14:41 | 5:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | 132/33 kV transformer T-2 | 2021-12-29 08:52 | 2021-12-29 16:13 | 7:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV transformer T-3 | 2021-12-29 08:51 | 2021-12-29 14:52 | 6:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | 400/230 kV transformer T-01 | 2021-12-29 08:58 | 2021-12-29 15:27 | 6:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 132/33 kV transformer T-1 | 2021-12-29 13:43 | 2021-12-29 13:43 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T-4 |  | 2021-12-29 13:15 |  | S/O | After.maint work | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-1 | 2021-12-29 09:53 | 2021-12-29 13:53 | 4:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2021-12-30 13:55 | 2021-12-30 15:36 | 1:41 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2021-12-30 14:40 | 2021-12-30 17:13 | 2:33 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 415:21 |  | Unserved Energy: |  | 1028.5833
Dhaka (South) Grid Circle :
Keraniganj | 132/33 kV transformer T-2 | 2021-12-03 11:02 | 2021-12-03 12:51 | 1:49 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2021-12-03 14:44 | 2021-12-03 16:15 | 1:31 | S/O | Due to temperature high | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2021-12-04 08:35 | 2021-12-04 12:05 | 3:30 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 with 33 kV Bus | 2021-12-04 09:12 | 2021-12-04 14:48 | 5:36 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer T-02 | 2021-12-05 10:44 | 2021-12-05 13:28 | 2:44 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132 kV GIS 132 kV Bus coupler | 2021-12-06 11:51 | 2021-12-06 12:49 | 0:58 | S/O | Due to SCADA test | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2021-12-06 17:05 | 2021-12-06 17:26 | 0:21 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2021-12-08 16:46 | 2021-12-08 19:31 | 2:45 | S/O | Due to maint.work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2021-12-09 14:56 | 2021-12-09 20:07 | 5:11 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 with 33 kV Bus-1 | 2021-12-11 08:46 | 2021-12-11 12:12 | 3:26 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2021-12-14 09:10 | 2021-12-14 15:34 | 6:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | 132 kV Bus-2 | 2021-12-09 09:02 | 2021-12-09 17:03 | 8:01 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV Bus-1 | 2021-12-09 09:26 | 2021-12-09 14:59 | 5:33 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230 kV Bus-1 | 2021-12-11 08:08 | 2021-12-11 16:55 | 8:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 230/132 kV transformer T01 | 2021-12-12 08:26 | 2021-12-12 15:51 | 7:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | 400/230 kV transformer T01 | 2021-12-13 08:34 | 2021-12-13 15:57 | 7:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | 132 kV main Bus | 2021-12-13 10:10 | 2021-12-13 15:12 | 5:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 230/132 kV transformer T01 | 2021-12-13 08:35 | 2021-12-13 17:02 | 8:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | 400/230 kV transformer ATR01 | 2021-12-14 08:58 | 2021-12-14 15:45 | 6:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 230/132 kV transformer T02 | 2021-12-14 08:31 | 2021-12-14 17:03 | 8:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | 132 kV Bus-2 | 2021-12-14 08:25 | 2021-12-14 16:16 | 7:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Madanganj | 132 kV reserve Bus | 2021-12-14 10:58 | 2021-12-14 19:55 | 8:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | 400/230 kV transformer ATR01 | 2021-12-15 09:23 | 2021-12-15 17:05 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 230/132 kV transformer T02 | 2021-12-15 08:25 | 2021-12-15 16:55 | 8:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | 132/33 kV transformer T2 | 2021-12-17 10:06 | 2021-12-17 15:35 | 5:29 | S/O | Due to DPDC work at 33 kV side | 20 | 109.6667 | Power interruption
Ghorashal | 230/132 kV transformer T02 | 2021-12-17 08:25 | 2021-12-17 11:55 | 3:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhulta | 400/230 kV transformer T01 | 2021-12-18 08:38 | 2021-12-18 17:01 | 8:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 230/132 kV transformer T02 | 2021-12-18 08:48 | 2021-12-18 14:22 | 5:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | 132 kV reserve Bus | 2021-12-19 09:25 | 2021-12-19 09:25 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | 400/230 kV transformer T02 | 2021-12-19 09:14 | 2021-12-19 15:45 | 6:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | 230/132 kV transformer TR3 | 2021-12-19 10:56 | 2021-12-19 16:58 | 6:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhulta | 400/230 kV transformer T02 | 2021-12-20 10:09 | 2021-12-20 16:03 | 5:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 230/132 kV transformer T03 | 2021-12-21 08:32 | 2021-12-21 16:55 | 8:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Gulshan | 132/33 kV transformer T-1 | 2021-12-22 09:56 | 2021-12-22 10:43 | 0:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 230 kV Bus-1 | 2021-12-22 09:11 | 2021-12-22 13:32 | 4:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Gulshan | 132/33 kV transformer T-2 | 2021-12-23 08:31 | 2021-12-23 16:03 | 7:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 230 kV Bus-2 | 2021-12-23 09:08 | 2021-12-23 13:35 | 4:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | 132/33 kV transformer T-2 | 2021-12-24 09:15 | 2021-12-24 17:02 | 7:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | 230/132 kV transformer T01 | 2021-12-26 10:35 | 2021-12-26 10:35 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Kamrangirchar | 132/33 kV transformer T-1 | 2021-12-28 08:46 | 2021-12-28 16:58 | 8:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | 132/33 kV transformer T-1 | 2021-12-28 11:45 | 2021-12-28 12:41 | 0:56 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230 kV Bus-2 | 2021-12-29 09:32 | 2021-12-29 16:20 | 6:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Kamrangirchar | 132/33 kV transformer T-2 | 2021-12-29 08:56 | 2021-12-29 13:28 | 4:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | 400 kV Bus-2 | 2021-12-30 10:26 | 2021-12-30 14:46 | 4:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | 230/132 kV transformer T02 | 2021-12-31 08:08 | 2021-12-31 15:34 | 7:26 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer T03 | 2021-12-31 17:12 | 2021-12-31 18:43 | 1:31 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 207:22 |  | Unserved Energy: |  | 109.6667
Chattogram Grid Circle :
Bakulia | 132 kV Bus-B | 2021-12-02 08:14 | 2021-12-02 12:26 | 4:12 | S/O | Due to A/M work | 0 | 0 | No interruption
GPH | 132/33 kV transformers T1 & T2 | 2021-12-03 11:17 | 2021-12-03 14:47 | 3:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat GIS | 132/33 kV transformer T2 | 2021-12-03 10:45 | 2021-12-03 10:45 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV transformers T1 & T3 | 2021-12-03 09:03 | 2021-12-03 10:53 | 1:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Bakulia | 132/33 kV transformer T3 | 2021-12-04 07:18 | 2021-12-04 07:18 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Halishahar | 132/33 kV transformer T-1 | 2021-12-04 10:39 | 2021-12-04 16:54 | 6:15 | S/O | Due to GIS work | 0 | 0 | No interruption
GPH | 230/132 kV transformer T02 | 2021-12-06 14:30 | 2021-12-06 16:09 | 1:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandraghona | 132/33 kV transformer T1 | 2021-12-08 09:44 | 2021-12-08 14:28 | 4:44 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T3 | 2021-12-09 10:32 | 2021-12-09 11:12 | 0:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | 132/33 kV transformer T2 | 2021-12-10 07:22 | 2021-12-10 11:38 | 4:16 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2021-12-11 07:35 | 2021-12-11 11:26 | 3:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | 132/33 kV transformer T-2 | 2021-12-22 12:27 | 2021-12-22 12:27 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Halishahar | 132/33 kV transformers T1 & T2 | 2021-12-22 13:26 | 2021-12-22 15:04 | 1:38 | S/O | Due to C/M work | 25 | 40.8333 | Power interruption
Shahmirpur | 132/33 kV transformer T2 | 2021-12-24 07:55 | 2021-12-24 07:55 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Patanga | 132/33 kV transformers T1 & T2 | 2021-12-24 08:18 | 2021-12-24 09:55 | 1:37 | S/O | Due to C/M work | 34 | 54.9667 | Power interruption
Shahmirpur | 132/33 kV transformer T2 | 2021-12-24 08:01 | 2021-12-24 13:17 | 5:16 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirsorai | 230/33/11 kV transformer T01 |  | 2021-12-24 08:01 |  | S/O | After maint.work | 0 | 0 | No interruption
Dohazari | 132 kV main bus | 2021-12-31 06:51 | 2021-12-31 14:59 | 8:08 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 47:36 |  | Unserved Energy : |  | 95.8
Cumilla Grid Circle :
Sylhet | 132/33 kV transformer T2 | 2021-12-01 09:27 | 2021-12-01 11:25 | 1:58 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2021-12-01 14:29 | 2021-12-01 16:15 | 1:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Comilla(N) | 230/132 kV transformer T-02 | 2021-12-04 09:29 | 2021-12-04 14:22 | 4:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | 230 kV Bus-1 | 2021-12-05 09:15 | 2021-12-05 17:06 | 7:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | 400/230 kV transformer ICT01 | 2021-12-06 09:28 | 2021-12-06 17:28 | 8:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | 230/132 kV transformer AT-02 | 2021-12-06 09:12 | 2021-12-06 17:25 | 8:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | 400/230 kV transformer ICT02 | 2021-12-07 09:29 | 2021-12-07 17:34 | 8:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Kachua | 132/33 kV transformer T1 | 2021-12-08 09:27 | 2021-12-08 10:42 | 1:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Kulaura | 132 kV Bus-1 | 2021-12-08 10:35 | 2021-12-08 10:35 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | 132/33 kV transformer T2 | 2021-12-09 08:17 | 2021-12-09 15:43 | 7:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Chowmuhani | 132/33 kV transformer T3 | 2021-12-13 08:25 | 2021-12-13 15:52 | 7:27 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2021-12-14 08:23 | 2021-12-14 16:02 | 7:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Comilla(S) | 132/33 kV transformer T1 | 2021-12-15 11:28 | 2021-12-15 11:28 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T3 |  | 2021-12-15 10:10 |  | S/O | After maint.work | 0 | 0 | No interruption
Ashuganj | 132 kV Bus-1 | 2021-12-18 07:32 | 2021-12-18 07:32 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Daudkandi | 132/33 kV transformer T1 | 2021-12-18 08:27 | 2021-12-18 16:55 | 8:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | 132 kV Bus-2 | 2021-12-19 07:40 | 2021-12-19 16:39 | 8:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Daudkandi | 132/33 kV transformer T2 | 2021-12-19 08:18 | 2021-12-19 17:13 | 8:55 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T3 | 2021-12-20 08:26 | 2021-12-20 15:01 | 6:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur | 132/33 kV transformer T1 | 2021-12-21 08:36 | 2021-12-21 18:16 | 9:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2021-12-22 08:36 | 2021-12-22 19:05 | 10:29 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T5 | 2021-12-23 08:36 | 2021-12-23 19:15 | 10:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | 132/33 kV transformer T1 | 2021-12-25 08:34 | 2021-12-25 18:04 | 9:30 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2021-12-26 08:23 | 2021-12-26 19:23 | 11:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Comilla(S) | 132/33 kV transformer T1 with 33 Bus | 2021-12-29 08:00 | 2021-12-29 10:27 | 2:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Ramganj | 132/33 kV transformer T1 | 2021-12-29 08:51 | 2021-12-29 17:37 | 8:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | 132 kV Bus-1 | 2021-12-30 07:37 | 2021-12-30 07:37 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Ramganj | 132/33 kV transformer T2 | 2021-12-30 09:05 | 2021-12-30 16:42 | 7:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | 132/33 kV transformer T2 | 2021-12-30 08:15 | 2021-12-30 11:02 | 2:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Comilla(S) | 132/33 kV transformer T1 |  | 2021-12-30 18:17 |  | S/O | After maint.work | 0 | 0 | No interruption
| 132/33 kV transformer T2 |  | 2021-12-31 18:07 |  | S/O | After maint.work | 0 | 0 | No interruption
|  |  | Total : | 64:33 |  | Unserved Energy : |  | 0
Khulna Grid Circle :
Magura | 132/33 kV transformer T1 | 2021-12-01 08:25 | 2021-12-01 16:21 | 7:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal(O) | 132 kV Bus coupler | 2021-12-02 08:10 | 2021-12-02 17:05 | 8:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV transformer T-02 | 2021-12-02 08:00 | 2021-12-02 16:18 | 8:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Magura | 132/33 kV transformer T-02 | 2021-12-02 08:36 | 2021-12-02 16:17 | 7:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Mongla | 132 kV Full Bus | 2021-12-03 08:03 | 2021-12-03 17:12 | 9:09 | S/O | Due to D/W work | 20 | 183 | Power interruption
Bhandaria | 132/33 kV transformer T1 | 2021-12-07 09:54 | 2021-12-07 10:19 | 0:25 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2021-12-08 08:27 | 2021-12-08 15:57 | 7:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | 230 kV Bus-1 | 2021-12-08 09:47 | 2021-12-08 16:13 | 6:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhandaria | 132/33 kV transformer T1 | 2021-12-09 08:45 | 2021-12-09 17:21 | 8:36 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2021-12-10 08:17 | 2021-12-10 16:25 | 8:08 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2021-12-11 08:26 | 2021-12-11 15:52 | 7:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | 230 kV Bus-2 | 2021-12-11 09:28 | 2021-12-11 15:32 | 6:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhandaria | 132/33 kV transformer T2 | 2021-12-12 08:26 | 2021-12-12 15:51 | 7:25 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2021-12-13 08:48 | 2021-12-13 16:07 | 7:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Baisal(N) | 230/33 kV transformer T02 | 2021-12-14 09:20 | 2021-12-14 15:15 | 5:55 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/33 kV transformer T01 | 2021-12-14 15:26 | 2021-12-14 17:15 | 1:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Shariatpur | 132/33 kV transformer T1 | 2021-12-15 12:24 | 2021-12-15 13:32 | 1:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(C) | 132/33 kV transformer T3 |  | 2021-12-16 14:11 |  | S/O | After maint.work | 0 | 0 | No interruption
| 132/33 kV transformer T3 | 2021-12-18 10:07 | 2021-12-18 14:08 | 4:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhandaria | 132/33 kV transformer T1 | 2021-12-19 09:55 | 2021-12-19 12:12 | 2:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Baisal(O) | 132/33 kV transformer T2 | 2021-12-23 07:52 | 2021-12-23 16:43 | 8:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | 132/33 kV transformer T2 | 2021-12-23 08:14 | 2021-12-23 09:12 | 0:58 | S/O | Due to A/M work | 30 | 29 | No interruption
Baisal (S) | 132/33 kV transformer T2 | 2021-12-24 08:29 | 2021-12-24 13:07 | 4:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Patuakhali | 132/33 kV transformer T1 | 2021-12-26 14:37 | 2021-12-26 17:05 | 2:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhola | 230/33 kV transformer T01 | 2021-12-28 09:47 | 2021-12-28 14:34 | 4:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(C) | 132/33 kV transformer T1 | 2021-12-29 09:05 |  |  | S/O | Due to C/M work | 0 | 0 | No interruption
Bhola | 230/33 kV transformer T01 | 2021-12-29 10:01 | 2021-12-29 15:40 | 5:39 | S/O | Due to A/M work | 25 | 141.25 | No interruption
Magura | 132/33 kV transformer T2 | 2021-12-30 08:10 | 2021-12-30 17:05 | 8:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhola | 230/33 kV transformer T01 | 2021-12-30 09:37 | 2021-12-30 11:48 | 2:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Baisal (N) | 132/33 kV transformer T4 | 2021-12-30 09:55 | 2021-12-30 14:11 | 4:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Magura | 132/33 kV transformer T2 | 2021-12-31 08:08 | 2021-12-31 13:56 | 5:48 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 164:59 |  | Unserved Energy : |  | 353.25
HVDC Grid Circle
Jashore | 132/33 kV transformer T3 | 2021-12-02 08:10 | 2021-12-02 08:10 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Pabna | 132/33 kV transformer T1 | 2021-12-07 09:14 | 2021-12-07 15:22 | 6:08 | S/O | Due to A/M work | 0 | 0
Jashore | 132 kV Bus-1 & 2 | 2021-12-10 09:21 | 2021-12-10 13:13 | 3:52 | S/O | Due to A/M work | 61 | 235.8667 | Power interruption
Pabna | 132/33 kV transformer T2 | 2021-12-10 08:26 | 2021-12-10 09:09 | 0:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | 230/132 kV transformer T-2 | 2021-12-11 09:07 | 2021-12-11 16:32 | 7:25 | S/O | Due to A/M work | 0 | 0 | No interruption
HVDC | HVDC 20DF21 230 kV Filter | 2021-12-11 15:00 | 2021-12-11 16:06 | 1:06 | S/O | Due to maint. work | 0 | 0 | No interruption
Banapole | 132/33 kV transformer T1 | 2021-12-12 07:42 | 2021-12-12 08:16 | 0:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | 230/132 kV transformer T-02 | 2021-12-12 08:15 | 2021-12-12 17:02 | 8:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenaidah | 132/33 kV transformer T1 | 2021-12-12 08:32 | 2021-12-12 14:37 | 6:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | 230/132 kV transformer T-01 | 2021-12-13 08:40 | 2021-12-13 19:27 | 10:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenaidah | 132/33 kV transformer T2 | 2021-12-13 08:29 | 2021-12-13 13:44 | 5:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Pabna | 132/33 kV transformer T2 | 2021-12-13 08:50 | 2021-12-13 13:15 | 4:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | 230/132 kV transformer T-01 | 2021-12-14 08:53 | 2021-12-14 16:58 | 8:05 | S/O | Due to A/M work | 0 | 0 | No interruption
HVDC | HVDC 230 kV filter 20DF21 32 | 2021-12-18 10:17 | 2021-12-18 15:31 | 5:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Pabna | 132/33 kV transformer T3 | 2021-12-19 10:10 | 2021-12-19 13:58 | 3:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjadpur | 132/33 kV transformer T1 | 2021-12-19 08:38 | 2021-12-19 16:20 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara | 132/33 kV transformer GIT1 | 2021-12-21 14:12 | 2021-12-21 16:16 | 2:04 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/5.5 kV transformer T4 | 2021-12-28 09:54 | 2021-12-28 17:02 | 7:08 | S/O | Due to C/M work | 0 | 0 | No interruption
HVDC | 400 kV Bus-1 | 2021-12-28 09:27 | 2021-12-28 17:00 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjadpur | 132/33 kV transformer T4 | 2021-12-29 08:38 | 2021-12-29 15:21 | 6:43 | S/O | Due to A/M work | 0 | 0 | No interruption
HVDC | 230 kV Bus-1 | 2021-12-29 09:53 | 2021-12-29 17:13 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenaidah | 132/33 kV transformer T2 | 2021-12-31 08:08 | 2021-12-31 13:56 | 5:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjadpur | 132 kV Bus | 2021-12-31 08:25 | 2021-12-31 15:55 | 7:30 | S/O | Due to A/M work | 25 | 187.5 | Power interruption
|  |  | Total : | 124:02 |  | Unserved Energy : |  | 423.3667
Bogura Grid Circle:
Amnura | 132/33 kV transformer T3 | 2021-12-01 08:27 | 2021-12-01 16:19 | 7:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Thakurgaon | 132/33 kV transformer T3 | 2021-12-01 09:05 | 2021-12-01 16:55 | 7:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Amnura | 132/33 kV transformer T3 | 2021-12-02 08:24 | 2021-12-02 16:09 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | 230/132 kV transformer T01 | 2021-12-04 08:30 | 2021-12-04 16:54 | 8:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | 230/132 kV transformer T02 | 2021-12-05 11:07 | 2021-12-05 11:07 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Jaldhaka | 132/33 kV transformer T1 | 2021-12-05 11:43 | 2021-12-05 12:45 | 1:02 | S/O | Due to C/M work | 8 | 8.2667 | Power interruption
Rajshahi | 230/132 kV transformer T01 | 2021-12-06 08:21 | 2021-12-06 16:10 | 7:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura(N) | 132 kV Busbar | 2021-12-07 07:17 | 2021-12-07 09:45 | 2:28 | S/O | Due to D/W work | 0 | 0 | No interruption
Rajshahi | 230/132 kV transformer T02 | 2021-12-07 08:38 | 2021-12-07 16:40 | 8:02 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer T01 | 2021-12-08 08:35 | 2021-12-08 16:10 | 7:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi(O) | 33 kV Full Bus | 2021-12-11 08:04 | 2021-12-11 11:30 | 3:26 | S/O | Due to C/M work | 65 | 223.1667 | Power interruption
Purbasadipur | 132/33 kV transformer T2 | 2021-12-11 08:15 | 2021-12-11 11:27 | 3:12 | S/O | Due to A/M work | 20 | 64 | Power interruption
Rajshahi | 132/33 kV transformer T2 | 2021-12-11 08:30 | 2021-12-11 16:22 | 7:52 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2021-12-12 08:33 | 2021-12-12 16:29 | 7:56 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer T02 | 2021-12-14 10:41 | 2021-12-14 10:41 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 132 kV Bus-A | 2021-12-14 08:07 | 2021-12-14 15:20 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV Bus-B | 2021-12-15 08:23 | 2021-12-15 13:30 | 5:07 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T03 | 2021-12-15 10:19 | 2021-12-15 12:55 | 2:36 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T04 | 2021-12-15 08:05 | 2021-12-15 10:16 | 2:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Joypurhat | 132/33 kV transformer T1 | 2021-12-18 09:09 | 2021-12-18 15:53 | 6:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura(N) | 132 kV Bus | 2021-12-19 06:58 | 2021-12-19 06:58 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Barapukuria | 132/33 kV transformer T02 | 2021-12-19 09:20 | 2021-12-19 12:39 | 3:19 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230 kV Bus-B | 2021-12-20 09:06 | 2021-12-20 14:07 | 5:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Joypurhat | 132/33 kV transformer T2 | 2021-12-20 08:20 | 2021-12-20 14:03 | 5:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 132/33 kV transformer T03 | 2021-12-22 10:06 | 2021-12-22 12:23 | 2:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi | 230/132 kV transformer T01 | 2021-12-22 11:23 | 2021-12-22 13:01 | 1:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Mohastanghor | 132/33 kV transformer T1 | 2021-12-22 08:26 | 2021-12-22 11:02 | 2:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjadpur | 132/33 kV transformer T2 | 2021-12-22 08:30 | 2021-12-22 16:18 | 7:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura(N) | 132 kV main Bus | 2021-12-22 10:44 | 2021-12-22 10:44 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Saidpur | 132/33 kV transformer T4 | 2021-12-22 11:45 | 2021-12-22 16:12 | 4:27 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV Bus-B | 2021-12-22 11:40 | 2021-12-22 15:50 | 4:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Joypurhat | 132/33 kV transformer T3 | 2021-12-23 08:21 | 2021-12-23 14:14 | 5:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura(N) | 132 kV main Bus | 2021-12-23 10:44 | 2021-12-23 15:54 | 5:10 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230/132 kV transformer T03 | 2021-12-26 09:37 | 2021-12-26 12:09 | 2:32 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer T02 | 2021-12-26 12:10 | 2021-12-26 17:15 | 5:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Rajshahi(N) | 132 kV Bus coupler | 2021-12-27 11:00 | 2021-12-27 16:36 | 5:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T1 | 2021-12-28 10:21 | 2021-12-28 15:35 | 5:14 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 & 33 kV Bus | 2021-12-28 14:27 | 2021-12-28 15:35 | 1:08 | S/O | Due to A/M work | 7 | 7.9333 | Power interruption
Purbasadipur | 132/33 kV transformer T3 | 2021-12-29 09:55 | 2021-12-29 09:55 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Rajshahi(N) | 230 kV Bus coupler | 2021-12-29 10:15 | 2021-12-29 15:29 | 5:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV transformer T1 with 33 kV Bus | 2021-12-29 07:38 | 2021-12-29 09:20 | 1:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T1 | 2021-12-30 12:54 | 2021-12-30 15:18 | 2:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV transformer T2 | 2021-12-30 09:04 | 2021-12-30 11:40 | 2:36 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2021-12-30 12:23 | 2021-12-30 15:13 | 2:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura(N) | 230/132 kV transformer T01 | 2021-12-30 12:07 | 2021-12-30 13:40 | 1:33 | S/O | Due to D/W work | 0 | 0 | No interruption
Mohastanghor | 132 kV Bus-1 | 2021-12-31 09:24 | 2021-12-31 11:40 | 2:16 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV Bus-2 | 2021-12-31 11:55 | 2021-12-31 15:51 | 3:56 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 195:12 |  | Unserved Energy : |  | 303.3667
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1219:05 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/5 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: December2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agarogaon | Agarogaon-Rampura 132 kV Ckt-1 | 2021-12-01 12:17 | 2021-12-01 12:40 | 0:23 | S/O | Due to A/M work | 0 | 0 | No interruption
| Agarogaon-Rampura 132 kV Ckt-2 | 2021-12-01 12:43 | 2021-12-01 13:04 | 0:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-1 | 2021-12-01 10:10 | 2021-12-01 16:00 | 5:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV Ckt | 2021-12-01 09:34 | 2021-12-01 15:37 | 6:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Tongi milegate 132 kV Ckt-2 | 2021-12-02 10:09 | 2021-12-02 15:29 | 5:20 | S/O | Due to D/W work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamrai 132 kV Ckt-1 | 2021-12-02 09:07 | 2021-12-02 10:01 | 0:54 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kaliakoir-Dhamrai 132 kV Ckt-2 | 2021-12-02 10:07 | 2021-12-02 11:01 | 0:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV Ckt-1 | 2021-12-05 10:07 | 2021-12-05 10:07 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV Ckt-1 | 2021-12-05 07:10 | 2021-12-05 07:10 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV Ckt-1 | 2021-12-05 10:45 | 2021-12-05 13:37 | 2:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Uttara | Uttara 3rd phase -Mirpur 132 kV Ckt | 2021-12-05 08:53 | 2021-12-05 23:20 | 14:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | Agargaon-Satmosjid 132 kV Ckt-1 | 2021-12-06 09:20 | 2021-12-06 09:20 | 0:00 | S/O |  | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Aminbazar 230 kV Ckt-1 | 2021-12-07 09:09 | 2021-12-07 11:01 | 1:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Uttara | Uttara 3rd phase -Mirpur 132 kV Ckt-2 | 2021-12-07 09:19 | 2021-12-07 17:07 | 7:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Aminbazar 230 kV Ckt-1 | 2021-12-08 11:03 | 2021-12-08 12:10 | 1:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV Ckt | 2021-12-08 08:32 | 2021-12-08 16:51 | 8:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | Agargaon-Satmosjid 132 kV Ckt-2 | 2021-12-08 14:58 | 2021-12-08 15:29 | 0:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Kodda MW 230 kV Ckt | 2021-12-09 09:23 | 2021-12-09 10:45 | 1:22 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kaliakoir-Tongi 230 kV Ckt | 2021-12-09 10:52 | 2021-12-09 11:42 | 0:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Tongi milegate 132 kV Ckt-2 | 2021-12-09 12:44 | 2021-12-09 14:32 | 1:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | Kodda-Rajendrapur 132 kV Ckt-1 |  | 2021-12-09 16:06 |  |  | After maint. Work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-1 | 2021-12-12 08:29 | 2021-12-12 16:30 | 8:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Manikganj | Manikganj-Kodda 132 kV Ckt-2 | 2021-12-12 10:41 | 2021-12-12 11:30 | 0:49 | S/O | Due to A/M work | 0 | 0 | No interruption
2021-12-13 10:41
Tongi | Tongi-Ghorashal 230 kV Ckt-1 | 2021-12-13 09:55 | 2021-12-13 17:27 | 7:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Manikganj | Manikganj-Kabirpur 132 kV Ckt-2 | 2021-12-13 09:11 | 2021-12-13 16:22 | 7:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV Ckt-1 |  | 2021-12-13 15:05 |  |  | After maint.work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV Ckt-2 | 2021-12-14 07:07 | 2021-12-14 07:07 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV Ckt-1 | 2021-12-14 09:30 | 2021-12-14 10:15 | 0:45 | S/O | Due to C/M work | 0 | 0 | No interruption
| Tongi-Kabirpur 132 kV Ckt-2 | 2021-12-14 10:17 | 2021-12-14 10:58 | 0:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV Ckt-2 | 2021-12-15 06:50 | 2021-12-15 06:50 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Kaliakoir 230 kV Ckt | 2021-12-15 08:47 | 2021-12-15 15:18 | 6:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV Ckt-1 | 2021-12-18 09:53 | 2021-12-18 15:55 | 6:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Ghorashal 230 kV Ckt-1 | 2021-12-18 09:00 | 2021-12-18 17:34 | 8:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh S/S | Mymensingh S/S-Bhaluka 132 kV Ckt-1 | 2021-12-18 08:50 | 2021-12-18 16:19 | 7:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | Joydevpur-Kodda BR Power Gen.132 kV Ckt-1 | 2021-12-19 08:25 | 2021-12-19 11:20 | 2:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV Ckt-2 | 2021-12-19 08:47 | 2021-12-19 20:12 | 11:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh S/S | Mymensingh S/S-Bhaluka 132 kV Ckt-1 | 2021-12-19 08:33 | 2021-12-19 16:58 | 8:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV Ckt-1 | 2021-12-19 09:42 | 2021-12-19 15:44 | 6:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydepur | Joydepur-Kodda BR Power Gen.132 kV Ckt-2 | 2021-12-19 11:32 | 2021-12-19 12:32 | 1:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kodda 132 kV Ckt-1 | 2021-12-19 12:35 | 2021-12-19 13:02 | 0:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Joydepur | Joydepur-Ghorashal 132 kV Ckt-1 | 2021-12-19 12:42 | 2021-12-19 13:57 | 1:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV Ckt-1 | 2021-12-20 07:09 | 2021-12-20 07:09 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Mirpur 132 kV Ckt-2 | 2021-12-20 09:14 | 2021-12-20 16:25 | 7:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV Ckt-1 | 2021-12-20 09:06 | 2021-12-20 13:39 | 4:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Bhaluka 132 kV Ckt-1 | 2021-12-20 10:13 | 2021-12-20 16:30 | 6:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | Tangail-RPCL 132 kV Ckt-1 | 2021-12-20 08:35 | 2021-12-20 17:03 | 8:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV Ckt-2 | 2021-12-21 09:07 | 2021-12-21 14:47 | 5:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV Ckt-2 | 2021-12-21 08:48 | 2021-12-21 16:25 | 7:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Bhaluka 132 kV Ckt-1 | 2021-12-21 08:51 | 2021-12-21 16:01 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh 132 kV Ckt-1 | 2021-12-21 08:20 | 2021-12-21 16:57 | 8:37 | S/O | Due to A/M work | 0 | 0 | No interruption
| Tangail-Mymensingh 132 kV Ckt-1 | 2021-12-22 07:52 | 2021-12-22 07:52 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV Ckt-2 | 2021-12-22 08:32 | 2021-12-22 16:51 | 8:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV Ckt-1 | 2021-12-22 10:01 | 2021-12-22 15:39 | 5:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Tongi milegate 132 kV Ckt-2 | 2021-12-22 11:50 | 2021-12-22 19:28 | 7:38 | S/O | Due to D/W work | 0 | 0 | No interruption
| Tongi-Tongi(N) 132 kV Ckt-1 | 2021-12-22 12:35 | 2021-12-22 15:09 | 2:34 | S/O | Due to protection test | 0 | 0 | No interruption
| Tongi-Tongi(N) 132 kV Ckt-2 | 2021-12-22 15:27 | 2021-12-22 16:18 | 0:51 | S/O | Due to protection work | 0 | 0 | No interruption
Joydevpur | Joydevpur-Ghorashal 132 kV Ckt-1 | 2021-12-23 09:09 | 2021-12-23 16:48 | 7:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Tongi milegate 132 kV Ckt-2 | 2021-12-23 11:04 | 2021-12-23 15:25 | 4:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh RPCL 132 kV Ckt-1 | 2021-12-23 12:48 | 2021-12-23 15:59 | 3:11 | S/O | Due to protection work | 0 | 0 | No interruption
Tongi | Tongi-Tongi milegate 132 kV Ckt-1 | 2021-12-23 15:31 | 2021-12-23 19:13 | 3:42 | S/O | Due to D/W work | 0 | 0 | No interruption
Tangail | Tangail-RPCL 132 kV Ckt-2 | 2021-12-23 16:15 | 2021-12-23 17:49 | 1:34 | S/O | Due to protection work | 0 | 0 | No interruption
| Tangail-Kaliakoir 132 kV Ckt-2 | 2021-12-25 08:10 | 2021-12-25 18:07 | 9:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Savar-Manikganj P/P 132 kV Ckt-1 | 2021-12-26 09:14 | 2021-12-26 17:00 | 7:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh RPCL 132 kV Ckt-2 | 2021-12-26 08:38 | 2021-12-26 18:03 | 9:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Tongi milegate 132 kV Ckt-1 | 2021-12-26 10:46 | 2021-12-26 15:59 | 5:13 | S/O | Due to D/W work | 0 | 0 | No interruption
Agarogaon | Agarogaon-Cantonment 132 kV Ckt-1 | 2021-12-27 07:59 | 2021-12-27 09:38 | 1:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh RPCL 132 kV Ckt-2 | 2021-12-27 08:13 | 2021-12-27 17:06 | 8:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt | 2021-12-27 11:45 | 2021-12-27 12:23 | 0:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | Tangail-RPCL 132 kV Ckt-2 | 2021-12-28 08:51 | 2021-12-28 16:51 | 8:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Tongi milegate 132 kV Ckt-1 | 2021-12-28 12:22 | 2021-12-28 17:24 | 5:02 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-1 |  | 2021-12-28 11:43 |  | S/O | After maint.work | 0 | 0 | No interruption
Kodda | Kodda-Rajendrapur 132 kV Ckt-1 | 2021-12-28 15:51 | 2021-12-28 16:20 | 0:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Agarogaon | Agarogaon-Cantonment 132 kV Ckt-2 | 2021-12-29 11:43 | 2021-12-29 12:48 | 1:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Tongi 132 kV Ckt-1 | 2021-12-29 09:31 | 2021-12-29 13:22 | 3:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajendrapur | Rajendrapur-Kodda 132 kV Ckt-2 | 2021-12-29 12:30 | 2021-12-29 13:10 | 0:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Savar-Manikganj P/P 132 kV Ckt-1 | 2021-12-29 09:19 | 2021-12-29 16:55 | 7:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Tongi 132 kV Ckt-2 | 2021-12-30 09:05 | 2021-12-30 13:58 | 4:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Savar-Manikganj 132 kV Ckt-1 | 2021-12-30 09:17 | 2021-12-30 13:24 | 4:07 | S/O | Due to D/W work | 0 | 0 | No interruption
Tangail | Tangail-Kaliakoir 132 kV Ckt-1 | 2021-12-30 08:39 | 2021-12-30 16:52 | 8:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Savar-Manikganj P/P 132 kV Ckt-2 | 2021-12-30 14:11 | 2021-12-30 16:27 | 2:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-1 | 2021-12-31 10:31 | 2021-12-31 17:42 | 7:11 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 343:39 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Hasnabad | Hasnabad-APR 230 kV Ckt | 2021-12-01 07:33 | 2021-12-01 17:21 | 9:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj 132 kV Ckt-1 | 2021-12-01 09:19 | 2021-12-01 17:01 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Aminbazar 132 kV Ckt-1 | 2021-12-01 10:47 | 2021-12-01 12:48 | 2:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-APR 230 kV Ckt | 2021-12-02 07:04 | 2021-12-02 17:18 | 10:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur | Shyampur-APR 230 kV Ckt | 2021-12-02 06:46 | 2021-12-02 17:14 | 10:28 | S/O |  | 0 | 0 | No interruption
Narsingdi | Narsingdi-Ghorashal 132 kV Ckt-2 | 2021-12-02 08:35 | 2021-12-02 14:48 | 6:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Hasnabad 230 kV Ckt-1 | 2021-12-02 10:45 | 2021-12-02 11:38 | 0:53 | S/O | Due to A/M work | 0 | 0 | No interruption
| Keraniganj-Hasnabad 230 kV Ckt-2 | 2021-12-02 11:44 | 2021-12-02 12:38 | 0:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur | Shyampur-APR 230 kV Ckt-1 | 2021-12-03 06:34 | 2021-12-03 17:54 | 11:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-APR 230 kV Ckt-2 | 2021-12-03 06:57 | 2021-12-03 17:57 | 11:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur(O) | Shyampur(O)-Shyampur GIS 132 kV Ckt-1 | 2021-12-03 09:16 | 2021-12-03 18:13 | 8:57 | S/O | Due to A/M work | 0 | 0 | No interruption
APR | APR -Shyampur 230 kV Ckt | 2021-12-04 06:42 | 2021-12-04 19:05 | 12:23 | S/O | Due to A/M work | 0 | 0 | No interruption
| Hasnabad-APR 230 kV Ckt-2 | 2021-12-04 06:42 | 2021-12-04 19:03 | 12:21 | S/O |  | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Aminbazar 230 kV Ckt-1 | 2021-12-04 09:21 | 2021-12-04 13:39 | 4:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Narsingdi 132 kV Ckt-2 | 2021-12-04 10:17 | 2021-12-04 15:45 | 5:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur -Narsingdi 132 kV Ckt | 2021-12-07 07:52 | 2021-12-07 19:42 | 11:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Bhulta | Bhulta-Haripur 230 kV Ckt-2 | 2021-12-08 09:59 | 2021-12-08 16:39 | 6:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Kazla 132 kV Ckt-2 | 2021-12-10 09:08 | 2021-12-10 19:14 | 10:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur(O) | Shyampur(O)-Shyampur(N) 132 kV Ckt-2 | 2021-12-10 08:52 | 2021-12-10 16:54 | 8:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Meghnaghat 230 kV Ckt-1 | 2021-12-11 08:29 | 2021-12-11 08:29 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Siddhirganj GT 132 kV Ckt-1 | 2021-12-11 09:14 | 2021-12-11 16:52 | 7:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur -Meghnaghat 230 kV Ckt-1 | 2021-12-12 10:36 | 2021-12-12 19:18 | 8:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Madanganj S/S | Madanganj S/S-Madanganj Summit 132 kV Ckt | 2021-12-12 10:41 | 2021-12-12 11:30 | 0:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Kazla 132 kV Ckt-2 | 2021-12-12 09:07 | 2021-12-12 15:52 | 6:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur -Meghnaghat 230 kV Ckt-2 | 2021-12-13 09:33 | 2021-12-13 19:18 | 9:45 | S/O | Due to A/M work | 0 | 0 | No interruption
| Haripur -HPL 230 kV Ckt-1 | 2021-12-13 10:32 | 2021-12-13 14:46 | 4:14 | S/O | Due to C/M work | 0 | 0 | No interruption
| Haripur -Bhulta 132 kV Ckt | 2021-12-13 08:54 | 2021-12-13 18:57 | 10:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Bhulta 230 kV Ckt-1 | 2021-12-14 08:36 | 2021-12-14 13:21 | 4:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur -Meghnaghat 230 kV Ckt-2 | 2021-12-14 10:40 | 2021-12-14 20:05 | 9:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Tongi 230 kV Ckt-1 | 2021-12-15 12:48 | 2021-12-15 14:46 | 1:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur -HPL 230 kV Ckt-1 | 2021-12-15 09:54 | 2021-12-15 17:22 | 7:28 | S/O | Due to A/M work | 0 | 0 | No interruption
| Haripur -HPL 230 kV Ckt-2 | 2021-12-18 08:57 | 2021-12-18 14:53 | 5:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Cumilla(N) 230 kV Ckt-1 | 2021-12-18 09:41 | 2021-12-18 14:40 | 4:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Sreenagar 132 kV Ckt-1 | 2021-12-19 15:34 | 2021-12-19 19:29 | 3:55 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur -Siddhirganj 230 kV Ckt-1 | 2021-12-20 08:31 | 2021-12-20 17:17 | 8:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV Ckt-1 | 2021-12-20 08:22 | 2021-12-20 16:44 | 8:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Nwabganj 132 kV Ckt-2 | 2021-12-20 11:51 | 2021-12-20 18:16 | 6:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Cumilla(N) 230 kV Ckt-2 | 2021-12-20 09:10 | 2021-12-20 16:30 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Sreenagar 132 kV Ckt-2 | 2021-12-20 16:21 | 2021-12-20 18:16 | 1:55 | S/O | Due to relay test | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV Ckt-1 | 2021-12-21 08:22 | 2021-12-21 16:54 | 8:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur -Haripur 230 kV Ckt-2 | 2021-12-21 09:51 | 2021-12-21 14:03 | 4:12 | S/O | Due to C/M work | 0 | 0 | No interruption
| Haripur -Siddhirganj 230 kV Ckt-1 | 2021-12-21 08:28 | 2021-12-21 14:07 | 5:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Cumilla(N) 230 kV Ckt-2 | 2021-12-21 09:27 | 2021-12-21 16:00 | 6:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Gulshan 132 kV Ckt-1 | 2021-12-21 08:22 | 2021-12-21 15:52 | 7:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV Ckt-2 | 2021-12-22 08:24 | 2021-12-22 17:08 | 8:44 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ghorashal-Joydevpur 132 kV Ckt-1 | 2021-12-22 09:15 | 2021-12-22 17:14 | 7:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur -Siddhirganj 230 kV Ckt-2 | 2021-12-22 09:55 | 2021-12-22 17:36 | 7:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Gulshan 132 kV Ckt-1 | 2021-12-22 10:12 | 2021-12-22 10:31 | 0:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV Ckt-2 | 2021-12-23 09:10 | 2021-12-23 16:39 | 7:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Gulshan 132 kV Ckt-2 | 2021-12-23 08:44 | 2021-12-23 16:17 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV Ckt-2 | 2021-12-24 08:45 | 2021-12-24 13:06 | 4:21 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ghorashal-Bhulta 230 kV Ckt | 2021-12-25 09:27 | 2021-12-25 17:01 | 7:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur -Ullon 132 kV Ckt | 2021-12-26 11:10 | 2021-12-26 16:01 | 4:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-APR 230 kV Ckt | 2021-12-26 08:42 | 2021-12-26 14:48 | 6:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Mdanganj | Mdanganj-Summit P/P 132 kV Ckt | 2021-12-26 11:08 | 2021-12-27 10:39 | 23:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV CKt-1 | 2021-12-26 08:18 | 2021-12-26 16:52 | 8:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Bhulta 230 kV Ckt-1 | 2021-12-27 09:48 | 2021-12-27 19:07 | 9:19 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ghorashal-Joydevpur 132 kV Ckt-2 | 2021-12-27 10:20 | 2021-12-27 17:50 | 7:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV CKt-2 | 2021-12-28 09:19 | 2021-12-28 16:53 | 7:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Narsingdi 132 kV Ckt-1 | 2021-12-29 09:28 | 2021-12-29 16:47 | 7:19 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ghorashal-Joydevpur 132 kV Ckt-2 | 2021-12-29 07:46 | 2021-12-29 13:25 | 5:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Shyampur 230 kV Ckt | 2021-12-29 07:23 | 2021-12-29 20:26 | 13:03 | S/O | Due to A/M work | 0 | 0 | No interruption
| Hasnabad-Shyampur 230 kV Ckt | 2021-12-30 08:41 | 2021-12-30 15:38 | 6:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Narsingdi 132 kV Ckt-1 | 2021-12-30 09:28 | 2021-12-30 15:02 | 5:34 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 459:51 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Hathazari | Hathazari-Kaptai 132 kV Ckt-2 | 2021-12-01 08:53 | 2021-12-01 16:55 | 8:02 | S/O | Due to A/M work | 0 | 0 | No interruption
PHP | PHP-Feni 132 kV Ckt-2 | 2021-12-02 08:42 | 2021-12-02 17:11 | 8:29 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha 230-Sikalbaha 132 kV Ckt-2 | 2021-12-02 10:15 | 2021-12-02 13:44 | 3:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Khulshi 132 kV Ckt | 2021-12-02 09:32 | 2021-12-02 09:32 | 0:00 | S/O | Due to project work | 0 | 0 | No interruption
PHP | PHP-Baroierhat 132 kV Ckt | 2021-12-02 08:45 | 2021-12-02 17:27 | 8:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Madunaghat 132 kV Ckt-1 | 2021-12-03 07:24 | 2021-12-03 07:24 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt-1 | 2021-12-04 08:56 | 2021-12-04 16:10 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
BSRM | BSRM-Mirsarai 230 kV Ckt-1 | 2021-12-05 11:35 | 2021-12-05 11:35 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 230 kV Ckt-2 | 2021-12-06 09:51 | 2021-12-06 17:02 | 7:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Kaptai 132 kV Ckt-2 | 2021-12-07 09:27 | 2021-12-07 15:50 | 6:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 230 kV Ckt-1 | 2021-12-07 09:47 | 2021-12-07 17:04 | 7:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Kaptai 132 kV Ckt-2 | 2021-12-08 09:10 | 2021-12-08 15:28 | 6:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 230 kV Ckt-1 | 2021-12-08 09:38 | 2021-12-08 16:35 | 6:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Halishahar | Halishahar-Rampur (T)-Khulshi 132 kV Ckt-1 | 2021-12-08 09:28 | 2021-12-08 15:08 | 5:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| Halishahar-Rampur (T)-Khulshi 132 kV Ckt-1 | 2021-12-09 07:50 | 2021-12-09 14:43 | 6:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Madunaghat 132 kV Ckt | 2021-12-09 07:50 | 2021-12-09 14:50 | 7:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Kaptai 132 kV Ckt-2 | 2021-12-09 09:09 | 2021-12-09 15:19 | 6:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Halishahar | Halishahar-Rampur (T)-Khulshi 132 kV Ckt-1 | 2021-12-09 07:50 | 2021-12-09 14:48 | 6:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt-1 | 2021-12-09 08:33 | 2021-12-09 16:58 | 8:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahmirpur | Shahmirpur-Juldah 132 kV Ckt-1 | 2021-12-09 10:53 | 2021-12-09 11:59 | 1:06 | S/O | Due to A/M work | 0 | 0 | No interruption
| Shahmirpur-Juldah 132 kV Ckt-2 | 2021-12-09 12:02 | 2021-12-09 12:54 | 0:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Shahmirpur 132 kV Ckt-1 | 2021-12-09 13:00 | 2021-12-09 14:33 | 1:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Halishar-Rampur 1322 kV Ckt-2 | 2021-12-13 07:48 | 2021-12-13 14:11 | 6:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV Ckt-2 | 2021-12-14 08:33 | 2021-12-14 16:20 | 7:47 | S/O | Due to A/M work | 0 | 0 | No interruption
BSRM | BSRM -AKSM 230 kV Ckt | 2021-12-15 09:02 | 2021-12-15 16:17 | 7:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-GPH 230 kV Ckt | 2021-12-18 09:25 | 2021-12-18 15:02 | 5:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV Ckt-1 | 2021-12-19 09:20 | 2021-12-19 19:51 | 10:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV Ckt-1 | 2021-12-19 09:50 | 2021-12-19 09:50 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha(O) | Sikalbaha(O)-Sikalbaha (N) 132 kV Ckt |  | 2021-12-19 19:51 |  | S/O | After maint.work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV Ckt-2 | 2021-12-20 10:01 | 2021-12-20 14:09 | 4:08 | S/O | Due to D/W work | 0 | 0 | No interruption
BSRM | BSRM -GPH 230 kV Ckt | 2021-12-20 08:42 | 2021-12-20 15:51 | 7:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV Ckt-2 | 2021-12-20 08:36 | 2021-12-20 15:45 | 7:09 | S/O | Due to A/M work | 0 | 0 | No interruption
| Dohazari-Sikalbaha 132 kV Ckt-2 | 2021-12-21 09:16 | 2021-12-21 17:07 | 7:51 | S/O | Due to A/M work | 0 | 0 | No interruption
GPH | GPH-BSRM 230 kV Ckt | 2021-12-21 09:20 | 2021-12-21 16:30 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV Ckt-3 | 2021-12-21 08:19 | 2021-12-21 16:06 | 7:47 | S/O | Due to A/M work | 0 | 0 | No interruption
GPH | GPH-BSRM 230 kV Ckt-2 | 2021-12-22 09:02 | 2021-12-22 15:20 | 6:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV Ckt-3 | 2021-12-22 08:49 | 2021-12-22 19:40 | 10:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV Ckt-2 | 2021-12-22 09:56 | 2021-12-22 09:56 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Julda | Julda-Shahmirpur 132 kV Ckt-1 | 2021-12-22 13:24 | 2021-12-22 15:00 | 1:36 | S/O | Due to C/M work | 0 | 0 | No interruption
| Julda-Shahmirpur 132 kV Ckt-2 | 2021-12-22 15:01 | 2021-12-22 16:16 | 1:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-2 | 2021-12-24 06:46 | 2021-12-24 12:02 | 5:16 | S/O | Due to D/W work | 0 | 0 | No interruption
Cox'sbazar | Cox'sbazar-Matarbari 132 kV Ckt | 2021-12-24 06:43 | 2021-12-24 12:02 | 5:19 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-ECPV 132 kV Ckt | 2021-12-24 08:55 | 2021-12-24 11:58 | 3:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat GIS-T.K.chemical 132 kV Ckt | 2021-12-25 09:22 | 2021-12-25 12:46 | 3:24 | S/O | Due to D/W work | 0 | 0 | No interruption
| Madunaghat-Noapara 33 kV PBS feeder | 2021-12-25 09:05 | 2021-12-25 09:05 | 0:00 | S/O | Due to OPGW work | 0 | 0 | No interruption
BSRM | BSRM -BR power Gen.230 kV Ckt | 2021-12-25 12:32 | 2021-12-25 21:03 | 8:31 | S/O | Due to D/W work | 0 | 0 | No interruption
Madunaghat | Madunaghat(O)-T.k.Chemical 132 kV Ckt | 2021-12-26 08:30 | 2021-12-26 08:30 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV Ckt-1 | 2021-12-26 08:08 | 2021-12-26 14:35 | 6:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV Ckt-1 | 2021-12-27 09:02 | 2021-12-27 15:59 | 6:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV Ckt-2 | 2021-12-28 08:27 | 2021-12-28 14:51 | 6:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-AKSML 230 kV Ckt | 2021-12-28 10:42 | 2021-12-28 17:20 | 6:38 | S/O | Due to A/M work | 0 | 0 | No interruption
| Hathazari-Maduaghat 132 kV Ckt-2 | 2021-12-28 09:43 | 2021-12-28 09:43 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV Ckt-2 | 2021-12-29 08:40 | 2021-12-29 15:08 | 6:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt-1 | 2021-12-29 09:30 | 2021-12-29 17:17 | 7:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Hathazari 132 kV Ckt-2 | 2021-12-29 09:43 | 2021-12-29 12:01 | 2:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Chandraghona 132 kV Ckt-1 | 2021-12-29 11:04 | 2021-12-29 13:47 | 2:43 | S/O | Due to C/M work | 0 | 0 | No interruption
| Rangamati-Kagrachari 132 kV Ckt-1 | 2021-12-29 13:56 | 2021-12-29 15:01 | 1:05 | S/O | Due to C/M work | 0 | 0 | No interruption
| Rangamati-Chandraghona 132 kV Ckt-2 | 2021-12-29 15:06 | 2021-12-29 15:40 | 0:34 | S/O | Due to C/M work | 0 | 0 | No interruption
| Rangamati-Kagrachari 132 kV Ckt-2 | 2021-12-29 15:45 | 2021-12-29 16:12 | 0:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Baraulia | Baraulia-Sitalpur 132 kV Ckt | 2021-12-31 14:48 | 2021-12-31 15:35 | 0:47 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 287:34 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
B.Baria | B.Baria-Shahjibazar 132 kV Ckt-1 | 2021-12-01 09:02 | 2021-12-01 16:31 | 7:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Bibiyana 230 kV Ckt-2 | 2021-12-01 09:10 | 2021-12-01 17:28 | 8:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV Ckt-2 | 2021-12-01 11:27 | 2021-12-01 12:49 | 1:22 | S/O | Due to A/M work | 0 | 0 | No interruption
| Sylhet-Chatak 132 kV Ckt-1 | 2021-12-01 12:56 | 2021-12-01 13:51 | 0:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Fenchuganj 230 kV Ckt-2 | 2021-12-02 09:29 | 2021-12-02 17:14 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Chatak | Chatak-Sunamganj 132 kV Ckt | 2021-12-03 07:12 | 2021-12-03 10:35 | 3:23 | S/O | Due to D/W work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-1 | 2021-12-04 07:21 | 2021-12-04 07:21 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV Ckt-2 | 2021-12-05 11:08 | 2021-12-05 12:20 | 1:12 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bibiyana-Kaliakoir 400 kV Ckt-1 | 2021-12-05 09:02 | 2021-12-05 11:06 | 2:04 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bibiyana-Kaliakoir 400 kV Ckt-1 | 2021-12-08 09:30 | 2021-12-08 17:30 | 8:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjbazar | Shahjbazar-Sreemongal 132 kV Ckt-1 | 2021-12-08 08:36 | 2021-12-08 17:15 | 8:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-BSRM 230 kV Ckt-1 | 2021-12-08 08:57 | 2021-12-08 15:58 | 7:01 | S/O | Due to A/M work | 0 | 0 | No interruption
| Cumilla(N)-BSRM 230 kV Ckt-1 | 2021-12-09 08:21 | 2021-12-09 16:08 | 7:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjbazar | Shahjbazar-Sreemongal 132 kV Ckt-1 | 2021-12-09 08:59 | 2021-12-09 17:15 | 8:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Kulaura | Kulaura-Fenchuganj 132 kV Ckt-1 | 2021-12-11 08:17 | 2021-12-11 15:35 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-BSRM 230 kV Ckt-1 | 2021-12-11 08:54 | 2021-12-11 16:29 | 7:35 | S/O | Due to A/M work | 0 | 0 | No interruption
| Cumilla(N)-BSRM 230 kV Ckt-2 | 2021-12-12 09:19 | 2021-12-12 19:13 | 9:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Kulaura | Kulaura-Fenchuganj 132 kV Ckt-1 | 2021-12-12 08:52 | 2021-12-12 19:21 | 10:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj S/S-Fenchuganj P/S 132 kV Ckt-1 | 2021-12-12 09:11 | 2021-12-12 17:42 | 8:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjbazar | Shahjbazar-Sreemongal 132 kV Ckt-2 | 2021-12-12 15:54 | 2021-12-12 19:24 | 3:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ashuganj (S) 230 kV Ckt-1 | 2021-12-12 15:02 | 2021-12-12 15:02 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj S/S-Fenchuganj P/P 132 kV Ckt-1 | 2021-12-13 11:14 | 2021-12-13 16:56 | 5:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Kulaura | Kulaura-Fenchuganj 132 kV Ckt-1 | 2021-12-13 10:18 | 2021-12-13 16:04 | 5:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj S/S-Fenchuganj P/P 132 kV Ckt-1 | 2021-12-14 09:33 | 2021-12-14 16:29 | 6:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Kachua 132 kV Ckt-2 | 2021-12-14 13:09 | 2021-12-14 13:09 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV Ckt-1 | 2021-12-15 08:37 | 2021-12-15 16:20 | 7:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Bibiyana-3 STG P/P 400 kV Ckt | 2021-12-17 11:47 | 2021-12-17 11:47 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV Ckt-2 | 2021-12-18 07:05 | 2021-12-18 09:01 | 1:56 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV Ckt-1 | 2021-12-18 08:09 | 2021-12-18 16:57 | 8:48 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV Ckt-1 | 2021-12-18 09:20 | 2021-12-18 18:38 | 9:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | Sreemongal-Fenchuganj 132 kV Ckt-2 | 2021-12-18 08:35 | 2021-12-18 17:02 | 8:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.Baria 132 kV Ckt-1 | 2021-12-18 14:55 | 2021-12-18 15:29 | 0:34 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ashuganj-B.Baria 132 kV Ckt-2 | 2021-12-18 15:31 | 2021-12-18 17:50 | 2:19 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV Ckt-2 | 2021-12-19 07:51 | 2021-12-19 17:15 | 9:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Kulaura | Kulaura-Fenchuganj 132 kV Ckt-2 | 2021-12-19 08:33 | 2021-12-19 16:59 | 8:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | Sreemongal-Fenchuganj 132 kV Ckt-2 | 2021-12-19 08:52 | 2021-12-19 17:12 | 8:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 132 kV Ckt-1 | 2021-12-19 12:13 | 2021-12-19 13:15 | 1:02 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ashuganj-Ghorashal 132 kV Ckt-2 | 2021-12-19 11:25 | 2021-12-19 12:10 | 0:45 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV Ckt-1 | 2021-12-20 08:27 | 2021-12-20 17:06 | 8:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Kulaura 132 kV Ckt-2 | 2021-12-20 09:12 | 2021-12-20 17:10 | 7:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | Sreemongal-Fenchuganj 132 kV Ckt-1 | 2021-12-20 08:33 | 2021-12-20 16:42 | 8:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Chattak 132 kV Ckt-1 | 2021-12-20 08:37 | 2021-12-20 16:14 | 7:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV Ckt-1 | 2021-12-21 08:58 | 2021-12-21 16:12 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | Sreemongal-Shahjibazar 132 kV Ckt-1 | 2021-12-21 08:42 | 2021-12-21 16:23 | 7:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Chattak 132 kV Ckt-1 | 2021-12-21 08:58 | 2021-12-21 16:12 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV Ckt-1 | 2021-12-22 08:56 | 2021-12-22 16:53 | 7:57 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV Ckt-1 | 2021-12-22 08:36 | 2021-12-22 16:16 | 7:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV Ckt-1 | 2021-12-23 08:41 | 2021-12-23 16:38 | 7:57 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV Ckt-1 | 2021-12-23 08:37 | 2021-12-23 17:22 | 8:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Kulaura 132 kV Ckt-1 | 2021-12-23 09:32 | 2021-12-23 16:51 | 7:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur S/S | Chandpur S/S-Chandpur Desh 132 kV Ckt-1 & 2 |  | 2021-12-24 20:15 |  |  | After maint.work | 0 | 0 | No interruption
Sreemongal | Sreemongal-Fenchuganj 132 kV Ckt-2 | 2021-12-25 08:56 | 2021-12-25 15:13 | 6:17 | S/O | Due to C/M work | 0 | 0 | No interruption
| Sreemongal-Fenchuganj 132 kV Ckt-1 | 2021-12-25 15:14 | 2021-12-25 17:35 | 2:21 | S/O | Due to C/M work | 0 | 0 | No interruption
| Sreemongal-Fenchuganj 132 kV Ckt-1 | 2021-12-26 09:16 | 2021-12-26 16:40 | 7:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjbazar | Shahjbazar-B.Baria 132 kV Ckt-1 | 2021-12-26 08:47 | 2021-12-26 16:46 | 7:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Kulaura 132 kV Ckt-1 | 2021-12-27 14:34 | 2021-12-27 17:05 | 2:31 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV Ckt-2 | 2021-12-27 08:41 | 2021-12-27 16:43 | 8:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV Ckt-2 | 2021-12-29 09:07 | 2021-12-29 19:28 | 10:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Chattak 132 kV Ckt-1 | 2021-12-29 10:30 | 2021-12-29 11:54 | 1:24 | S/O | Due to C/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV Ckt-2 | 2021-12-29 08:46 | 2021-12-29 16:37 | 7:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV Ckt-2 | 2021-12-30 10:21 | 2021-12-30 12:37 | 2:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | Feni-Baroierhat 132 kV Ckt-1 | 2021-12-30 09:11 | 2021-12-30 14:49 | 5:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV Ckt-2 | 2021-12-30 09:05 | 2021-12-30 16:42 | 7:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Kulaura 132 kV Ckt-2 | 2021-12-30 14:44 | 2021-12-30 17:16 | 2:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Shahjibazar 132 kV Ckt-3 | 2021-12-30 14:54 | 2021-12-30 16:12 | 1:18 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 372:35 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Satkhira | Satkhira-Khulna(S) 132 kV Ckt-2 | 2021-12-01 07:42 | 2021-12-01 07:42 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Gopalganj (N) 132 kV Ckt-1 & 2 | 2021-12-01 09:18 | 2021-12-01 16:54 | 7:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj(N)-Gopalganj (O) 132 kV Ckt-1 & 2 | 2021-12-03 09:00 | 2021-12-03 19:03 | 10:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Barishal 132 kV Ckt-1 | 2021-12-04 07:21 | 2021-12-04 17:07 | 9:46 | S/O | Due to A/M work | 0 | 0 | No interruption
| Barisal(N)-Barishal (S)132 kV Ckt-1 | 2021-12-05 07:21 | 2021-12-05 17:20 | 9:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna© | Khulna©-Khulna(S) 132 kV Ckt-1 | 2021-12-06 19:12 | 2021-12-06 19:12 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | Goalpara-Khulna© 132 kV Ckt-1 | 2021-12-08 08:45 | 2021-12-08 13:10 | 4:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajbari | Rajbari-Bheramara 132 kV Ckt-1 | 2021-12-08 09:33 | 2021-12-08 16:16 | 6:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | Goalpara-Khulna© 132 kV Ckt-2 | 2021-12-09 08:47 | 2021-12-09 15:08 | 6:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajbari | Rajbari-Bheramara 132 kV Ckt-1 | 2021-12-09 08:28 | 2021-12-09 15:22 | 6:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Mongla | Mongla-Narail 132 kV Ckt-2 | 2021-12-11 07:27 | 2021-12-11 14:25 | 6:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Mongla 132 kV Ckt-1 | 2021-12-11 08:42 | 2021-12-11 15:12 | 6:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal(S) | Barisal(S)-Barishal(N)132 kV Ckt-2 | 2021-12-12 07:26 | 2021-12-12 17:27 | 10:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Mongla 132 kV Ckt-1 | 2021-12-12 08:45 | 2021-12-12 17:08 | 8:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj(O) | Gopalganj(O)-Gallamari 132 kV Ckt-1 | 2021-12-12 23:26 | 2021-12-16 10:01 | 82:35 | S/O | Due to A/M work | 0 | 0 | No interruption
| Gopalganj(O)-Gopalganj (N) 132 kV Ckt-1 | 2021-12-12 23:29 | 2021-12-16 10:09 | 82:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Barishal(S)132 kV Ckt-2 | 2021-12-13 08:29 | 2021-12-13 16:59 | 8:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Magura | Magura-Narail 132 kV Ckt-1 | 2021-12-13 14:56 | 2021-12-13 14:56 | 0:00 | S/O | Due to project work | 0 | 0 | No interruption
Gopalganj(O) | Gopalganj(O)-Gopalganj (N) 132 kV Ckt-1 |  | 2021-12-14 08:22 |  | S/O | After maint.work | 0 | 0 | No interruption
| Gopalganj(O)-Faridpur 132 kV Ckt-1 | 2021-12-13 08:47 | 2021-12-13 16:18 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna© | Khulna©-NWPGCL 132 kV Ckt-1 | 2021-12-15 09:34 | 2021-12-15 13:38 | 4:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj(O) | Gopalganj(O)-Gallamari 132 kV Ckt | 2021-12-17 08:04 | 2021-12-17 17:50 | 9:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Khulna(C) 132 kV Ckt-2 | 2021-12-19 08:10 | 2021-12-19 08:10 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna© | Khulna©-Satkhira 132 kV Ckt-2 | 2021-12-18 09:45 | 2021-12-18 11:47 | 2:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Rajbari 132 kV Ckt-1 | 2021-12-19 08:15 | 2021-12-19 16:15 | 8:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | Goalpara-Khulna 225 MW.P.P 132 kV Ckt | 2021-12-19 09:52 | 2021-12-19 15:21 | 5:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj(O) | Gopalganj(O)-Gallamari 132 kV Ckt-2 | 2021-12-19 08:19 | 2021-12-19 15:41 | 7:22 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV Ckt-2 | 2021-12-19 09:07 | 2021-12-19 19:02 | 9:55 | S/O | Due to A/M work | 0 | 0 | No interruption
| Khulna(S)-Gallamari 132 kV Ckt-1 & 2 |  | 2021-12-20 11:07 |  | S/O | After maint.work | 0 | 0 | No interruption
| Khulna(S)-Khulna(C) 132 kV Ckt-2 | 2021-12-20 09:06 | 2021-12-20 15:28 | 6:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Rajbari 132 kV Ckt-1 | 2021-12-20 08:30 | 2021-12-20 16:38 | 8:08 | S/O | Due to D/W work | 0 | 0 | No interruption
| Faridpur-Rajbari 132 kV Ckt-2 | 2021-12-20 16:56 | 2021-12-20 19:36 | 2:40 | S/O | Due to protection test | 0 | 0 | No interruption
Khulna© | Khulna©-NWPGCL 132 kV Ckt-1 | 2021-12-21 09:35 | 2021-12-21 11:40 | 2:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Gollamari 132 kV Ckt-1 | 2021-12-21 08:37 | 2021-12-21 16:16 | 7:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Noapara | Noapara-Jashore 132 kV Ckt-1 | 2021-12-21 08:28 | 2021-12-21 14:45 | 6:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna© | Khulna©-NWPGCL 132 kV Ckt-2 | 2021-12-21 11:40 | 2021-12-21 12:35 | 0:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Shariatpur 132 kV Ckt-2 | 2021-12-21 11:52 | 2021-12-21 13:54 | 2:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Gopalganj (N) 132 kV Ckt-2 | 2021-12-22 08:46 | 2021-12-22 15:56 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Gollamari 132 kV Ckt-2 | 2021-12-22 09:38 | 2021-12-22 14:58 | 5:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Mongla | Mongla-Bagerhat 132 kV Ckt-2 | 2021-12-22 07:12 | 2021-12-22 08:30 | 1:18 | S/O | Due to D/W work | 0 | 0 | No interruption
Barisal(O) | Barisal(O)-Barishal Summit 132 kV Ckt- | 2021-12-24 07:55 | 2021-12-24 07:55 | 0:00 | S/O |  | 0 | 0 | No interruption
Bagerhat | Bagerhat-Mongla 132 kV Ckt-2 |  | 2021-12-24 09:51 |  | S/O | After maint.work | 0 | 0 | No interruption
Gopalganj(O) | Gopalganj(O)-Gopalganj (N) 132 kV Ckt-1 |  | 2021-12-24 12:43 |  | S/O |  | 0 | 0 | No interruption
| Gopalganj(O)-Gallamari 132 kV Ckt-1 |  | 2021-12-24 12:45 |  | S/O | After maint.work | 0 | 0 | No interruption
Barisal(O) | Barisal(O)-Barishal Summit 132 kV Ckt- | 2021-12-25 08:30 | 2021-12-25 15:42 | 7:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Gopalganj (N) 132 kV Ckt-1 & 2 | 2021-12-25 09:23 | 2021-12-25 20:38 | 11:15 | S/O | Due to D/W work | 0 | 0 | No interruption
Barisal(O) | Barisal(O)-Barishal Summit 132 kV Ckt- | 2021-12-26 08:35 | 2021-12-26 16:47 | 8:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Gopalganj (N) 132 kV Ckt-2 | 2021-12-26 09:05 | 2021-12-26 14:44 | 5:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Gopalganj (N) 132 kV Ckt-1 & 2 | 2021-12-26 08:33 | 2021-12-26 16:13 | 7:40 | S/O | Due to D/W work | 0 | 0 | No interruption
Barisal(S) | Barisal(S)-Barishal Summit 132 kV Ckt- | 2021-12-27 07:36 | 2021-12-27 15:49 | 8:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Gopalganj (N) 132 kV Ckt-2 | 2021-12-27 09:34 | 2021-12-27 17:36 | 8:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV Ckt | 2021-12-29 08:47 | 2021-12-29 16:16 | 7:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur S/S | Faridpur S/S-Faidpur P/S 132 kV Ckt | 2021-12-29 09:06 | 2021-12-29 15:53 | 6:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | Goalpara-KPCL-1P/S 132 kV Ckt-2 | 2021-12-30 09:40 | 2021-12-30 14:55 | 5:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | Faridpur -Faridpur P/S 132 kV Ckt | 2021-12-30 09:11 | 2021-12-30 15:48 | 6:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV Ckt | 2021-12-30 08:43 | 2021-12-30 15:28 | 6:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Gopalganj (N) 132 kV Ckt-2 | 2021-12-31 08:38 | 2021-12-31 15:22 | 6:44 | S/O | Due to C/M work | 0 | 0 | No interruption
| Faridpur-Gopalganj (N) 132 kV Ckt-2 | 2021-12-31 15:47 | 2021-12-31 16:24 | 0:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Magura | Magura-Narail 132 kV Ckt-1 |  | 2021-12-31 16:19 |  | S/O | After maint.work | 0 | 0 | No interruption
|  |  | Total : | 188:57 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Ishurdi | Ishurdi-Baghabari 230 kV Ckt-1 | 2021-12-05 08:20 | 2021-12-05 18:02 | 9:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara HVDC | Bheramara HVDC-Bahrampur 400 kV Ckt-2 | 2021-12-05 09:46 | 2021-12-05 16:20 | 6:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Baghabari | Baghabari-Ishurdi 230 kV Ckt-2 | 2021-12-08 09:20 | 2021-12-08 16:48 | 7:28 | S/O | Due to A/M work | 0 | 0 | No interruption
| Jessore-Noapara 132 kV Ckt-1 | 2021-12-20 08:24 | 2021-12-20 14:22 | 5:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Jessore | Jessore-Noapara 132 kV Ckt-1 | 2021-12-22 08:24 | 2021-12-22 14:22 | 5:58 | S/O | Due to A/M work | 0 | 0 | No interruption
| Jessore-Noapara 132 kV Ckt-2 | 2021-12-22 08:31 | 2021-12-22 14:42 | 6:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara | Bheramara-Rajshahi 132 kV Ckt-2 | 2021-12-23 09:06 | 2021-12-23 18:51 | 9:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Jessore | Jessore-Noapara 132 kV Ckt-2 | 2021-12-23 08:48 | 2021-12-23 15:30 | 6:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara | Bheramara-Rajshahi 132 kV Ckt-1 | 2021-12-23 20:42 | 2021-12-23 20:50 | 0:08 | S/O | Due to protection test | 0 | 0 | No interruption
Baghabari | Baghabari-Bhangura 132 kV Ckt-1 | 2021-12-24 08:58 | 2021-12-24 15:01 | 6:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV Ckt-1 | 2021-12-26 09:40 | 2021-12-26 15:39 | 5:59 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ishurdi-HVDC Bheramara 230 kV Ckt-4 | 2021-12-28 09:52 | 2021-12-28 17:42 | 7:50 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ishurdi-Ghorashal 230 kV Ckt-2 | 2021-12-28 08:36 | 2021-12-28 16:37 | 8:01 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ishurdi-Natore 132 kV Ckt-2 | 2021-12-28 11:54 | 2021-12-28 15:03 | 3:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Baghabari | Baghabari-Sirajganj 230 kV Ckt-1 | 2021-12-28 14:36 | 2021-12-28 15:59 | 1:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ruppur 132 kV Ckt-1 | 2021-12-29 08:43 | 2021-12-29 18:10 | 9:27 | S/O | Due to SCADA work | 0 | 0 | No interruption
| Ishurdi-Ruppur 132 kV Ckt-2 | 2021-12-30 08:24 | 2021-12-30 14:40 | 6:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara | Bheramara -Bheramara G.K 132 kV Ckt-2 | 2021-12-30 09:38 | 2021-12-30 11:18 | 1:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bheramara -Bheramara G.K 132 kV Ckt-2 | 2021-12-30 12:31 | 2021-12-30 12:31 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 375:11 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Bogura | Bogura-Naogaon 132 kV Ckt-1 | 2021-12-01 07:55 | 2021-12-01 16:26 | 8:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | Barapukuria -Barapukuria P/S 230 kV Ckt-1 | 2021-12-01 08:38 | 2021-12-01 17:02 | 8:24 | S/O | Due to A/M work | 0 | 0 | No interruption
| Barapukuria -Barapukuria P/S 230 kV Ckt-2 | 2021-12-02 09:09 | 2021-12-02 14:18 | 5:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura-Naogaon 132 kV Ckt-1 | 2021-12-02 08:28 | 2021-12-02 16:20 | 7:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | Naogaon-Niyamatpur 132 kV Ckt | 2021-12-03 08:08 | 2021-12-03 16:07 | 7:59 | S/O | Due to A/M work | 10 | 79.8333 | Power interruption
Barapukuria | Barapukuria -Saidpur 132 kV Ckt-2 | 2021-12-04 08:14 | 2021-12-04 16:55 | 8:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | Naogaon-Niyamatpur 132 kV Ckt | 2021-12-04 08:34 | 2021-12-04 16:32 | 7:58 | S/O | Due to A/M work | 10 | 79.6667 | Power interruption
Bogura | Bogura-Naogaon 132 kV Ckt-2 | 2021-12-05 08:43 | 2021-12-05 16:25 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bogura-Naogaon 132 kV Ckt-2 | 2021-12-06 08:25 | 2021-12-06 15:35 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | Barapukuria -Saidpur 132 kV Ckt-2 | 2021-12-06 08:38 | 2021-12-06 16:55 | 8:17 | S/O | Due to A/M work | 0 | 0 | No interruption
| Barapukuria -Bogura 132 kV Ckt-1 | 2021-12-08 08:01 | 2021-12-08 16:28 | 8:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | Natore-Rajshahi 132 kV Ckt-1 | 2021-12-08 08:10 | 2021-12-08 15:47 | 7:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | Barapukuria -Bogura 230 kV Ckt-1 | 2021-12-09 08:20 | 2021-12-09 16:22 | 8:02 | S/O | Due to A/M work | 0 | 0 | No interruption
| Barapukuria -Bogura 230 kV Ckt-1 | 2021-12-10 08:33 | 2021-12-10 15:38 | 7:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhangura | Bhangura-Baghabari 132 kV Ckt | 2021-12-11 08:46 | 2021-12-11 17:17 | 8:31 | S/O | Due to D/W work | 0 | 0 | No interruption
Natore | Natore-Rajshahi 132 kV Ckt-1 | 2021-12-11 08:42 | 2021-12-11 14:56 | 6:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura -B.Pukuria 230 kV Ckt-2 | 2021-12-11 08:03 | 2021-12-11 16:59 | 8:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | Barapukuria -Bogura 230 kV Ckt-2 | 2021-12-12 08:18 | 2021-12-12 16:25 | 8:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | Natore-Rajshahi 132 kV Ckt-2 | 2021-12-12 08:24 | 2021-12-12 16:42 | 8:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Rangpur 132 kV Ckt-1 | 2021-12-12 14:22 | 2021-12-12 17:07 | 2:45 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura | Bogura -B.Pukuria 230 kV Ckt-2 | 2021-12-13 08:25 | 2021-12-13 15:43 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | Natore-Rajshahi 132 kV Ckt-2 | 2021-12-13 08:05 | 2021-12-13 15:46 | 7:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Barapukuria 132 kV Ckt-1 | 2021-12-13 08:49 | 2021-12-13 11:14 | 2:25 | S/O | Due to A/M work | 0 | 0 | No interruption
| Saidpur-Purbasadipur 132 kV Ckt-1 | 2021-12-13 11:18 | 2021-12-13 13:09 | 1:51 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura (New) | Bogura (New)-Bogura(O) 132 kV Ckt-2 | 2021-12-14 08:20 | 2021-12-14 10:02 | 1:42 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | C.nawabganj-Amnura 132 kV Ckt-2 | 2021-12-14 08:25 | 2021-12-14 14:45 | 6:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | Natore-Rajshahi 132 kV Ckt-2 | 2021-12-14 08:20 | 2021-12-14 15:45 | 7:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Barapukuria 132 kV Ckt-1 | 2021-12-14 08:15 | 2021-12-14 12:09 | 3:54 | S/O | Due to A/M work | 0 | 0 | No interruption
| Rangpur-Barapukuria 132 kV Ckt-2 | 2021-12-14 12:12 | 2021-12-14 15:30 | 3:18 | S/O | Due to C/M work | 0 | 0 | No interruption
C.nawabganj | C.nawabganj P/P-Amnura 132 kV Ckt | 2021-12-15 08:54 | 2021-12-15 17:22 | 8:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Rajshahi NPSL 132 kV Ckt | 2021-12-15 08:16 | 2021-12-15 15:51 | 7:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | Natore-Rajshahi 132 kV Ckt-2 | 2021-12-15 08:20 | 2021-12-15 15:45 | 7:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura(N) | Bogura(N)-Bogura(O) 132 kV Ckt-1 | 2021-12-17 09:00 | 2021-12-17 09:00 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Rajshahi S/S | Rajshahi S/S-Katakhali P/P 132 kV Ckt | 2021-12-18 08:42 | 2021-12-18 12:18 | 3:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV Ckt-1 | 2021-12-18 08:18 | 2021-12-18 15:31 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Amnura S/S | Amnura S/S-Amnura P.P 132 kV Ckt | 2021-12-19 08:20 | 2021-12-19 13:58 | 5:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura-Natore 132 kV Ckt-1 | 2021-12-19 08:41 | 2021-12-19 17:17 | 8:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV Ckt-1 | 2021-12-19 08:30 | 2021-12-19 16:22 | 7:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura(N) | Bogura(N)-Sherpur 132 kV Ckt-2 | 2021-12-19 14:40 | 2021-12-19 16:54 | 2:14 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bogura(N)-Bogura(O) 132 kV Ckt-2 | 2021-12-20 09:16 | 2021-12-20 16:01 | 6:45 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bogura-Natore 132 kV Ckt-1 | 2021-12-20 08:18 | 2021-12-20 16:42 | 8:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV Ckt-1 | 2021-12-20 08:29 | 2021-12-20 16:07 | 7:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-HVDC Bheramara 132 kV Ckt-1 |  | 2021-12-21 08:55 |  | S/O | After maint.work | 0 | 0 | No interruption
Bogura(N) | Bogura(N)-Bogura Confidence 132 kV Ckt-1 | 2021-12-21 09:45 | 2021-12-21 15:45 | 6:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangpur | Rangpur-Barapukuria 132 kV Ckt-2 | 2021-12-21 09:52 | 2021-12-21 15:35 | 5:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV Ckt-2 | 2021-12-21 08:25 | 2021-12-21 16:35 | 8:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura-Natore 132 kV Ckt-2 | 2021-12-21 08:03 | 2021-12-21 16:25 | 8:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV Ckt-2 | 2021-12-22 08:20 | 2021-12-22 16:08 | 7:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura(N) | Bogura(N)-Bogura(O) 132 kV Ckt-2 | 2021-12-22 10:44 | 2021-12-22 10:44 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura(N) | Bogura(N)-Confidence 132 kV Ckt | 2021-12-22 11:18 | 2021-12-22 15:54 | 4:36 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogura(N)-Sherpur 132 kV Ckt-2 | 2021-12-22 10:42 | 2021-12-22 14:04 | 3:22 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogura(N)-Sherpur 132 kV Ckt-1 | 2021-12-22 10:41 | 2021-12-22 14:03 | 3:22 | S/O | Due to D/W work | 0 | 0 | No interruption
Natore | Natore-Bpgura(O) 132 kV Ckt-1 | 2021-12-22 13:05 | 2021-12-22 14:25 | 1:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi S/S | Rajshahi S/S-Rajshahi P/P 132 kV Ckt | 2021-12-23 08:16 | 2021-12-23 15:50 | 7:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV Ckt-2 | 2021-12-23 08:21 | 2021-12-23 14:42 | 6:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura(O) | Bogura(O)-Bogura(O) 132 kV Ckt-2 | 2021-12-23 10:44 | 2021-12-23 18:29 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura(N) | Bogura(N)-Confidence 132 kV Ckt-2 | 2021-12-24 06:31 | 2021-12-24 10:12 | 3:41 | S/O | Due to D/W work | 0 | 0 | No interruption
Rajshahi S/S | Rajshahi S/S-HVDC Bheramara 230 kV Ckt-1 & 2 | 2021-12-25 08:11 | 2021-12-25 15:03 | 6:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Baghabari 230 kV CKt-1 | 2021-12-26 11:09 | 2021-12-26 17:10 | 6:01 | S/O | Due to D/W work | 0 | 0 | No interruption
Purbasadipur | Purbasadipur -Thakurgaon 132 kV Ckt | 2021-12-27 08:30 | 2021-12-27 16:23 | 7:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | Palashbari-Mohastanghor 132 kV Ckt-1 | 2021-12-28 08:54 | 2021-12-28 15:31 | 6:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | Purbasadipur -Thakurgaon 115 MW P.P 132 kV Ckt-1 | 2021-12-28 08:25 | 2021-12-28 16:26 | 8:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Thaurgaon | Thaurgaon-Thaurgaon 115 MW 132 kV Ckt-1 | 2021-12-28 08:26 | 2021-12-28 16:42 | 8:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Mohastangarh | Mohastangarh-Palshabri 132 kV Ckt-1 | 2021-12-29 09:08 | 2021-12-29 15:14 | 6:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | Purbasadipur -Thakurgaon 132 kV Ckt-2 | 2021-12-29 08:40 | 2021-12-29 16:56 | 8:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Thaurgaon | Thaurgaon-Thaurgaon P/S 132 kV Ckt-2 | 2021-12-29 09:02 | 2021-12-29 16:45 | 7:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | Palashbari-Mohastanghor 132 kV Ckt-2 | 2021-12-30 07:39 | 2021-12-30 07:39 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | Purbasadipur -Thakurgaon P.P 132 kV Ckt-2 | 2021-12-30 09:26 | 2021-12-30 11:40 | 2:14 | S/O | Due to D/W work | 0 | 0 | No interruption
Thaurgaon | Thaurgaon-Thaurgaon P/S 132 kV Ckt-2 | 2021-12-30 08:58 | 2021-12-30 16:15 | 7:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Purbasadipur | Purbasadipur -Thakurgaon P.P 132 kV Ckt-2 | 2021-12-31 08:40 | 2021-12-31 16:13 | 7:33 | S/O | Due to D/W work | 0 | 0 | No interruption
Thaurgaon | Thaurgaon-Thaurgaon P/S 132 kV Ckt-2 | 2021-12-31 08:40 | 2021-12-31 15:37 | 6:57 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 438:53 |  | Unserved Energy: |  | 159.5
Others :
Maniknagar | Maniknagar-Matuail 132 kV Ckt | 2021-12-04 09:10 | 2021-12-04 16:12 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Maniknagar-Matuail 132 kV Ckt | 2021-12-17 08:24 | 2021-12-17 16:22 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
| Maniknagar-Narinda 132 kV Ckt-1 | 2021-12-21 10:02 | 2021-12-21 19:18 | 7:58 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 2284:55 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.
r) Sirajganj-Baghabari 230 kV Ckt-1 was under shut down from 11:09 to 17:10 for D/W.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:December 2021
| Area | Previous Month (November' 2021) |  |  |  | Current Month (December '2021)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 11 | 2 | 175 | 188 | 8 | - | 163 | 171
2 | Dhaka (South) Grid Circle. | 14 | - | 96 | 110 | 15 | - | 110 | 125
3 | Chattogram Grid Circle. | 8 | 2 | 106 | 116 | 11 | 1 | 78 | 90
4 | Cumilla Grid Circle. | 11 | 3 | 129 | 143 | 13 | 4 | 96 | 113
5 | Khulna Grid Circle. | 6 | 2 | 87 | 95 | 7 | 3 | 90 | 100
6 | HVDC Grid Circle | 3 | - | 36 | 39 | 2 | 1 | 43 | 46
7 | Bogura Grid Circle. | 6 | - | 143 | 149 |  | 3 | 119 | 122
8 | Others | 1 | - | 1 | 2 |  |  | 3 | 3
9 | Total | 60 | 9 | 773 | 842 | 56 | 12 | 702 | 770
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:December 2021
| Area | Previous Month (November' 2021) |  |  |  | Current Month (December '2021)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 73.91 |  | 218.32 | 292.23 | - | - | 1028.58 | 1028.58
2 | Dhaka (South) Grid Circle. | 124.23 | - | - | 124.23 | 34.93 |  | 109.67 | 144.6
3 | Chattogram Grid Circle. | 78.69 | - | - | 78.69 | 223.06 | 122.67 | 95.8 | 441.53
4 | Cumilla Grid Circle. | 2.88 | 12 | 100.83 | 115.71 | 16.97 | - | - | 16.97
5 | Khulna Grid Circle. | 91.18 | 8.8 | 43.63 | 143.61 | 3.6 |  | 353.25 | 356.85
6 | HVDC Grid Circle | - | - | 142.67 | 142.67 | 12.67 | 5.67 | 423.37 | 441.71
7 | Bogura Grid Circle. | 59.2 | 15.73 | 838.5 | 913.43 |  | 522.33 | 462.83 | 985.16
8 | Others | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Total | 430.09 | 36.53 | 1343.95 | 1810.57 | 291.23 | 650.67 | 2473.5 | 3415.4
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:December 2021
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | - | 2 | 2 | - | - | 2 | 1028.5833
2 | Dhaka (South) | 5031.6 | 2 | 1 | 3 | 1 | 1 | 1 | 144.6
3 | Chattogram | 2042 | 2 | 2 | 4 | 1 | - | 3 | 186.83
4 | Khulna | 2434 | 1 | 3 | 4 | 1 | 1 | 2 | 356.85
5 | HVDC | 5954.3 | 2 | 2 | 4 | 1 | 1 | 2 | 441.7
6 | Bogura | 3145.6 | 2 | 4 | 6 | 1 |  | 5 | 825.7
7 | Cumilla | 2981 | - | - | - | - | - | - | -
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 2984.2633
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 99.98%
4 | Khulna | 99.9%
5 | HVDC | 100% | [6 empty] | Executive Engineer
6 | Bogura | 99.86% | [6 empty] | Information Management Division
7 | Cumilla | 99.97% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:December 2021
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | - | - | - | - | - | - | -
2 | Dhaka (South) | 990.29 |  | - | - | - | - | - | - | -
3 | Chattogram | 917 | - | 2 |  | 2 | 2 |  |  | 254.7
4 | Khulna | 1238.4 | - | - | - | - | - | - | - | - | -
5 | HVDC | 1325 | - | - | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - |  | 2 | 2 |  |  | 2 | 159.5
7 | Cumilla | 1648.16 | - | 3 |  | 3 | 3 |  |  | 16.97
8 | Others | - |  | - | - | - | - | - | - | -
| Total | 10176.6215 | 0 | [6 empty] | 431.17
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 99.97%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 99.99% | [7 empty] | Executive Engineer
6 | Bogura | 99.98% | [7 empty] | Information Management Division
7 | Cumilla | 99.98% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:December 2021
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2021-12-18 | 12 | - | 1 | 34 min | 1 | 1hr'55 min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:December 2021
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Kodda | 2 | 8:07 | 85 | 689.9167 | Due to S/D of 132/33 kV Transformers T3 & T4
|  | 8:28 | 40 | 338.6667 | Due to S/D of 132/33 kV Transformers-T1 & T2 with 33 kV Bus
Rampura | 1 | 0:34 | 40 | 22.6667 | Due to tripping of 230/132 kV Transformer T-01
Keraniganj | 1 | 0:23 | 32 | 12.2667 | Due to tripping of 132/33 kV Transformers-T1 & T2
Siddhirganj | 1 | 5:29 | 20 | 109.6667 | Due to S/D of 132/33 kV Transformer T2
Cox'sbazar | 2 | 3:41 | 22 | 81.0333 | Due to 33 kV feeder fault of 132/33 kV Transformer T3
|  | 0:24 | 25 | 10
Khulshi |  | 0:17 | 466 | 132.0333 | Due to tripping of Khulshi-Modern Steel 132 kV Ckt
Sikalbaha(O) |  | 1:55 | 64 | 122.6667 | Due to bursting of L/A
Halishahar |  | 1:38 | 25 | 40.8333 | Due to S/D of 132/33 kV Transformers T1 & T2
Patanga |  | 1:37 | 34 | 54.9667
Sylhet | 3 | 0:21 | 20 | 7 | Due to tripping of Sylhet-Fenchuganj 132 kV Ckt
|  | 0:13 | 24 | 5.2 | Due to tripping of Sylhet-Fenchuganj -Bibyanibazar 132 kV Ckt
|  | 0:13 | 22 | 4.7667 | Due to tripping of Sylhet-Fenchuganj 132 kV Ckt
Gallamari | 1 | 0:06 | 36 | 3.6 | Due to tripping of 132/33 kV transformers T-1 & T2
Mongla | 1 | 9:09 | 20 | 183 | Due to S/D of 132 kV Full Bus
Faridpur | 1 | 0:58 | 30 | 29 | Due to S/D of 132/33 kV TransformerT2
Bhola | 1 | 5:39 | 25 | 141.25 | Due to S/D of 230/33 kV transformer T01
Banapole | 1 | 0:20 | 38 | 12.6667 | Due to tripping of 132/33 kV transformers T-1 & T2
| 1 | 0:34 | 10 | 5.6667 | Due to red-hot maint.of 132/33 kV Transformer T1
Jashore | 1 | 3:52 | 61 | 235.8667 | Due to S/D of 132 kV Bus-1 & 2
Shahjadpur | 1 | 7:30 | 25 | 187.5 | Due to S/D of 132 kV Bus
Purbasadipur | 1 | 0:20 | 25 | 8.3333 | Due to tripping of 33 kV feeder fault
Naogaon | 1 | 21:25 | 24 | 514
Jaldhaka | 1 | 1:02 | 8 | 8.2667 | Due to S/D of 132/33 kV TransformerT1
Rajshahi(O) | 1 | 3:26 | 65 | 223.1667 | Due to S/D of 33 kV full Bus
Purbasadipur | 1 | 3:12 | 20 | 64 | Due to S/D of 132/33 kV TransformerT2
Naogaon | 3 | 1:08 | 7 | 7.9333
|  | 7:59 | 10 | 79.8333 | Due to S/D of Naogaon-Niyamatpur 132 kV Ckt
|  | 7:58 | 10 | 79.6667
| Total Unserved energy : |  |  | 3415.4333 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: December '2021
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 114 | 1 | 2021-12-01 | 12:00
2 | Munsiganj | 70 | 24 | 2021-12-01 | 21:00
3 | Sonargaon | 72 | 23 | 2021-12-01 | 11:00
4 | Shyampur | 176 | 21 | 2021-12-01 | 10:00
5 | Bhulta | 177 | 21 | 2021-12-01 | 18:30
6 | Madanganj | 56 | 2 | 2021-12-01 | 18:30
7 | Shitalakhya | 106 | 1 | 2021-12-01 | 12:00
8 | Rahim steel | 30 | 6 | 2021-12-01 | 9:00
9 | Matuail | 60 | 9 | 2021-12-01 | 10:00
10 | Ghorasal | 88 | 30 | 2021-12-01 | 18:00
11 | Narsingdi | 128 | 5 | 2021-12-01 | 19:00
12 | Haripur (SBU) | 136 | 5 | 2021-12-01 | 17:00
13 | Sreenagar | 28 | 16 | 2021-12-01 | 20:00
14 | Ullon | 46 | 4 | 2021-12-01 | 18:00
15 | Hasnabad | 78 | 8 | 2021-12-01 | 18:00
16 | Magbazar | 71 | 1 | 2021-12-01 | 13:00
17 | Maniknagar | 56 | 1 | 2021-12-01 | 13:00
18 | Bangabhaban | 8 | 1 | 2021-12-01 | 10:00
19 | Narinda | 64 | 5 | 2021-12-01 | 12:00
20 | Dhanmondi | 149 | 9 | 2021-12-01 | 13:00
21 | Lalbag | 86 | 2 | 2021-12-01 | 13:00
22 | Madartek | 52 | 2 | 2021-12-01 | 18:00
23 | Dhaka University | 26 | 8 | 2021-12-01 | 13:00
24 | Aftabnagar | 16 | 6 | 2021-12-01 | 12:00
25 | Fatullah | 52 | 1 | 2021-12-01 | 12:00
26 | Nawabganj | 33 | 3 | 2021-12-01 | 21:00
27 | Mirpur | 94 | 1 | 2021-12-01 | 12:00
28 | Kalyanpur | 66 | 1 | 2021-12-01 | 17:00
29 | Gulshan | 86 | 9 | 2021-12-01 | 18:00
30 | Uttara | 63 | 1 | 2021-12-01 | 13:00
31 | Uttara(new) | 22 | 30 | 2021-12-01 | 13:00
32 | Kamrangirchar | 96 | 5 | 2021-12-01 | 13:00
33 | Savar | 147 | 5 | 2021-12-01 | 18:00
34 | Bhasantec | 88 | 4 | 2021-12-01 | 18:00
35 | Agargaon | 59 | 8 | 2021-12-01 | 13:00
36 | Satmosjid | 76 | 2 | 2021-12-01 | 19:00
37 | Tongi | 108 | 28 | 2021-12-01 | 12:00
38 | Kabirpur | 224 | 1 | 2021-12-01 | 18:00
39 | Basundhara | 174 | 2 | 2021-12-01 | 14:00
40 | Manikganj | 143 | 2 | 2021-12-01 | 3336:00
41 | Joydevpur | 78 | 19 | 2021-12-01 | 24:00
42 | New Tongi | 257 | 11 | 2021-12-01 | 15:00
43 | Kodda | 90 | 29 | 2021-12-01 | 12:00
44 | Dhamrai | 94 | 9 | 2021-12-01 | 18:30
45 | Rajendrapur | 12 | 1 | 2021-12-01 | 18:30
46 | Valuka | 102 | 4 | 2021-12-01 | 18:00
47 | Tangail | 146 | 2 | 2021-12-01 | 18:00
48 | Mymensing | 158 | 14 | 2021-12-01 | 18:00
49 | Kishorganj | 94 | 14 | 2021-12-01 | 21:00
50 | Netrokona | 84 | 30 | 2021-12-01 | 18:30
51 | Jamalpur | 105 | 28 | 2021-12-01 | 19:00
52 | Sherpur | 106 | 29 | 2021-12-01 | 18:00
53 | Srimongal | 44 | 7 | 2021-12-01 | 18:00
Page: 2/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: December '2021
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
54 | Shahjibazar | 87 | 13 | 2021-12-01 | 18:00
56 | Fenchuganj | 34 | 14 | 2021-12-01 | 18:30
57 | Kulawara | 30 | 1 | 2021-12-01 | 18:00
58 | Sylhet | 97 | 20 | 2021-12-01 | 18:00
59 | Chatak | 18 | 1 | 2021-12-01 | 20:00
60 | Sunamganj | 33 | 23 | 2021-12-01 | 18:00
61 | Bianibazar | 40 | 20 | 2021-12-01 | 19:30
62 | Cumilla (S) | 111 | 5 | 2021-12-01 | 19:30
63 | Cumilla(N) | 95 | 27 | 2021-12-01 | 18:30
64 | Chandpur | 50 | 9 | 2021-12-01 | 19:30
65 | Feni | 85 | 1 | 2021-12-01 | 18:00
66 | Chowmuhani | 134 | 29 | 2021-12-01 | 20:00
67 | Ashuganj | 40 | 30 | 2021-12-01 | 12:00
68 | Daudkandi | 98 | 9 | 2021-12-01 | 19:00
69 | B.Baria | 102 | 1 | 2021-12-01 | 19:30
70 | Ramganj | 60 | 15 | 2021-12-01 | 20:00
71 | Chaddagram | 40 | 29 | 2021-12-01 | 10:00
72 | PHP | 10 | 14 | 2021-12-01 | 10:00
73 | Kochua | 42 | 17 | 2021-12-01 | 20:00
74 | Madanhat | 50 | 7 | 2021-12-01 | 18:30
75 | Hathazari | 77 | 8 | 2021-12-01 | 19:30
76 | Khulshi | 167 | 4 | 2021-12-01 | 13:00
77 | Halishahar | 89 | 12 | 2021-12-01 | 17:00
78 | Baraulia | 149 | 1 | 2021-12-01 | 13:00
79 | Sikalbaha | 36 | 1 | 2021-12-01 | 18:00
80 | Dohazari | 80 | 31 | 2021-12-01 | 18:00
81 | Cox'sbazar | 90 | 3 | 2021-12-01 | 13:00
82 | Chandraghona | 34 | 22 | 2021-12-01 | 13:00
83 | Kaptai | 20 | 19 | 2021-12-01 | 1:00
84 | A. Khaer Stl. | 8 | 6 | 2021-12-01 | 18:00
85 | Bakulia | 95 | 1 | 2021-12-01 | 18:00
86 | Julda | 26 | 23 | 2021-12-01 | 11:00
87 | TK chemical | 24.5 | 18 | 2021-12-01 | 18:00
88 | Modern Steel | 9 | 2 | 2021-12-01 | 9:00
89 | Shahmirpur | 39 | 26 | 2021-12-01 | 18:00
90 | Khagrachhari | 24 | 18 | 2021-12-01 | 18:30
91 | Matarbari | 29 | 31 | 2021-12-01 | 8:00
92 | Baroiar Hat | 56 | 26 | 2021-12-01 | 13:00
93 | Rangamati | 10 | 1 | 2021-12-01 | 18:00
94 | Abul Khair 230 | 168.9 | 22 | 2021-12-01 | 13:00
95 | BSRM | 168 | 15 | 2021-12-01 | 7:00
96 | GPH Ispat | 99 | 1 | 2021-12-01 | 18:00
97 | Goalpara | 26 | 29 | 2021-12-01 | 13:00
98 | Central s/s | 84 | 19 | 2021-12-01 | 18:00
99 | Noapara | 42 | 11 | 2021-12-01 | 20:00
100 | Jashore | 80 | 5 | 2021-12-01 | 18:00
101 | Benapol | 40 | 2 | 2021-12-01 | 18:00
101 | Jhenidah | 84 | 4 | 2021-12-01 | 18:30
102 | Bottail | 99 | 28 | 2021-12-01 | 19:30
Page: 3/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: December '2021
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
103 | G.K Project | 41 | 31 | 2021-12-01 | 18:30
104 | Faridpur | 110 | 14 | 2021-12-01 | 19:00
105 | Madaripur | 71 | 20 | 2021-12-01 | 20:00
106 | Sariatpur | 52 | 23 | 2021-12-01 | 19:30
107 | Gopalganj | 70 | 23 | 2021-12-01 | 18:30
108 | Bagerhat | 80 | 30 | 2021-12-01 | 18:00
109 | Mongla | 48 | 20 | 2021-12-01 | 12:00
110 | Satkhira | 77 | 4 | 2021-12-01 | 18:00
111 | Gallamari | 48 | 30 | 2021-12-01 | 13:00
112 | Magura | 40 | 1 | 2021-12-01 | 18:00
113 | Norail | 37 | 18 | 2021-12-01 | 18:00
114 | Chuadanga | 65 | 5 | 2021-12-01 | 18:00
115 | Barsal(N) | 34 | 10 | 2021-12-01 | 18:30
116 | Barsal(S) | 88 | 14 | 2021-12-01 | 13:00
117 | Patuakhali | 79 | 5 | 2021-12-01 | 21:00
118 | Bhandaria | 42 | 27 | 2021-12-01 | 20:00
119 | Borguna | 12 | 1 | 2021-12-01 | 20:00
120 | Borhan Uddin | 40 | 31 | 2021-12-01 | 18:00
121 | Ishurdi | 55 | 4 | 2021-12-01 | 18:00
122 | Ruppur Paromanobik | 4 | 6 | 2021-12-01 | 11:00
123 | Natore | 90 | 11 | 2021-12-01 | 18:00
124 | Bogura | 114 | 15 | 2021-12-01 | 18:30
125 | Naogaon | 85 | 7 | 2021-12-01 | 18:00
126 | Rajshahi | 99 | 11 | 2021-12-01 | 20:00
127 | Rajshahi New | 17 | 11 | 2021-12-01 | 11:00
128 | C.Nawabganj | 48 | 12 | 2021-12-01 | 13:00
129 | Amnura | 42 | 3 | 2021-12-01 | 18:00
130 | Pabna | 92 | 11 | 2021-12-01 | 18:00
131 | Shahjadpur | 75 | 1 | 2021-12-01 | 18:30
132 | Serajganj | 69 | 8 | 2021-12-01 | 19:00
133 | Niyamatpur | 48 | 31 | 2021-12-01 | 19:00
134 | Joypurhat | 50 | 13 | 2021-12-01 | 18:00
135 | Sherpur(Bogura) | 48 | 1 | 2021-12-01 | 18:00
136 | Mohastangar | 50 | 6 | 2021-12-01 | 18:00
137 | Bangura | 23 | 2 | 2021-12-01 | 18:30
138 | Rangpur | 104 | 21 | 2021-12-01 | 18:00
139 | Lalmonirhat | 43 | 19 | 2021-12-01 | 18:00
140 | Saidpur | 87 | 23 | 2021-12-01 | 19:00
141 | Purbasadipur | 97 | 11 | 2021-12-01 | 18:00
142 | Thakurgaon | 69 | 4 | 2021-12-01 | 18:00
143 | Palshbari | 90 | 9 | 2021-12-01 | 18:00
144 | Barapukuria | 51 | 21 | 2021-12-01 | 19:00
145 | Panchugar | 47 | 1 | 2021-12-01 | 18:00
146 | Joldhaka | 47 | 29 | 2021-12-01 | 18:30
147 | Kurigram | 55 | 20 | 2021-12-01 | 18:00
148 | Mitha Pukur | 40 | 30 | 2021-12-01 | 18:30
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:December 2021
Area | MW | Date | Hour | Remarks
Dhaka | 3722 | 02.12.2021 | 12:00
Chattogram | 1233 | 30.12.2021 | 18:00
Khulna | 1104 | 20.12.2021 | 18:30
Rajshahi | 918 | 07.12.2021 | 18:30
Cumilla | 797 | 30.12.2021 | 18:00
Mymensingh | 753 | 15.12.2021 | 18:00
Sylhet | 352 | 01.12.2021 | 18:00
Barisal | 266 | 14.12.2021 | 20:00
Rangpur | 653 | 29.12.2021 | 18:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: December '2021
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 419 | 27 | 2021-12-01 | 9:00 | 397 | 9 | 2021-12-01 | 12:00
2 | Bheramara | 400 | 409 | 21 | 2021-12-01 | 3:00 | 393 | 3 | 2021-12-01 | 18:00
3 | Ashuganj(N) | 400 | 412 | 26 | 2021-12-01 | 22:00 | 380 | 13 | 2021-12-01 | 5:00
4 | Payra | 400 | 422 | 20 | 2021-12-01 | 6:00 | 404 | 3 | 2021-12-01 | 1:00
5 | Kaliakoir | 400 | 417 | 28 | 2021-12-01 | 2:00 | 387 | 1 | 2021-12-01 | 16:00
6 | Bhulta | 400 | 407 | 26 | 2021-12-01 | 22:00 | 356 | 9 | 2021-12-01 | 12:00
7 | Gopalganj | 400 | 421 | 11 | 2021-12-01 | 15:00 | 393 | 14 | 2021-12-01 | 21:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 244 | 25 | 2021-12-01 | 20:00 | 227 | 2 | 2021-12-01 | 10:00
2 | Ishurdi | 230 | 247 | 24 | 2021-12-01 | 6:00 | 226 | 1 | 2021-12-01 | 13:00
3 | Ashuganj | 230 | 252 | 25 | 2021-12-01 | 23:00 | 235 | 1 | 2021-12-01 | 12:00
4 | Serajganj | 230 | 246 | 31 | 2021-12-01 | 17:00 | 229 | 4 | 2021-12-01 | 9:00
5 | Baghabari | 230 | 244 | 28 | 2021-12-01 | 1:00 | 228 | 1 | 2021-12-01 | 14:00
6 | Barapukuria | 230 | 240 | 29 | 2021-12-01 | 4:00 | 223 | 4 | 2021-12-01 | 9:00
7 | Bogura | 230 | 243 | 30 | 2021-12-01 | 15:00 | 227 | 2 | 2021-12-01 | 7:00
8 | Rajshahi | 230 | 248 | 21 | 2021-12-01 | 17:00 | 221 | 5 | 2021-12-01 | 11:00
9 | Khulna South | 230 | 250 | 25 | 2021-12-01 | 4:00 | 223 | 1 | 2021-12-01 | 7:00
10 | Rampura | 230 | 241 | 26 | 2021-12-01 | 1:00 | 221 | 2 | 2021-12-01 | 13:00
11 | Haripur | 230 | 242 | 23 | 2021-12-01 | 20:00 | 221 | 9 | 2021-12-01 | 12:00
12 | Hasnabad | 230 | 243 | 24 | 2021-12-01 | 13:00 | 222 | 1 | 2021-12-01 | 15:00
13 | Shyampur | 230 | 243 | 4 | 2021-12-01 | 21:00 | 221 | 9 | 2021-12-01 | 12:00
14 | Aminbazar | 230 | 245 | 24 | 2021-12-01 | 1:00 | 212 | 31 | 2021-12-01 | 2:00
15 | Tongi | 230 | 247 | 28 | 2021-12-01 | 12:00 | 217 | 9 | 2021-12-01 | 12:00
16 | Comilla (N) | 230 | 244 | 27 | 2021-12-01 | 19:30 | 226 | 1 | 2021-12-01 | 15:00
17 | Hathazari | 230 | 245 | 27 | 2021-12-01 | 19:00 | 220 | 1 | 2021-12-01 | 23:00
18 | Megnaghat | 230 | 249 | 24 | 2021-12-01 | 6:00 | 227 | 2 | 2021-12-01 | 12:00
19 | Fenchuganj | 230 | 249 | 16 | 2021-12-01 | 17:00 | 236 | 5 | 2021-12-01 | 9:00
20 | Siddhirganj | 230 | 245 | 25 | 2021-12-01 | 1:00 | 223 | 2 | 2021-12-01 | 11:00
21 | Maniknagar | 230 | 243 | 24 | 2021-12-01 | 5:00 | 222 | 4 | 2021-12-01 | 13:00
22 | Old Airport | 230 | 244 | 24 | 2021-12-01 | 12:00 | 222 | 9 | 2021-12-01 | 12:00
23 | Barisal | 230 | 250 | 3 | 2021-12-01 | 13:00 | 239 | 7 | 2021-12-01 | 20:00
24 | Bhola 225 MW | 230 | 252 | 3 | 2021-12-01 | 8:00 | 240 | 14 | 2021-12-01 | 14:00
25 | AKSML | 230 | 248 | 27 | 2021-12-01 | 22:00 | 213 | 1 | 2021-12-01 | 4:00
26 | BSRM | 230 | 245 | 27 | 2021-12-01 | 21:00 | 213 | 1 | 2021-12-01 | 4:00
27 | Bibiyana | 230 | 250 | 26 | 2021-12-01 | 8:00 | 235 | 8 | 2021-12-01 | 11:00
28 | Bhulta | 230 | 245 | 24 | 2021-12-01 | 6:00 | 222 | 9 | 2021-12-01 | 12:00
29 | Ashuganj (S) | 230 | 232 | 0 | 2021-12-01 | 16:00 | 231 | 1 | 2021-12-01 | 12:00
30 | Kaliakoir | 230 | 244 | 28 | 2021-12-01 | 22:00 | 220 | 2 | 2021-12-01 | 13:00
31 | GPH | 230 | 245 | 27 | 2021-12-01 | 22:00 | 211 | 1 | 2021-12-01 | 4:00
132 kV Substation
1 | Siddhirganj | 132 | 142 | 24 | 2021-12-01 | 0.25 | 130 | 2 | 2021-12-01 | 0.5
2 | Munsiganj | 132 | 144 | 26 | 2021-12-01 | 0.83333 | 130 | 9 | 2021-12-01 | 0.5
3 | Sonargaon | 132 | 141 | 14 | 2021-12-01 | 0 | 132 | 1 | 2021-12-01 | 0.5
4 | Shyampur | 132 | 144 | 3 | 2021-12-01 | 0.70833 | 130 | 9 | 2021-12-01 | 0.5
5 | Bhulta | 132 | 147 | 11 | 2021-12-01 | 0.8125 | 123 | 4 | 2021-12-01 | 0.58333
6 | Madanganj | 132 | 143 | 27 | 2021-12-01 | 0.875 | 129 | 9 | 2021-12-01 | 0.5
7 | Shitalakhya | 132 | 144 | 27 | 2021-12-01 | 0.75 | 104 | 14 | 2021-12-01 | 0
8 | Rahim Steal | 132 | 141 | 16 | 2021-12-01 | 0.70833 | 130 | 4 | 2021-12-01 | 0.41667
9 | Matuail | 132 | 142 | 24 | 2021-12-01 | 0.25 | 130 | 2 | 2021-12-01 | 0.5
10 | Ghorasal | 132 | 145 | 17 | 2021-12-01 | 0.75 | 124 | 13 | 2021-12-01 | 0.77083
11 | Narsinghdi | 132 | 141 | 31 | 2021-12-01 | 0.70833 | 128 | 8 | 2021-12-01 | 0.625
12 | Haripur (SBU) | 132 | 142 | 24 | 2021-12-01 | 0.375 | 118 | 13 | 2021-12-01 | 0.75
13 | Sreenagar | 132 | 140 | 3 | 2021-12-01 | 0.70833 | 129 | 9 | 2021-12-01 | 0.41667
14 | Ullon | 132 | 139 | 16 | 2021-12-01 | 0.20833 | 127 | 1 | 2021-12-01 | 0.5
15 | Hasnabad | 132 | 143 | 25 | 2021-12-01 | 0 | 130 | 9 | 2021-12-01 | 0.5
16 | Magbazar | 132 | 140 | 16 | 2021-12-01 | 0.29167 | 127 | 1 | 2021-12-01 | 0.5
17 | Maniknagar | 132 | 143 | 24 | 2021-12-01 | 0.20833 | 129 | 2 | 2021-12-01 | 0.54167
18 | Bangabhaban | 132 | 143 | 24 | 2021-12-01 | 0.20833 | 129 | 2 | 2021-12-01 | 0.54167
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: December '2021
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
19 | Narinda | 132 | 143 | 24 | 2021-12-01 | 0.20833 | 129 | 2 | 2021-12-01 | 0.54167
20 | Dhanmondi | 132 | 142 | 24 | 2021-12-01 | 0.16667 | 130 | 4 | 2021-12-01 | 0.45833
21 | Lalbag | 132 | 141 | 31 | 2021-12-01 | 0.33333 | 125 | 2 | 2021-12-01 | 0.45833
22 | Madartek | 132 | 139 | 16 | 2021-12-01 | 0.33333 | 127 | 2 | 2021-12-01 | 0.45833
23 | Dhaka University | 132 | 138 | 14 | 2021-12-01 | 0.91667 | 127 | 9 | 2021-12-01 | 0.5
24 | Aftabnagar | 132 | 140 | 16 | 2021-12-01 | 0.33333 | 127 | 9 | 2021-12-01 | 0.5
25 | Fatullah | 132 | 143 | 3 | 2021-12-01 | 0.70833 | 132 | 8 | 2021-12-01 | 0.45833
26 | Nawabganj | 133 | 141 | 3 | 2021-12-01 | 0.70833 | 118 | 14 | 2021-12-01 | 0.16667
27 | Mirpur | 132 | 142 | 28 | 2021-12-01 | 0.041667 | 126 | 1 | 2021-12-01 | 0.625
28 | Kalyanpur | 132 | 142 | 28 | 2021-12-01 | 0.041667 | 127 | 1 | 2021-12-01 | 0.58333
29 | Gulshan | 132 | 138 | 14 | 2021-12-01 | 0 | 126 | 1 | 2021-12-01 | 0.625
30 | Uttara | 132 | 141 | 19 | 2021-12-01 | 0.75 | 126 | 1 | 2021-12-01 | 0.5
31 | Uttara(New) | 132 | 141 | 23 | 2021-12-01 | 0.375 | 126 | 1 | 2021-12-01 | 0.625
32 | Kamrangirchar | 132 | 140 | 24 | 2021-12-01 | 0.25 | 129 | 11 | 2021-12-01 | 0.45833
33 | Savar | 132 | 143 | 28 | 2021-12-01 | 0.95833 | 126 | 1 | 2021-12-01 | 0.625
34 | Bhasantec | 132 | 141 | 16 | 2021-12-01 | 0.33333 | 129 | 2 | 2021-12-01 | 0.41667
35 | Agargaon | 132 | 141 | 16 | 2021-12-01 | 0.375 | 130 | 2 | 2021-12-01 | 0.45833
36 | Satmosjid | 132 | 141 | 16 | 2021-12-01 | 0.33333 | 129 | 2 | 2021-12-01 | 0.41667
37 | Tongi | 132 | 144 | 18 | 2021-12-01 | 19:30 | 129 | 1 | 2021-12-01 | 0.41667
38 | Kabirpur | 132 | 141 | 23 | 2021-12-01 | 0.91667 | 128 | 9 | 2021-12-01 | 18:29
39 | Basundhara | 132 | 142 | 20 | 2021-12-01 | 18:30 | 126 | 1 | 2021-12-01 | 0.625
40 | Manikganj | 132 | 144 | 23 | 2021-12-01 | 0.875 | 95 | 14 | 2021-12-01 | 0.79167
41 | Joydevpur | 132 | 143 | 17 | 2021-12-01 | 0.70833 | 127 | 1 | 2021-12-01 | 0.45833
42 | New Tongi | 132 | 144 | 23 | 2021-12-01 | 0.70833 | 123 | 1 | 2021-12-01 | 0.41667
43 | Kodda | 132 | 142 | 24 | 2021-12-01 | 18:00 | 125 | 2 | 2021-12-01 | 18:30
44 | Dhamrai | 132 | 141 | 31 | 2021-12-01 | 19:00 | 118 | 1 | 2021-12-01 | 0.5
45 | Rajendrapur | 132 | 145 | 13 | 2021-12-01 | 19:30 | 126 | 9 | 2021-12-01 | 12:00
46 | Valuka | 132 | 135 | 24 | 2021-12-01 | 0.45833 | 120 | 12 | 2021-12-01 | 0.5
47 | Tangail | 132 | 140 | 18 | 2021-12-01 | 0.91667 | 129 | 1 | 2021-12-01 | 0.5
48 | Mymensing | 132 | 137 | 24 | 2021-12-01 | 0.375 | 123 | 12 | 2021-12-01 | 0.5
49 | Kishorganj | 132 | 137 | 21 | 2021-12-01 | 0.70833 | 126 | 9 | 2021-12-01 | 0.5
50 | Netrokona | 132 | 135 | 4 | 2021-12-01 | 0.083333 | 121 | 12 | 2021-12-01 | 0.5
51 | Jamalpur | 132 | 142 | 28 | 2021-12-01 | 0.83333 | 120 | 2 | 2021-12-01 | 0.29167
52 | Sherpur | 132 | 140 | 14 | 2021-12-01 | 0.41667 | 117 | 2 | 2021-12-01 | 0.29167
53 | Srimongal | 132 | 141 | 17 | 2021-12-01 | 0.70833 | 134 | 2 | 2021-12-01 | 0.5
54 | Shahjibazar | 132 | 139 | 17 | 2021-12-01 | 0.70833 | 131 | 9 | 2021-12-01 | 0.5
55 | Fenchuganj | 132 | 139 | 3 | 2021-12-01 | 0.25 | 134 | 11 | 2021-12-01 | 0.625
56 | Khulawara | 132 | 138 | 15 | 2021-12-01 | 0.041667 | 134 | 9 | 2021-12-01 | 0.5
57 | Sylhet | 132 | 136 | 3 | 2021-12-01 | 0.041667 | 132 | 29 | 2021-12-01 | 0.5
58 | Chattak | 132 | 138 | 17 | 2021-12-01 | 0.20833 | 132 | 29 | 2021-12-01 | 0.45833
59 | Sunamganj | 132 | 136 | 28 | 2021-12-01 | 0.125 | 130 | 29 | 2021-12-01 | 0.79167
60 | Biani Bazar | 132 | 137 | 24 | 2021-12-01 | 0.16667 | 131 | 29 | 2021-12-01 | 0.66667
61 | Comilla(South) | 132 | 131 | 25 | 2021-12-01 | 0.91667 | 123 | 13 | 2021-12-01 | 0.75
62 | Comilla (North) | 132 | 148 | 28 | 2021-12-01 | 0.25 | 137 | 1 | 2021-12-01 | 0.66667
63 | Chandpur | 132 | 148 | 18 | 2021-12-01 | 0.041667 | 132 | 6 | 2021-12-01 | 0.125
64 | Feni | 132 | 145 | 28 | 2021-12-01 | 0.83333 | 130 | 1 | 2021-12-01 | 0.083333
65 | Chowmuhani | 132 | 143 | 31 | 2021-12-01 | 0.041667 | 132 | 2 | 2021-12-01 | 0.125
66 | Ashuganj | 132 | 143 | 17 | 2021-12-01 | 0.70833 | 134 | 9 | 2021-12-01 | 0.5
67 | Daudkandi | 132 | 144 | 29 | 2021-12-01 | 0.75 | 133 | 1 | 2021-12-01 | 0.625
68 | Brahminbaria | 132 | 138 | 17 | 2021-12-01 | 0.29167 | 128 | 9 | 2021-12-01 | 0.5
69 | Ramganj | 132 | 143 | 21 | 2021-12-01 | 0.70833 | 132 | 2 | 2021-12-01 | 0.25
70 | Chaddagram | 132 | 145 | 29 | 2021-12-01 | 0.875 | 133 | 9 | 2021-12-01 | 0.41667
71 | PHP | 132 | 143 | 29 | 2021-12-01 | 0.20833 | 129 | 1 | 2021-12-01 | 0.083333
72 | Kochua | 132 | 145 | 3 | 2021-12-01 | 0.70833 | 132 | 6 | 2021-12-01 | 0.20833
73 | Madanhat | 132 | 143 | 11 | 2021-12-01 | 0.8125 | 127 | 24 | 2021-12-01 | 0.5
74 | Hathazari | 132 | 145 | 27 | 2021-12-01 | 0.79167 | 131 | 1 | 2021-12-01 | 0.041667
75 | Khulshi | 132 | 142 | 28 | 2021-12-01 | 0.83333 | 125 | 6 | 2021-12-01 | 0.20833
76 | Halishahar | 132 | 143 | 28 | 2021-12-01 | 0.83333 | 128 | 6 | 2021-12-01 | 0.16667
77 | Baraulia | 132 | 143 | 11 | 2021-12-01 | 0.83333 | 127 | 1 | 2021-12-01 | 0.083333
78 | Sikalbaha | 132 | 148 | 5 | 2021-12-01 | 0.79167 | 127 | 18 | 2021-12-01 | 0
79 | Dohazari | 132 | 142 | 24 | 2021-12-01 | 0.33333 | 125 | 1 | 2021-12-01 | 0.95833
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: December '2021
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
80 | Cox'sbazar | 132 | 131 | 24 | 2021-12-01 | 0.70833 | 109 | 4 | 2021-12-01 | 0.83333
81 | Chandraghona | 132 | 144 | 28 | 2021-12-01 | 0.875 | 128 | 1 | 2021-12-01 | 0.16667
82 | Kaptai | 132 | 141 | 27 | 2021-12-01 | 0.875 | 134 | 15 | 2021-12-01 | 0.75
83 | A. Khaer Stl. | 132 | 144 | 31 | 2021-12-01 | 0.20833 | 127 | 14 | 2021-12-01 | 0.41667
84 | Bakulia | 132 | 146 | 23 | 2021-12-01 | 0.33333 | 126 | 1 | 2021-12-01 | 0.083333
85 | Julda | 132 | 144 | 31 | 2021-12-01 | 0.25 | 126 | 1 | 2021-12-01 | 0.125
86 | TK Chemical | 132 | 148 | 27 | 2021-12-01 | 0 | 127 | 2 | 2021-12-01 | 0.25
87 | Modern Steel | 132 | 142 | 20 | 2021-12-01 | 0.91667 | 125 | 1 | 2021-12-01 | 0.16667
88 | Shahmirpur | 132 | 144 | 31 | 2021-12-01 | 0.25 | 126 | 1 | 2021-12-01 | 0.083333
89 | Khagrachhari | 132 | 142 | 27 | 2021-12-01 | 0.91667 | 126 | 6 | 2021-12-01 | 0.66667
90 | Matarbari | 132 | 135 | 28 | 2021-12-01 | 0.77083 | 108 | 5 | 2021-12-01 | 0.83333
91 | Baroiar Hat | 132 | 142 | 4 | 2021-12-01 | 0.75 | 130 | 6 | 2021-12-01 | 0.45833
92 | Rangamati | 132 | 143 | 27 | 2021-12-01 | 0.91667 | 128 | 1 | 2021-12-01 | 0.16667
93 | Goalpara | 132 | 143 | 24 | 2021-12-01 | 0.25 | 125 | 1 | 2021-12-01 | 0.29167
94 | Khulna Central | 132 | 141 | 11 | 2021-12-01 | 0.25 | 125 | 1 | 2021-12-01 | 0.29167
95 | Noapara | 132 | 141 | 17 | 2021-12-01 | 0.16667 | 125 | 1 | 2021-12-01 | 0.29167
96 | Jessore | 132 | 141 | 24 | 2021-12-01 | 0.20833 | 124 | 1 | 2021-12-01 | 0.54167
97 | Benapol | 132 | 141 | 18 | 2021-12-01 | 0.083333 | 123 | 1 | 2021-12-01 | 0.54167
98 | Jhenida | 132 | 142 | 10 | 2021-12-01 | 0.70833 | 128 | 1 | 2021-12-01 | 0.29167
99 | Bottail | 132 | 142 | 17 | 2021-12-01 | 0.083333 | 129 | 1 | 2021-12-01 | 0.29167
100 | G.K Project | 132 | 144 | 10 | 2021-12-01 | 17:0 | 130 | 5 | 2021-12-01 | 0.45833
101 | Faridpur | 132 | 142 | 11 | 2021-12-01 | 0.25 | 130 | 2 | 2021-12-01 | 0.45833
102 | Madaripur | 132 | 146 | 22 | 2021-12-01 | 0.20833 | 136 | 20 | 2021-12-01 | 0.75
103 | Sariatpur | 132 | 145 | 16 | 2021-12-01 | 0.125 | 137 | 4 | 2021-12-01 | 0.83333
104 | Gopalganj | 132 | 145 | 25 | 2021-12-01 | 0.70833 | 129 | 3 | 2021-12-01 | 0.5
105 | Bagerhat | 132 | 141 | 24 | 2021-12-01 | 0.16667 | 120 | 2 | 2021-12-01 | 0.29167
106 | Mongla | 132 | 141 | 24 | 2021-12-01 | 0.45833 | 123 | 1 | 2021-12-01 | 0.5
107 | Satkhira | 132 | 141 | 31 | 2021-12-01 | 0.20833 | 124 | 1 | 2021-12-01 | 0.5
108 | Gallamari | 132 | 145 | 20 | 2021-12-01 | 0.83333 | 131 | 3 | 2021-12-01 | 0.5
109 | Magura | 132 | 144 | 21 | 2021-12-01 | 0.083333 | 125 | 7 | 2021-12-01 | 0.375
110 | Norail | 132 | 142 | 17 | 2021-12-01 | 0.125 | 126 | 1 | 2021-12-01 | 0.54167
111 | Chuadanga | 132 | 142 | 21 | 2021-12-01 | 0.125 | 126 | 1 | 2021-12-01 | 0.54167
112 | Barisal(N) | 132 | 146 | 23 | 2021-12-01 | 0.125 | 138 | 4 | 2021-12-01 | 0.75
113 | Barisal(S) | 132 | 145 | 3 | 2021-12-01 | 0.25 | 128 | 14 | 2021-12-01 | 0.54167
114 | Patuakhali | 132 | 144 | 6 | 2021-12-01 | 0.25 | 126 | 14 | 2021-12-01 | 0.54167
115 | Bhandaria | 132 | 146 | 3 | 2021-12-01 | 0.375 | 135 | 3 | 2021-12-01 | 0.79167
116 | Borguna | 132 | 145 | 3 | 2021-12-01 | 0.25 | 137 | 3 | 2021-12-01 | 0.875
117 | Ishurdi | 132 | 143 | 20 | 2021-12-01 | 0.70833 | 131 | 1 | 2021-12-01 | 0.5
118 | Ruppur paromanobik | 132 | 142 | 11 | 2021-12-01 | 0.70833 | 131 | 1 | 2021-12-01 | 0.54167
118 | Natore | 132 | 143 | 28 | 2021-12-01 | 0.083333 | 131 | 5 | 2021-12-01 | 0.45833
119 | Bogra | 132 | 143 | 27 | 2021-12-01 | 0.083333 | 120 | 19 | 2021-12-01 | 0.33333
120 | Noagaon | 132 | 139 | 27 | 2021-12-01 | 0.70833 | 121 | 7 | 2021-12-01 | 0.33333
121 | Rajshahi | 132 | 142 | 20 | 2021-12-01 | 0.77083 | 130 | 5 | 2021-12-01 | 0.45833
122 | Rajshahi New | 132 | 142 | 10 | 2021-12-01 | 0.70833 | 130 | 5 | 2021-12-01 | 0.45833
123 | C.Nawabganj | 132 | 142 | 20 | 2021-12-01 | 0.77083 | 128 | 4 | 2021-12-01 | 0.45833
124 | Amnura | 132 | 143 | 13 | 2021-12-01 | 0.75 | 128 | 1 | 2021-12-01 | 0.58333
125 | Pabna | 132 | 142 | 24 | 2021-12-01 | 0.25 | 130 | 5 | 2021-12-01 | 0.45833
126 | Shahjadpur | 132 | 147 | 24 | 2021-12-01 | 0.77083 | 137 | 1 | 2021-12-01 | 0.54167
127 | Serajganj | 132 | 142 | 24 | 2021-12-01 | 0.77083 | 132 | 1 | 2021-12-01 | 0.5
128 | Niyamatpur | 132 | 139 | 29 | 2021-12-01 | 0.125 | 117 | 19 | 2021-12-01 | 0.33333
129 | Joypurhat | 132 | 140 | 24 | 2021-12-01 | 0.8125 | 116 | 19 | 2021-12-01 | 0.33333
130 | Sherpur(Bogura) | 132 | 143 | 28 | 2021-12-01 | 0.041667 | 131 | 7 | 2021-12-01 | 0.33333
132 | Mohastangor | 132 | 143 | 28 | 2021-12-01 | 0.125 | 125 | 7 | 2021-12-01 | 0.33333
133 | Bangura | 132 | 144 | 24 | 2021-12-01 | 0.66667 | 133 | 1 | 2021-12-01 | 0.5
134 | Rangpur | 132 | 141 | 29 | 2021-12-01 | 0.20833 | 123 | 10 | 2021-12-01 | 0.5
135 | Lalmonirhat | 132 | 138 | 28 | 2021-12-01 | 0.125 | 123 | 4 | 2021-12-01 | 0.54167
136 | Saidpur | 132 | 137 | 28 | 2021-12-01 | 0.20833 | 122 | 4 | 2021-12-01 | 0.54167
137 | Purbasadipur | 132 | 135 | 26 | 2021-12-01 | 0.95833 | 116 | 20 | 2021-12-01 | 0.41667
138 | Thakurgaon | 132 | 134 | 26 | 2021-12-01 | 0.95833 | 114 | 20 | 2021-12-01 | 0.41667
139 | Palashbari | 132 | 140 | 29 | 2021-12-01 | 0.041667 | 122 | 19 | 2021-12-01 | 0.29167
140 | Barapukuria | 132 | 140 | 29 | 2021-12-01 | 0.16667 | 123 | 4 | 2021-12-01 | 0.375
141 | Panchagar | 132 | 137 | 26 | 2021-12-01 | 0.95833 | 117 | 19 | 2021-12-01 | 0.5
142 | Joldhaka | 132 | 137 | 28 | 2021-12-01 | 0.125 | 121 | 9 | 2021-12-01 | 0.75
143 | Kurigram | 132 | 138 | 28 | 2021-12-01 | 0.083333 | 122 | 9 | 2021-12-01 | 0.75
144 | Mithapukur | 132 | 142 | 28 | 2021-12-01 | 0.083333 | 127 | 2 | 2021-12-01 | 0.29167
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:December 2021
Name of the | Auto transformer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 46 | 160
Hasnabad | TR2 | 225 | 46 | 160 | 20/12/2021 | 24:00
| TR3 | 225 | 46 | 160
| TR1 | 225 | 150 | 420 | 01.12.2021 | 10:00
Tongi | TR2 | 225 | 150 | 420 |  | 17:00
| TR3 | 225 | 150 | 420 |  | 17:00
Haripur | TR1 | 225 | 78 | 275
| TR2 | 225 | 78 | 275 | 2021-01-11 | 16:00
| TR3 | 225 | 78 | 275
| TR1 | 225 | 132 | 355
Rampura | TR2 | 225 | 132 | 355 | 2021-08-12 | 12:00
| TR3 | 225 | 132 | 355
Keraniganj | ATR1 | 300 | 80 | 202
| ATR2 | 300 | 80 | 202 | 26/12/2021 | 18:00
| ATR3 | 300 | 80 | 202
| TR1 | 225 | 90 | 218
Aminbazar | TR2 | 225 | 90 | 218 | 16/12/2021 | 20:00
| TR3 | 225 | 96 | 239
Agargaon | TR1 | 300 | 109 | 284
| TR2 | 300 | 109 | 284 | 2021-09-12 | 13:00
Maniknagar | TR1 | 300 | 102 | 280 | 2021-08-12 | 13:00
| TR2 | 300 | 102 | 280
Cumilla (N) | TR1 | 225 | 167 | 444 | 2021-08-12 | 5:00
| TR2 | 225 | 165 | 436
Fenchuganj | AT2 | 300 | 187 | 451 | 2021-11-12 | 10:00
| MT1 | 150 | 80 | 190
Hathazari | MT2 | 150 | 80 | 190 | 2021-07-12 | 7:00
| MT3 | 150 | 80 | 190
| MT4 | 150 | 80 | 190
| TR1 | 225 | 69 | 180
Ishurdi | TR2 | 225 | 69 | 180 | 18/12/2021 | 12:00
| TR3 | 225 | 69 | 180
Khulna(S) | TR1 | 225 | 78 | 195
| TR2 | 225 | 78 | 195 | 20/12/2021 | 180:00
| TR3 | 300 | 100 | 250
Bogura | TR1 | 225 | 94 | 258 | 02.12.21 | 7:00
| TR2 | 225 | 94 | 258
| TR3 | 225 | 128 | 347
Baghabari | TR1 | 300 | 120 | 300 | 2021-08-12 | 19:30
| TR2 | 225 | 90 | 225
Rajshahi | ATR-01 | 300 | 136 | 218 | 09.12.2021 | 20:00
| ATR-02 | 300 | 136 | 218
Barapukuria | TR1 | 225 | 172 | 750 |  |  | Due to unavailability of 230 kV side meters
| TR2 | 225 | 126 | 580 | 19/12/2021 | 8:00 | 132 kV current is being provided
| TR6 | 300 | 162 | 732
Bheramara | Transformer-1 | 225 | 114 | 300 | 18/12/2021 | 11:00
| Transformer-2 | 225 | 114 | 300
Shyampur | ATR-01 | 300 | 91 | 225 | 15/12/2021 | 10:00
| ATR-02 | 300 | 91 | 225
Kaliakoir | TR1 | 300 | 92 | 244 | 29/12/2021 | 12:00
Sikalbaha | ATR-1 | 300 | 157 | 423 | 2021-05-12 | 19:00
| ATR-2 | 300 | 157 | 423
Jhenaidah | T1(230/132 kV) | 300 | 118 | 320 | 2021-12-01 | 18:00
| T2(230/132 kV) | 300 | 118 | 320
Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:December 2021
Name of the | Transformer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps (400 kV side) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 254 | 375 | 2021-12-02 | 6:30
| TR2(400/230 kV) | 520 | 256 | 375
| TR1(400/132 kV) | 325 | 229 | 355 | 2021-12-01 | 17:30
| TR2(400/132 kV) | 325 | 230 | 355
Bibiyana | ICT1(400/230 kV) | 520 | 96 | 142 |  | 5:00
| ICT2(400/230kV) | 520 | 92 | 138 | 2021-12-02
Bhulta | ATR1(400/230 kV) | 520 | 181 | 314 | 21/12/2021 | 10:30
| ATR2(400/230kV) | 520 | 181 | 314 |  | 12:30
Ashuganj(N) | GSUT1(400/230 kV) | 567 | 394 | 634 | 21/12/2021 | 10:40
Gopalganj | ATR1(400/138 kV) | 325 | 297 | 423 | 14.12.2021 | 21:00
| ATR2(400/138kV) | 325 | 297 | 423
Payra | GSUT1 | 270 | 200 | 852 | 14/12/2021 | 21:00
| GSUT2 | 270 | 200 | 848
| GSUT3 | 270 | 200 | 848
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.
594
423

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:December 2021 | [6 empty] | (For Evening Peak) | [7 empty] | Month:December 2021 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2021-12-01 | 9537 | 9537 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-01 | 8254 | 8254 | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-02 | 9588 | 9588 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-02 | 8400 | 8400 | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-03 | 8300 | 8300 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-03 | 6698 | 6698 | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-04 | 9409 | 9409 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-04 | 7235 | 7235 | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-05 | 9231 | 9231 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-05 | 7990 | 7990 | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-06 | 8671 | 8671 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-06 | 7593 | 7593 | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-07 | 9321 | 9321 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-07 | 8001 | 8001 | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-08 | 9460 | 9460 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-08 | 8037 | 8037 | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-09 | 9444 | 9444 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-09 | 8186 | 8186 | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-10 | 8214 | 8214 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-10 | 6751 | 6751 | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-11 | 9326 | 9326 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-11 | 7253 | 7253 | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-12 | 9246 | 9246 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-12 | 7833 | 7833 | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-13 | 9313 | 9313 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-13 | 7769 | 7769 | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-14 | 9221 | 9221 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-14 | 7638 | 7638 | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-15 | 9137 | 9137 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-15 | 7828 | 7828 | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-16 | 7802 | 7802 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-16 | 6480 | 6480 | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-17 | 7955 | 7955 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-17 | 6418 | 6418 | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-18 | 9047 | 9047 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-18 | 6938 | 6938 | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-19 | 9061 | 9061 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-19 | 7644 | 7644 | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-20 | 9082 | 9082 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-20 | 7604 | 7604 | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-21 | 9336 | 9336 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-21 | 7803 | 7803 | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-22 | 9312 | 9312 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-22 | 7959 | 7959 | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-23 | 9245 | 9245 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-23 | 7927 | 7927 | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-24 | 8150 | 8150 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-24 | 6700 | 6700 | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-25 | 9013 | 9013 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-25 | 7631 | 7631 | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-26 | 9149 | 9149 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-26 | 7598 | 7598 | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-27 | 9446 | 9446 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-27 | 7888 | 7888 | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-28 | 9368 | 9368 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-28 | 7942 | 7942 | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-29 | 9398 | 9398 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-29 | 8046 | 8046 | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-30 | 9302 | 9302 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-30 | 8088 | 8088 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
2021-12-31 | 8193 | 8193 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-12-31 | 6768 | 6768 | - | - | - | - | - | - | - | - | - | - | - | -
Evening Peak | Max. L/S | 0 | - | -
| Min. L/S | 0 | - | -
| No. of Days | - | [12 empty] | 0 | 0 | 1
[15 empty] | 0 | 0 | 2
| Max. L/S | - | - | - | [10 empty] | 0 | 0 | 3
Day Peak | Min. L/S | - | - | - | [10 empty] | 0 | 0 | 4
| No. of Days | - | - | - | [10 empty] | 0 | 0 | 5
[15 empty] | 0 | 0 | 6
| Max. L/S | - | - | - | [10 empty] | 0 | 0 | 7
Full Day | Min. L/S | - | - | - | [10 empty] | 0 | 0 | 8
| No. of Days | - | [12 empty] | 0 | 0 | 9
| Average L/S | #DIV/0! | [12 empty] | 0 | 0 | 10
[15 empty] | 0 | 0 | 11
[15 empty] | 0 | 0 | 12
[15 empty] | 0 | 0 | 13
[15 empty] | 0 | 0 | 14
[15 empty] | 0 | 0 | 15
[15 empty] | 0 | 0 | 16
[15 empty] | 0 | 0 | 17
[15 empty] | 0 | 0 | 18
[15 empty] | 0 | 0 | 19
[15 empty] | 0 | 0 | 20
[15 empty] | 0 | 0 | 21
[15 empty] | 0 | 0 | 22
[15 empty] | 0 | 0 | 23
[15 empty] | 0 | 0 | 24
[15 empty] | 0 | 0 | 25
[15 empty] | 0 | 0 | 26
[15 empty] | 0 | 0 | 27
[15 empty] | 0 | 0 | 28
[15 empty] | 0 | 0 | 29
[15 empty] | 0 | 0 | 30
[15 empty] | #REF! | #REF! | 31

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:December 2021
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 9588 | 2021-12-02 | 19:00
2 | Maximum Day Peak Genaration | MW | 8400 | 2021-12-02 | 12:00
3 | Maximum Evening Peak Demand | MW | 9588 | 2021-12-02 | 12:00
4 | Minimum Generation | MW | 5167 | 2021-12-17 | 6:00
5 | Average of the daily evening peak Genaration | MW | 9041.1935
6 | Average of the daily day peak Genaration | MW | 7577.4194
7 | Maximum load shed | MW | 0 | - | -
8 | Minimum load shed | MW | 0 | - | -
9 | Total nos. of load shed days | Day | 0
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 0
11 | Total Generation | MkWh | 5526.8646
12 | Total Generation by BPDB | MkWh | 1148.0976 | % of total Gen. | 20.77%
13 | Total Generation by IPP | MkWh | 1864.9461 | '' | 33.74%
14 | A) Total Generation by Generation Companies | MkWh | 1546.138 | '' | 27.97%
| B) Total Generation by REB | MkWh | 126.8797 | " | 2.296%
| C) Total Generation by RENTAL | MkWh | 390.0595 | " | 7.058%
| D) Total Imported from India (BIPTC) | MkWh | 393.9694 | " | 7.128%
| E) Total Imported from Tripura, India (A.C) | MkWh | 56.7743 | " | 1.027%
15 | Fuel wise Generation.
| A) Gas | MkWh | 3368.8362 | % of total Gen. | 60.95%
| B) Oil | MkWh | 1203.3537 | '' | 21.77%
| C) Hydro | MkWh | 52.2948 | '' | 0.9462%
| D) Solar | MkWh | 23.3093 | '' | 0.4217%
| E) Coal | MkWh | 428.3268 | '' | 7.75%
| F) BIPTC (Import from India) | MkWh | 393.9694 | '' | 7.128%
| G) A.C (Import from Tripura, India) | MkWh | 56.7743 | '' | 1.027%
16 | Maximun of the daily total Generation . | MkWh | 190.906 | 2021-12-02
17 | Monthly Load factor | % | 77.488
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 16388.0044
| A) Gas | M.Taka | 3407.5578
| B) Liquid fuel | M.Taka | 8547.0336
| C) Coal | M.Taka | 2066.4782
| D) BIPTC (Import from India) | M.Taka | 1953.1441
| E) Tripura(Import from India) | M.Taka | 413.7906
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 665.5257 | 2021-12-21
| A) Gas | M.Taka | 131.6512 | 2021-12-02
| B) Liquid fuel | M.Taka | 508.5807 | 2021-12-21
| C) Coal | M.Taka | 79.9396 | 2021-12-08
| D) BIPTC (Import from India) | M.Taka | 74.5379 | 2021-12-16
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 3.9802
| B) Excluding Hydro & Solar | Taka/kWhR | 4.0349
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 103.1 | 31/12/2021 | 06:00
b) | Actual | FT (MSL) | 98.51 | 31/12/2021 | 06:00
22 | Peak Genaration of December 2020 | MW | 9098 | 5/12/2020 | 19:00
23 | Peak Demand of December 2020 | MW | 9098 | 5/12/2020 | 19:00
24 | Maximum peak Generation recorded upto 31/12/2021 | MW | 13792 | 27/04/21 | 20:00
25 | Maximum peak Demand recorded upto 31/12/2021 | MW | 14097 | 27/04/21 | 12:00
26 | Maximum load shed recorded upto 31/12/2021 | MW | 1459 | 04/05/2010 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.