## QF-MIS-03
QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month: February 2016
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | February 2016 |  | January 2016 |  | February 2015
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 7729 | 29/02/16 | 7080 | 25/01/16 | 7022 | 26/02/15 | 8177 | 13/08/15
|  |  | 19:30 |  | 19:00 |  | 19:30 |  | 21:00
2 | Minimum Generation (MW) | 3727 | 06/02/16 | 3309 | 20/01/16 | 2737 | 08/02/15 | - | -
|  |  | 4:00 |  | 5:00 |  | 4:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 7729 | 29/02/16 | 7080 | 25/01/16 | 7022 | 26/02/15 | 8177 | 13/08/15
|  |  | 19:30 |  | 19:00 |  | 19:30 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 6689 | 23/02/16 | 5766 | 31/01/16 | 5821 | 26/02/15 | 69786 | 14/07/15
|  |  | 12:00 |  | 9:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 7729 | 29/02/16 | 7080 | 25/01/16 | 7022 | 26/02/15 | 8177 | 13/08/15
|  |  | 19:30 |  | 19:00 |  | 19:30 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 7234.8966 |  | 6693.2903 |  | 6329.75 |  | 7773.29 | Aug-15
7 | Average Generation (MW) at Day Peak | 5818.5517 |  | 5081.8387 |  | 5045 |  | 6169.03 | Aug-14
8 | Maximum Power Import from India (MW) | 464 | 22/02/16 | 468 | 14/01/16 | 467 | 02/02/15 | 481 | 01/01/14
|  |  | 1:00 |  | 13:00 |  | 17:00 |  | 14:00
9 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | 0 | - | 1459 | 2010-05-04
|  |  | - |  | - |  | - |  | 20:00
10 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
|  |  | - |  | - |  | - |  | 20:00
11 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | 0 | -
|  |  | - |  | - |  | -
12 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
|  |  | - |  | - |  | -
13 | Maximum Load Shed (MW) at Day Peak | - | 0 | - | 0 | 0 | -
|  |  | 0:00 |  | 0:00 |  | -
14 | Generation During Max. Load Shed (MW) at Day Peak |  |  |  |  | - | -
-
15 | Minimum Load Shed (MW) at Day Peak | - | 0 | - | 0 | 0 | -
|  |  | 0:00 |  | 0:00 |  | -
16 | Generation During Min. Load Shed (MW) at Day Peak |  |  |  |  | - | -
-
17 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | 0 |  | 30 | April 10
18 | Nos. of Days Load Shed at Day Peak | - |  | - |  | 0 |  | 30 | Mar 10
19 | Gross Generation of BPDB (Mkwh) | 1676.0588 |  | 1652.402 |  | 1454.3618
20 | Station Use of BPDB (Mkwh) | 85.3625 |  | 85.4463 |  | 68.8274
21 | Net Generation of BPDB (Mkwh) | 1590.6963 |  | 1566.9557 |  | 1385.5344
22 | Net Generation of IPP, REB (Mkwh) | 464.9592 |  | 471.769 |  | 366.5549
|  | 108.8198 |  | 104.6013 |  | 148.0025
23 | Net Generation of Rental Power Plant (MKWh) | 1380.5695 |  | 1188.2906 |  | 944.5885
24 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 3545.0448 |  | 3331.6166 |  | 2844.6803
25 | Energy Generation by Gas (MKWh) | 2756.5889 |  | 2796.8147 |  | 2221.3989
26 | Energy Generation by Diesel (MKWh) | 79.9997 |  | 60.2559 |  | 69.1094
27 | Energy Generation by Furnace Oil (MKWh) | 658.3506 |  | 468.9676 |  | 492.3121
28 | Energy Generation by Hydro (MKWh) | 48.9778 |  | 29.9195 |  | 27.9261
29 | Energy Generation by Coal (MKWh) | 86.4904 |  | 61.1052 |  | 102.7613
30 | Enegry (HVDC) Import from India (MKWh) | 278.3004 |  | 271.6722 |  | 290.6611 |  | 334.8 | May-15
31 | Monthly Load Factor (%) | 72.66% |  | 70.03% |  | 67.75%

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month: February 2016
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 7729 | 29/02/16 | 19:30
Generation Period
| Dhaka | MW | 2811
| Chittagong | MW | 831
| Comilla | MW | 609
| Mymensingh | MW | 451
| Sylhet | MW | 258
a) | Total supply in East zone | MW | 4960
| Khulna | MW | 817
| Barisal | MW | 151
| Rajshahi | MW | 798
| Rangpur | MW | 453
b) | Total supply in West zone | MW | 2219
c) | Total supply in both zone ( a+b) | MW | 7179
Ref: | PGCB/IMD/4.01/2016/16 | Date: 14/03/2016
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month: February 2016
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 800 | 12/02/16 | 9:00
| b) Ishurdi end | MW | 36 | 03/02/16 | 18:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 300 | 03/02/16 | 18:00
| b) Ishurdi end | MW | 320 | 12/02/16
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 5.7255 | 22/02/16
| b) Ishurdi end | MKWH | 0.19869 | 03/02/16
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 0.19497 | 03/02/16
| b) Ishurdi end | MKWH | 4.6167 | 12/02/16
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 76.6034
| b) Ishurdi end | MKWH | 0.95345
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 0.92485
| b) Ishurdi end | MKWH | 74.5849
23 | Transmission loss of EWI/ NO-1 | % | 2.635
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 480 | 26/02/16 | 8:00
| b)Serajganj end | MW | - | - | -
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | - | - | -
| b)Sirajganj end | MW | 440 | 21/02/16 | 8:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 8.29 | 21/02/16
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 8.2 | 21/02/16
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 176.706
| b)Sirajganj end | MKWH | -
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | -
| b)Sirajganj end | MKWH | 174.298
30 | Transmission loss of EWI /NO-2 | % | 1.3627
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishurdi, Pabna.
* The energy metre of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: February 2016
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Netrokona | 132/33 kV Trnasformer T3 | 2016-02-08 13:02 | 2016-02-08 13:38 | 0:36 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Tongi | 132/33 kV Trnasformer T-1 | 2016-02-29 06:05 | 2016-02-29 06:21 | 0:16 | T | Tripped showing REF.87 N & E/F relay | 0 | 0 | No interruption
| 132/33 kV Trnasformer T-1 | 2016-02-29 06:45 | 2016-02-29 11:35 | 4:50 | T |  | 0 | 0 | No interruption
|  |  | Total : | 5:42 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Hasnabad | 230/132 kV Trnasformer TR1 | 2016-02-04 18:39 | 2016-02-04 19:54 | 1:15 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Manikganj | 132/33 kV Trnasformer T-3 | 2016-02-06 11:34 | 2016-02-06 13:38 | 2:04 | E/O | Due to Oil leakage | 0 | 0 | No interruption
| 132/33 kV Trnasformer T-3 | 2016-02-09 07:28 | 2016-02-09 08:58 | 1:30 | E/O | Due to Oil leakage in Current Transformer | 0 | 0 | No interruption
Siddhirganj | 132/33 kV Trnasformers T1 & T2 | 2016-02-12 04:31 | 2016-02-12 04:52 | 0:21 | T | Tripped showing inst.E/F relay | 0 | 0 | No interruption
Ullon | 132/33 kV Trnasformer T-3 | 2016-02-18 06:22 | 2016-02-18 09:05 | 2:43 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 7:53 |  | Unserved Energy: |  | 0
Chittagong Grid Circle :
Halishahar | 132/33 kV Transformer-T1 | 2016-02-01 10:37 | 2016-02-01 13:35 | 2:58 | E/O | Due to red hot maintenance at Y-phase132 kV bushing | 0 | 0 | No interruption
Madunaghat | 132/33 kV Trnasformer T-2 | 2016-02-20 10:48 | 2016-02-20 12:44 | 1:56 | E/O | Due to red hot maintenance at Y-phase132 kV bushing | 0 | 0 | No interruption
Hathazari | 230/132 kV Trnasformer MT-1 | 2016-02-29 14:49 | 2016-02-29 17:43 | 2:54 | E/O | Due to sparking at R-phase isolator | 0 | 0 | No interruption
|  |  | Total : | 7:48 |  | Unserved Energy: |  | 0
Comilla Grid Circle :
Comilla(S) | 132/33 kV Transformer-T1 | 2016-02-01 12:02 | 2016-02-01 13:44 | 1:42 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Chattak | 132/33 kV Trnasformer T-1 | 2016-02-06 22:27 | 2016-02-06 22:34 | 0:07 | T | Tripped showing O/C relay | 0 | 0 | No interruption
| 132/33 kV Trnasformer T-1 | 2016-02-10 10:55 | 2016-02-10 11:08 | 0:13 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Comilla(s) | 132/33 kV Trnasformer T-3 | 2016-02-10 12:16 | 2016-02-10 15:08 | 2:52 | E/O | Due to Oil leakage | 0 | 0 | No interruption
|  |  | Total : | 4:54 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Madaripur | 132/33 kV Transformer T-1 | 2016-02-06 11:21 | 2016-02-06 12:45 | 1:24 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Mogla | 132/33 kV Trnasformer T-1 | 2016-02-15 11:06 | 2016-02-15 11:17 | 0:11 | T | Tripped showing E/F relay | 27 | 4.95 | Power interruption
Gallamari | 132/33 kV Trnasformers T-1 & T2 | 2016-02-17 20:49 | 2016-02-17 21:09 | 0:20 | T | Tripped showing O/C relay | 30 | 7.5 | Power interruption
| 132/33 kV Trnasformers T-2 | 2016-02-20 08:20 | 2016-02-20 08:25 | 0:05 | T | Tripped showing inst. E/F relay | 40 | 2.6667 | Power interruption
Khulna ( C ) | 132/33 kV Trnasformers T-3 | 2016-02-20 08:20 | 2016-02-20 08:29 | 0:09 | T
| 132/33 kV Trnasformers T- 1, T-2 & T3 | 2016-02-24 15:08 | 2016-02-24 15:13 | 0:05 | T | Tripped showing inst. E/F relay | 0 | 0 | No interruption
Barisal | 132/33 kV Trnasformers T-1 & T2 | 2016-02-24 13:01 | 2016-02-24 13:08 | 0:07 | T | Tripped showing O/C relay | 42 | 4.9 | Power interruption
| 230/132 kV Trnasformer T2 | 2016-02-28 14:07 | 2016-02-28 16:56 | 2:49 | T | Tripped showing 51 HV trip at 230 kV side | 0 | 0 | No interruption
|  |  | Total : | 10:04 |  | Unserved Energy: |  | 20.0167
Bheramara HVDC Grid Circle :
Jhenaidah | 132/33 kV Trnasformer T-1 | 2016-02-06 10:37 | 2016-02-06 11:48 | 1:11 | E/O | Due to Oil leakage | 0 | 0 | No interruption
|  |  | Total : | 1:11 |  | Unserved Energy: |  | 0
Bogra Grid Circle:
Rajshahi | 132 kV bus-1 & 2 | 2016-02-08 07:50 | 2016-02-08 09:15 | 1:25 | E/O | Due to red hot maintenance | 52 | 73.6667 | Power interruption
| 132/33 kV Trnasformer T-2 | 2016-02-19 10:25 | 2016-02-20 16:50 | 30:25 | E/O | Due to Oil leakage | 0 | 0 | No interruption
|  |  | Total : | 31:50 |  | Unserved Energy: |  | 73.6667
Others :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 69:22 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: February 2016
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kishoreganj | Kishoreganj-Mymensingh 132 kV line-1 | 2016-02-01 05:12 | 2016-02-01 05:16 | 0:04 | T | Tripped showing distance relay | 244 | 16.2667 | Power interruption
| Kishoreganj-Mymensingh 132 kV line-2 | 2016-02-01 05:12 | 2016-02-01 05:17 | 0:05 | T
Mymensingh | Mymensingh-Jamalpur 132 kV line-2 | 2016-02-06 17:05 | 2016-02-06 18:18 | 1:13 | E/O | Due to air leakage | 0 | 0 | No interruption
Aminbazar | Aminbazar-Hasnabad 230 kV line-1 | 2016-02-23 06:19 | 2016-02-23 06:42 | 0:23 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
| Aminbazar-Hasnabad 230 kV line-2 | 2016-02-23 06:19 | 2016-02-23 06:44 | 0:25 | T |  | 0 | 0 | No interruption
|  |  | Total : | 2:10 |  | Unserved Energy: |  | 16.2667
Dhaka (South) Grid Circle :
Meghnaghat | Meghnaghat-Hasnabad 230 kV line-2 | 2016-02-01 01:37 | 2016-02-01 16:16 | 14:39 | T | Tripped showing dist.relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Shyampur 132 kV line | 2016-02-01 02:17 | 2016-02-01 02:30 | 0:13 | T | Tripped showing dist.Z1)relay | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Hasnabad 230 kV line-1 | 2016-02-01 15:55 | 2016-02-01 16:15 | 0:20 | T | Tripped showing dist.(Z1)relay | 0 | 0 | No interruption
| Haripur-Sonargaon 132 kV line-1 | 2016-02-01 03:12 | 2016-02-01 07:38 | 4:26 | T | Tripped showing dist.(Z1)relay | 0 | 0 | No interruption
Haripur | Haripur-Sonargaon 132 kV line-2 | 2016-02-01 03:35 | 2016-02-01 07:36 | 4:01 | T | Tripped showing dist.(Z1)relay | 0 | 0 | No interruption
| Haripur-Shyampur 132 kV line | 2016-02-01 05:24 | 2016-02-01 05:29 | 0:05 | T | Tripped showing dist.(Z1)relay | 0 | 0 | No interruption
| Haripur-Shyampur 132 kV line | 2016-02-01 06:49 | 2016-02-01 07:23 | 0:34 | T |  | 0 | 0 | No interruption
Hasnabad | Hasnabad-Shyampur 132 kV line | 2016-02-01 07:15 | 2016-02-01 07:20 | 0:05 | T | Tripped showing dist.(Z1)relay | 0 | 0 | No interruption
Soanagaon | Soanagaon-Haripur 132 kV line-1 | 2016-02-02 01:59 | 2016-02-02 08:27 | 6:28 | T | Tripped showing dist.(Z2)relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Shyampur 132 kV line | 2016-02-02 06:11 | 2016-02-02 06:32 | 0:21 | T | Tripped showing dist.(Z1)relay | 0 | 0 | No interruption
Ghorasal | Ghorashal-Ishurdi 230 kV line-1 | 2016-02-07 14:16 | 2016-02-07 15:20 | 1:04 | T | Tripped showing distance relay | 0 | 0 | No interruption
Kamrangirchar | Kamrangirchar-Hasnabad 132 kV line | 2016-02-09 15:08 | 2016-02-09 15:54 | 0:46 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Ullon | Ullon-Haripur 132 kV line | 2016-02-10 11:40 | 2016-02-10 12:11 | 0:31 | T | Tripped showing dist.(Z1)relay | 99 | 51.15 | Power interruption
Meghnaghat | Meghnaghat-Hasnabad 230 kV line-1 | 2016-02-10 06:07 | 2016-02-10 10:10 | 4:03 | T | Tripped showing dist.Z1)relay | 0 | 0 | No interruption
| Meghnaghat-Hasnabad 230 kV line-1 | 2016-02-10 06:18 | 2016-02-10 06:39 | 0:21 | T | Tripped showing dist.relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Shyampur 132 kV line | 2016-02-10 06:45 | 2016-02-10 06:54 | 0:09 | T | Tripped showing dist.Z1)relay | 40 | 6 | Power interruption
Meghnaghat | Meghnaghat-Hasnabad 230 kV line-1 | 2016-02-13 01:47 | 2016-02-13 09:06 | 7:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Meghnaghat-Hasnabad 230 kV line-2 | 2016-02-13 04:25 | 2016-02-13 09:03 | 4:38 | T | Tripped showing differential & E/F relay | 0 | 0 | No interruption
Siddhirganj Desh | Siddhirganj Desh-Siddhirganj S/S 132 kV line | 2016-02-19 08:45 | 2016-02-24 17:10 | 128:25 | T | Tripped showing inst.E/F relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Meghnaghat 230 kV line-2 | 2016-02-21 05:55 | 2016-02-21 08:49 | 2:54 | T | Tripped showing dist.relay | 0 | 0 | No interruption
Haripur | Haripur-Ullon 132 kV line | 2016-02-21 11:49 | 2016-02-21 11:56 | 0:07 | T | Tripped showing dist.relay | 75 | 8.75 | Power interruption
Ullon | Ullon-Siddhirganj 132 kV line-1 | 2016-02-21 11:49 | 2016-02-21 11:57 | 0:08 | T | Tripped showing dist.relay | 0 | 0 | No interruption
Ghorasal | Ghorashal-Ishurdi 230 kV line-2 | 2016-02-23 14:37 | 2016-02-23 15:20 | 0:43 | T | Tripped showing dist.relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Shyampur 132 kV line | 2016-02-27 15:51 | 2016-02-27 17:48 | 1:57 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 184:17 |  | Unserved Energy: |  | 65.9
Chittagong Grid Circle :
Hathazari | Hathazari-AKST 230 kV line-1 | 2016-02-04 13:03 | 2016-02-04 13:43 | 0:40 | T | Tripped showing general trip | 0 | 0 | No interruption
Madunaghat | Madunaghat-Khulshi 132 kV line-2 | 2016-02-08 12:44 | 2016-02-08 12:54 | 0:10 | T | Tripped showing dist.(Y-phase) relay | 0 | 0 | No interruption
Hathazari | Hathazari-AKSML 230 kV line | 2016-02-08 23:15 | 2016-02-09 11:03 | 11:48 | T | Tripped showing direectonal & E/F relay | 0 | 0 | No interruption
| Sikalbaha-Dohazari 132 kV line-1 & 2 | 2016-02-09 11:19 | 2016-02-09 11:43 | 0:24 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Sikalbaha-Madunaghat 132 kV line | 2016-02-09 11:19 | 2016-02-09 11:39 | 0:20 | T | Tripped showing dist.(Z3) relay | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-T.K chemical 132 kV line | 2016-02-09 11:19 | 2016-02-09 11:39 | 0:20 | T | Tripped showing dist.(B-phase) relay | 0 | 0 | No interruption
| Sikalbaha-Shah Mirpur 132 kV line- 1 & 2 | 2016-02-09 11:19 | 2016-02-09 12:01 | 0:42 | T | Tripped showing dist.(A,B,C) relay | 0 | 0 | No interruption
| Sikalbaha-Baraulia 132 kV line-1 & 2 | 2016-02-09 11:19 | 2016-02-09 11:46 | 0:27 | T | Tripped showing dist.(A,B,C) Z2 relay | 0 | 0 | No interruption
| Sikalbaha-T.K chemical 132 kV line | 2016-02-17 07:02 | 2016-02-17 07:53 | 0:51 | T | Tripped showing E/F & O/C relay | 0 | 0 | No interruption
|  |  | Total : | 15:42 |  | Unserved Energy: |  | 0
Comilla Grid Circle :
Ashuganj | Ashuganj-Sirajganj 230 kV line-2 | 2016-02-18 12:16 | 2016-02-18 12:29 | 0:13 | T | Tripped showing dist.(A,BC) Z1 relay | 0 | 0 | No interruption
Comilla (N) | Comilla (N)-BSRM 230 kV line | 2016-02-21 16:17 | 2016-02-21 19:20 | 3:03 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
| Comilla (N)-Feni 132 kV line-2 | 2016-02-22 15:37 | 2016-02-22 17:22 | 1:45 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj 132 kV line | 2016-02-24 17:22 | 2016-02-24 18:31 | 1:09 | E/O | Due to Oil leakage | 0 | 0 | No interruption
|  |  | Total : | 6:10 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Noapara | Noapara-Khulna ( C ) 132 kV line-2 | 2016-02-20 10:18 | 2016-02-20 10:23 | 0:05 | T | Tripped showing operating PRD relay | 0 | 0 | No interruption
|  |  | Total : | 0:05 |  | Unserved Energy: |  | 0
Bheramara HVDC Grid Circle :
Jessore | Jessore-Jhenidah 132 kV line-1 | 2016-02-20 15:12 | 2016-02-20 16:23 | 1:11 | T | Tripped showing dist.(Z3) relay | 10 | 11.8333 | Power interruption
| Jessore-Nopara 132 kV line-1 | 2016-02-20 15:12 | 2016-02-20 15:55 | 0:43 | T | Tripped showing E/F relay | 0 | 0 | No interruption
|  |  | Total : | 1:54 |  | Unserved Energy: |  | 11.8333
Bogra Grid Circle:
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Others :
Haripur | Haripur-Matuail 132 kV line | 2016-02-20 19:45 | 2016-02-20 19:59 | 0:14 | T | Tripped showing dist. relay | 39 | 9.1 | Power interruption
|  |  | Total : | 0:14 |  | Unserved Energy: |  | 9.1
Total outage period of Sub-station Equipment : |  |  |  | 194:50 | Hours
T = Tripping
E/O = Emergency Outage
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: February 2016
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
| 230/132 kV Trnasformer T03 | 2016-02-01 13:13 | 2016-02-01 14:07 | 0:54 | S/O | Due to annual maintenance | 30 | 7.5 | Power interruption
Aminbazar | 230/132 kV Trnasformer T1 | 2016-02-02 10:49 | 2016-02-02 11:54 | 1:05 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| 230/132 kV Trnasformer T2 | 2016-02-02 11:56 | 2016-02-02 12:41 | 0:45 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Jamalpur | 132/33 kV Trnasformer T1 | 2016-02-02 09:02 | 2016-02-02 18:35 | 9:33 | S/O | Due to painting work | 0 | 0 | No interruption
Agargaon | 132/33 kV Trnasformer T2 | 2016-02-02 12:11 | 2016-02-05 12:24 | 72:13 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Jamalpur | 132/33 kV Trnasformer T1 | 2016-02-03 08:40 | 2016-02-03 19:17 | 10:37 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| 132 kV bus-2 | 2016-02-06 09:08 | 2016-02-06 15:50 | 6:42 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Tongi | 132 kV bus-2 | 2016-02-07 09:20 | 2016-02-07 14:58 | 5:38 | S/O | Due to maintenance work | 0 | 0 | No interruption
| 132 kV bus-1 | 2016-02-08 09:20 | 2016-02-08 16:20 | 7:00 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| 132/33 kV Trnasformer T3 | 2016-02-10 07:37 | 2016-02-10 11:10 | 3:33 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Jamalpur | 132/33 kV Trnasformer T2 | 2016-02-10 09:38 | 2016-02-10 16:09 | 6:31 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| 132/33 kV Trnasformer T3 | 2016-02-10 07:37 | 2016-02-10 11:10 | 3:33 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| 132/33 kV Trnasformer T2 | 2016-02-12 09:20 | 2016-02-12 17:08 | 7:48 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Kabirpur | 132/33 kV Trnasformer T2 | 2016-02-13 07:05 | 2016-02-13 15:23 | 8:18 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| 132/33 kV Trnasformer T2 | 2016-02-13 08:38 | 2016-02-13 10:08 | 1:30 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| 132/33 kV Trnasformer T2 | 2016-02-14 09:09 | 2016-02-14 17:17 | 8:08 | S/O | Due to maintenance work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Trnasformer T2 | 2016-02-15 09:05 | 2016-02-15 17:30 | 8:25 | S/O | Due to maintenance work | 0 | 0 | No interruption
| 132/33 kV Trnasformer T2 | 2016-02-16 09:08 | 2016-02-16 17:45 | 8:37 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| 132/33 kV Trnasformer T2 | 2016-02-17 09:05 | 2016-02-17 18:07 | 9:02 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Trnasformers T1 & T3 | 2016-02-17 11:53 | 2016-02-17 19:38 | 7:45 | S/O | Due to annual maintenance | 40 | 310 | Power interruption
Jamalpur | 132/33 kV Trnasformer T2 | 2016-02-18 08:30 | 2016-02-18 18:04 | 9:34 | S/O | Due to painting work | 0 | 0 | No interruption
| 132/33 kV Trnasformer T2 | 2016-02-19 10:25 | 2016-02-19 14:21 | 3:56 | S/O | Due to painting work | 0 | 0 | No interruption
Savar | 132 kV main bus | 2016-02-20 09:48 | 2016-02-20 14:56 | 5:08 | S/O | Due to maintenance work | 60 | 308 | Power interruption
| 132/33 kV Trnasformer T1 | 2016-02-21 09:20 | 2016-02-21 15:26 | 6:06 | S/O | Due to maintenance work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Trnasformer T-3 | 2016-02-29 12:43 | 2016-02-29 13:53 | 1:10 | S/O | Due to load rearrangement work | 25 | 29.1667 | Power interruption
|  |  | Total : | 213:31 |  | Unserved Energy: |  | 654.6667
Dhaka (South) Grid Circle :
Maniknagar | 132/33 kV Trnasformer GT-1 | 2016-02-05 09:28 | 2016-02-05 16:32 | 7:04 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Haripur | 132 kV bus section -1 & 2 | 2016-02-06 10:20 | 2016-02-06 15:02 | 4:42 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Hasnabad | 230/132 kV Trnasformer T2 | 2016-02-09 07:43 | 2016-02-09 11:01 | 3:18 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Basundhara | 132/33 kV Trnasformer T-1 | 2016-02-07 08:40 | 2016-02-07 13:05 | 4:25 | S/O | Due to maintenance work | 0 | 0 | No interruption
Haripur | 132/33 kV Trnasformer T-2 | 2016-02-11 10:30 | 2016-02-11 13:55 | 3:25 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Kamrangirchar | 132/33 kV Trnasformer T-2 | 2016-02-13 08:32 | 2016-02-13 14:45 | 6:13 | S/O | Due to annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 29:07 |  | Unserved Energy: |  | 0
Chittagong Grid Circle :
Baraulia | 132 kV main bus | 2016-02-05 08:18 | 2016-02-05 11:45 | 3:27 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Aminbazar | 132 kV main bus | 2016-02-05 09:45 | 2016-02-05 16:26 | 6:41 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Madunagaht | 132/33 kV Trnasformer T-1 | 2016-02-06 09:11 | 2016-02-18 17:54 | 296:43 | S/O | Due to replacement work | 0 | 0 | No interruption
Hathazari | 132/33 kV Trnasformer T-2 | 2016-02-10 07:15 | 2016-02-10 15:27 | 8:12 | S/O | Due to development work | 0 | 0 | No interruption
| 132/33 kV Trnasformer T-1 | 2016-02-17 07:02 | 2016-02-17 14:38 | 7:36 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bhandaria | 132/33 kV Trnasformer T-1 | 2016-02-27 10:29 | 2016-02-27 12:03 | 1:34 | S/O | Due to annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 353:20 |  | Unserved Energy: |  | 0
Comilla Grid Circle :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Barisal | 132 kV bus-B | 2016-02-01 09:50 | 2016-02-01 11:58 | 2:08 | S/O | Due to project work | 0 | 0 | No interruption
Magura | 132/33 kV Trnasformer T1 | 2016-02-27 10:42 | 2016-02-27 12:03 | 1:21 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| 132/33 kV Trnasformer T2 | 2016-02-27 12:16 | 2016-02-27 13:09 | 0:53 | S/O | Due to annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 4:22 |  | Unserved Energy: |  | 0
Bheramara HVDC Grid Circle :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Bogra Grid Circle:
Natore | 132/33 kV Trnasformer T1 | 2016-02-04 09:02 | 2016-02-04 16:27 | 7:25 | S/O | Due to annual maintenance | 3 | 22.25 | Power interruption
Chapainawabganj | 132/33 kV Trnasformer T1 | 2016-02-04 09:17 | 2016-02-04 16:57 | 7:40 | S/O | Due to maintenance work | 0 | 0 | No interruption
Natore | 132/33 kV Trnasformer T1 | 2016-02-05 09:20 | 2016-02-05 12:30 | 3:10 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Chapainawabganj | 132/33 kV Trnasformer T1 | 2016-02-05 09:21 | 2016-02-05 16:35 | 7:14 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Natore | 132/33 kV Trnasformer T2 | 2016-02-06 10:40 | 2016-02-06 17:05 | 6:25 | S/O | Due to painting work | 4 | 25.6667 | Power interruption
Chapainawabganj | 132/33 kV Trnasformer T1 | 2016-02-07 09:24 | 2016-02-07 16:25 | 7:01 | S/O | Due to painting work | 0 | 0 | No interruption
Natore | 132/33 kV Trnasformer T3 | 2016-02-07 10:13 | 2016-02-07 17:20 | 7:07 | S/O | Due to painting work | 0 | 0 | No interruption
Natore | 132/33 kV Trnasformer T2 | 2016-02-08 10:22 | 2016-02-08 16:12 | 5:50 | S/O | Due to painting work | 0 | 0 | No interruption
Chapainawabganj | 132/33 kV Trnasformer T-2 | 2016-02-08 09:14 | 2016-02-08 16:42 | 7:28 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| 132/33 kV Trnasformer T-2 | 2016-02-09 09:32 | 2016-02-09 17:10 | 7:38 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Natore | 132/33 kV Trnasformer T3 | 2016-02-09 10:25 | 2016-02-09 17:09 | 6:44 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Chapainawabganj | 132/33 kV Trnasformer T-3 | 2016-02-11 10:31 | 2016-02-11 21:40 | 11:09 | S/O | Due to painting work | 0 | 0 | No interruption
|  |  | Total : | 84:51 |  | Unserved Energy: |  | 47.9167
Others :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule
maintenance: |  |  |  | 685:11 | Hours
S/O=Schedule Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: February 2016
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka Grid Circle :
| Aminbazar-Savar 132 kV line-1 | 2016-02-01 09:56 | 2016-02-01 11:56 | 2:00 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| Aminbazar-Savar 132 kV line-2 | 2016-02-01 12:05 | 2016-02-01 13:05 | 1:00 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| Aminbazar-Savar 132 kV line-2 | 2016-02-02 08:11 | 2016-02-02 12:03 | 3:52 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Aminbazar-Kallyanpur 132 kV line-1 | 2016-02-02 14:21 | 2016-02-02 14:56 | 0:35 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV line-2 | 2016-02-02 14:58 | 2016-02-02 15:19 | 0:21 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| Aminbazar-Meghnaghat 230 kV line-1 | 2016-02-03 08:53 | 2016-02-03 16:48 | 7:55 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| Aminbazar-Meghnaghat 230 kV line-1 | 2016-02-06 08:20 | 2016-02-06 16:34 | 8:14 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| Aminbazar-Meghnaghat 230 kV line-1 | 2016-02-07 09:23 | 2016-02-07 17:14 | 7:51 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| Aminbazar-Meghnaghat 230 kV line-2 | 2016-02-10 08:54 | 2016-02-10 17:09 | 8:15 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| Aminbazar-Meghnaghat 230 kV line-2 | 2016-02-11 08:23 | 2016-02-11 17:39 | 9:16 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Tongi(Old) | Tongi(Old)-Tongi new 132 kV line | 2016-02-14 10:24 | 2016-02-14 11:24 | 1:00 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Aminbazar | Aminbazar-Agargaon (Old) 230 kV line-1 | 2016-02-15 08:28 | 2016-02-15 20:43 | 12:15 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV line | 2016-02-15 09:10 | 2016-02-15 16:23 | 7:13 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-1 | 2016-02-16 12:05 | 2016-02-16 12:13 | 0:08 | S/O | Due to tree trimming | 0 | 0 | No interruption
Aminbazar | Aminbazar-Agargaon 230 kV line-2 | 2016-02-17 08:55 | 2016-02-17 17:03 | 8:08 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Savar | Savar-Aminbazar 132 kV line-1 | 2016-02-17 12:10 | 2016-02-17 17:46 | 5:36 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| Savar-Aminbazar 132 kV line-2 | 2016-02-18 09:57 | 2016-02-18 15:37 | 5:40 | S/O | Due to isolator maintenance | 0 | 0 | No interruption
Kodda | Kodda-Kabirpur 132 kV line-1 | 2016-02-19 11:14 | 2016-02-19 11:54 | 0:40 | S/O | Due to teleprotection work | 0 | 0 | No interruption
| Kodda-Kabirpur 132 kV line-2 | 2016-02-19 11:58 | 2016-02-19 12:23 | 0:25 | S/O |  | 0 | 0 | No interruption
Aminbazar | Aminbazar-Tongi 230 kV line-1 | 2016-02-20 08:35 | 2016-02-20 16:40 | 8:05 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Ashuganj 132 kV line-1 | 2016-02-20 15:12 | 2016-02-20 17:23 | 2:11 | S/O | Due to annual maintenance | 80 | 174.6667 | Power interruption
| Aminbazar-Tongi 230 kV line-1 | 2016-02-21 08:39 | 2016-02-21 17:26 | 8:47 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Aminbazar | Aminbazar-Tongi 230 kV line-1 | 2016-02-24 07:50 | 2016-02-24 16:40 | 8:50 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| Aminbazar-Tongi 230 kV line-2 | 2016-02-27 08:13 | 2016-02-27 17:41 | 9:28 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| Aminbazar-Tongi 230 kV line-2 | 2016-02-28 08:09 | 2016-02-28 17:56 | 9:47 | S/O | Due to annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 137:32 |  | Unserved Energy: |  | 174.6667
Dhaka (South) Grid Circle :
Siddhirganj | Siddhirganj-Maniknagar 230 kV line-2 | 2016-02-05 17:46 | 2016-02-05 18:26 | 0:40 | S/O | Due to maintenance work | 0 | 0 | No interruption
Lalbagh | Lalbagh-Kamrangirchar 132 kV line | 2016-02-09 08:57 | 2016-02-09 15:58 | 7:01 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kamrangirchar 132 kV line | 2016-02-12 09:21 | 2016-02-12 12:53 | 3:32 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Ullon | Ullon-Siddhirganj 132 kV line-1 | 2016-02-13 08:57 | 2016-02-13 14:52 | 5:55 | S/O | Due to isolator maintenance | 0 | 0 | No interruption
Haripur | Haripur-Rampura 230 kV line-2 | 2016-02-16 10:03 | 2016-02-16 17:35 | 7:32 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Hasnabad 230 kV line-2 | 2016-02-17 11:24 | 2016-02-17 14:16 | 2:52 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| Hasnabad-Meghnaghat 230 kV line-2 | 2016-02-27 07:20 | 2016-02-27 13:14 | 5:54 | S/O | Due to OPGW work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Meghnaghat 230 kV line-1 | 2016-02-27 13:17 | 2016-02-27 15:08 | 1:51 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Hasnabad-Meghnaghat 230 kV line-2 | 2016-02-28 09:46 | 2016-02-29 12:53 | 27:07 | S/O | Due to OPGW work | 0 | 0 | No interruption
|  |  | Total : | 62:24 |  | Unserved Energy: |  | 0
Chittagong Grid Circle :
Mdaunagaht | Mdaunagaht-Kpatai 132 kV line-1 | 2016-02-03 07:32 | 2016-02-03 14:58 | 7:26 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Juldah | Juldah-Sikalbaha 132 kV line | 2016-02-05 08:21 | 2016-02-05 14:20 | 5:59 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV line-1 | 2016-02-06 10:40 | 2016-02-06 12:04 | 1:24 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| Dohazari-Sikalbaha 132 kV line-1 | 2016-02-08 09:30 | 2016-02-08 14:42 | 5:12 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Madunaghat | Madunaghat-Hathazari 132 kV line-2 | 2016-02-12 07:38 | 2016-02-12 15:17 | 7:39 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV line | 2016-02-12 09:48 | 2016-02-12 09:59 | 0:11 | S/O | Due to project work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Hathazari 132 kV line-1 | 2016-02-13 07:55 | 2016-02-13 14:24 | 6:29 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV line-1 | 2016-02-13 09:12 | 2016-02-13 09:28 | 0:16 | S/O | For new tower erection work | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV line-1 & 2 | 2016-02-29 13:27 | 2016-02-29 13:45 | 0:18 | S/O | Due to extension work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-2 | 2016-02-29 08:15 | 2016-02-29 16:50 | 8:35 | S/O | Due to annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 43:29 |  | Unserved Energy: |  | 0
Comilla Grid Circle :
Comiila(N) | Comiila(N)-Bibiyana 230 kV line-2 | 2016-02-02 09:47 | 2016-02-02 17:09 | 7:22 | S/O | Due to annual mainteance | 0 | 0 | No interruption
Ashuganj | Ashuganj-Shahjibazar 132 kV line | 2016-02-06 09:38 | 2016-02-06 16:02 | 6:24 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Bibiyana 230 kV line | 2016-02-09 09:27 | 2016-02-09 15:41 | 6:14 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishorganj 132 kV line-1 | 2016-02-10 16:44 | 2016-02-10 18:00 | 1:16 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Ashuganj-Ghorashal 132 kV line-2 | 2016-02-12 10:01 | 2016-02-12 15:45 | 5:44 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj 132 kV P/S 132 kV line-1 | 2016-02-13 08:55 | 2016-02-13 16:23 | 7:28 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| Sylhet-Fenchuganj 132 kV line-1 | 2016-02-14 09:19 | 2016-02-14 15:46 | 6:27 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Bibiyana 230 kV line-2 | 2016-02-15 09:12 | 2016-02-15 16:23 | 7:11 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| Fenchuganj -Sylhet 132 kV line | 2016-02-15 09:28 | 2016-02-15 15:58 | 6:30 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Fenchuganj P/S | Fenchuganj P/S-Sylhet 132 kV line | 2016-02-16 09:08 | 2016-02-16 11:44 | 2:36 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sylhet 132 kV line-1 | 2016-02-17 09:12 | 2016-02-17 14:37 | 5:25 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishorganj 132 kV line-2 | 2016-02-19 08:15 | 2016-02-19 18:28 | 10:13 | S/O | Due to changing of PG clamp | 0 | 0 | No interruption
Comilla(S) | Comilla-Tripura 132 kV line-1 & 2 | 2016-02-28 09:40 | 2016-02-28 15:45 | 6:05 | S/O | Due to OPGW project work | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-2 | 2016-02-29 10:16 | 2016-02-29 12:05 | 1:49 | S/O | Due to removing nest | 0 | 0 | No interruption
Comilla(S) | Comilla-Tripura 132 kV line-1 & 2 | 2016-02-29 10:41 | 2016-02-29 16:24 | 5:43 | S/O | Due to project work | 0 | 0 | No interruption
|  |  | Total : | 86:27 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Barisal | Barisal-Patuakhali 132 kV line | 2016-02-04 08:25 | 2016-02-04 09:14 | 0:49 | S/O | Due to CT maintenance | 6 | 4.9 | Power interruption
| Barisal-Bhola 230 kV line-1 | 2016-02-20 08:25 | 2016-02-20 14:35 | 6:10 | S/O | Due to development work | 0 | 0 | No interruption
Noapara | Noapara-Jessore 132 kV line-2 | 2016-02-20 08:47 | 2016-02-20 16:21 | 7:34 | S/O | Due to conductor change | 15 | 113.5 | Power interruption
Barisal(N) | Barisal(N)-Bhola 230 kV line-2 | 2016-02-21 08:22 | 2016-02-21 11:12 | 2:50 | S/O | Due to project work | 0 | 0 | No interruption
|  |  | Total : | 17:23 |  | Unserved Energy: |  | 118.4
Bheramara HVDC Grid Circle :
Baghabari | Baghabari-Ishurdi 132 kV line-1 | 2016-02-09 09:37 | 2016-02-09 15:13 | 5:36 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Ishurdi | Ishurdi-Natore 132 kV line-1 | 2016-02-10 12:06 | 2016-02-10 14:55 | 2:49 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| Ishurdi-Bheramara 132 kV line-1 | 2016-02-24 13:10 | 2016-02-24 14:01 | 0:51 | S/O | Due to remove annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 9:16 |  | Unserved Energy: |  | 0
Bogra Grid Circle:
Rajshahi | Rajshahi-Natore 132 kV line-1 | 2016-02-10 11:02 | 2016-02-10 11:39 | 0:37 | S/O | Due to DS problem | 0 | 0 | No interruption
| Natore-Ishurdi 132 kV line-2 | 2016-02-11 10:20 | 2016-02-11 12:37 | 2:17 | S/O | Due to development work | 0 | 0 | No interruption
Natore | Natore-Rajshahi 132 kV line-1 | 2016-02-12 10:25 | 2016-02-12 12:45 | 2:20 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| Natore-Rajshahi 132 kV line-2 | 2016-02-12 14:42 | 2016-02-12 17:05 | 2:23 | S/O | Due to painting work | 0 | 0 | No interruption
Bogra | Bogra-Natore 132 kV line-1 | 2016-02-14 09:35 | 2016-02-14 13:05 | 3:30 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 11:07 |  | Unserved Energy: |  | 0
Others :
Maniknagar | Maniknagar-Bangabhaban 132 kV line-1 | 2016-02-12 09:42 | 2016-02-12 16:21 | 6:39 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| Maniknagar-Narinda 132 kV line-2 | 2016-02-21 11:45 | 2016-02-21 14:36 | 2:51 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 9:30 |  | Unserved Energy: |  | 0
Total outage period of Transmissiom Lines due to schedule
maintenance: |  |  |  | 377:08 | Hours
S/O=Schedule Outage
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month: February 2016
| Area | Previous Month (January 2016) |  |  |  | Current Month (February 2016)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 7 | - | 71 | 78 | 6 | 2 | 50 | 58
2 | Dhaka (South) Grid Circle. | 21 | 2 | 48 | 71 | 23 | 6 | 15 | 44
3 | Chittagong Grid Circle. | 3 | 1 | 23 | 27 | 9 | 3 | 16 | 28
4 | Comilla Grid Circle. | 7 | - | 51 | 58 | 5 | 3 | 15 | 23
5 | Khulna Grid Circle. | 1 | 3 | 33 | 37 | 8 | 1 | 7 | 16
6 | HVDC Grid Circle | 2 | 1 | 33 | 36 | 2 | 1 | 3 | 6
7 | Bogra Grid Circle. | 1 | - | 14 | 15 | - | 2 | 17 | 19
8 | Others . | 2 | - | 3 | 5 | 1 | - | 2 | 3
9 | Total | 44 | 7 | 276 | 327 | 54 | 18 | 125 | 197
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month: February 2016
| Area | Previous Month (January 2016) |  |  |  | Current Month (February 2016)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) grid circle. | 49.6667 | - | 7.5 | 57.1667 | 16.2667 | - | 829.3333 | 845.6
2 | Dhaka ( South) grid circle | 538.1 | - | - | 538.1 | 14.75 | 51.15 | - | 65.9
3 | Chittagong grid circle. | - | - | - | 0 | - | - | - | 0
4 | Comilla grid circle. | 20.8667 | - | 49.8333 | 70.7 | - | - | - | 0
5 | Khulna grid circle. | - | 26.25 | 76.4167 | 102.6667 | 20.0167 | - | 118.4 | 138.4167
6 | HVDC grid circle | - | - | 78.6333 | 78.6333 | 11.8333 | - | - | 11.8333
7 | Bogra grid circle. | 31.5 | - | - | 31.5 | - | 73.6667 | 47.9167 | 121.5833
8 | Others | - | - | - | 0 | 9.1 | - | - | 9.1
9 | Total | 640.1333 | 26.25 | 212.3833 | 878.7667 | 71.9667 | 124.8167 | 995.65 | 1192.4333
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month: February 2016
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 4930 | - | 4 | 4 | - | 1 | 3 | 654.6667
2 | Dhaka (South) | 4931 | - | - | 0 | - | - | - | 0
3 | Chittagong | 1872 | - | - | 0 | - | - | - | 0
4 | Khulna | 1682 | 4 | - | 4 | 4 | - | - | 20.0167
5 | Bheramara (HVDC) | 2346.9 | - | - | 0 | - | - | - | 0
6 | Bogra | 2765.89 | 1 | 2 | 3 | - | - | 3 | 121.5833
7 | Comilla | 2013.3 | - | - | 0 | - | - | - | 0
| Total | 20541.09 | [6 empty] | 796.2667
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 100%
2 | Dhaka (South) | 100%
3 | Chittagong | 99.98%
4 | Khulna | 99.98%
5 | Bheramara (HVDC) | 99.98% | [6 empty] | Executive Engineer
6 | Bogra | 99.95% | [6 empty] | Information Management Division
7 | Comilla | 100% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month: February 2016
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) | 1 | 1 | 2 | 1 | - | 1 | 190.9333
2 | Dhaka (South) | 965.69 |  | 4 | - | 4 | 3 | 1 | - | 75
3 | Chittagong | 917 | 20+9(Partial) | - | - | 0 | - | - | - | 0
4 | Khulna | 1238.4 | 21 | - | 2 | 2 | - | 1 | 1 | 118.4
5 | Bheramara (HVDC) | 598.7 |  | 1 | - | 1 | - | - | 1 | 11.8333
6 | Bogra | 1803.3 | 38 | - | - | 0 | - | - | - | 0
7 | Comilla | 1648.16 | 17 | - | - | 0 | - | - | - | 0
| Total | 8837.53 | 150+24(Partial) | [6 empty] | 407.1667
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 100%
2 | Dhaka (South) | 99.9%
3 | Chittagong | 99.99%
4 | Khulna | 100%
5 | Bheramara (HVDC) | 100% | [7 empty] | Executive Engineer
6 | Bogra | 100% | [7 empty] | Information Management Division
7 | Comilla | 99.99% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month: February 2016
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2016-02-01 | 6 | 0/42 | - | - | - | - | - | - | - | - | - | -
Note:-If U/F operates due to tripping of a generator is accounted in the category "Trouble in Generation System ".
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month: February 2016
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
|  | 0:04 | 244 | 16.2667 | Due to tripping of Kishoreganj-Mymensingh 132 kV line-1
Kishoreganj | 3 | 7:45 | 40 | 310 | Due to schedule outage of 132/33 kV Transformer-T1&T3
|  | 2:11 | 80 | 174.6667 | Due to schedule outage of Kishoreganj-Ashuganj 132 kV line-1
Aminbazar | 1 | 0:15 | 30 | 7.5 | Due to schedule outage of 230/132 kV Auto Transformer-T03
Savar | 1 | 5:08 | 60 | 308 | Due to schedule outage of 132 kV Bus
Mymensing | 1 | 1:10 | 25 | 29.1667 | Due to schedule outage of 132/33 kV Transformer-T3
Ullon | 1 | 0:31 | 99 | 51.15 | Due to tripping of Ullon-Haripur 132 kV line
Haripur | 2 | 0:07 | 75 | 8.75 | Due to tripping of Haripur-Ullon 132 kV line
|  | 0:14 | 39 | 9.1 | Due to tripping of Haripur-Matuail 132 kV line
Hasnabad | 1 | 0:09 | 40 | 6 | Due to tripping of Hasnabad-Shyampur 132 kV line
Mongla | 1 | 0:11 | 27 | 4.95 | Due to tripping of 132/33 kV Transformer-T1
Gallamari | 1 | 0:15 | 30 | 7.5 | Due to tripping of 132/33 kV Transformer-T1 & T3
Khulna ( C ) | 1 | 0:04 | 40 | 2.6667 | Due to tripping of 132/33 kV Transformer-T2
Barisal | 2 | 0:07 | 42 | 4.9 | Due to tripping of 132/33 kV Transformer-T1&T2
|  | 0:49 | 6 | 4.9 | Due to schedule outage of Barisal-Patuakhali 132 kV line
Noapara | 1 | 7:34 | 15 | 113.5 | Due to schedule outage of Noapara-Jessore 132 kV line-2
Jessore | 1 | 1:11 | 10 | 11.8333 | Due to tripping of Jessore-Jhenaidah 132 kV line-1
Rajshahi | 1 | 1:25 | 52 | 73.6667 | Due to emergency outage of 132 kV Bus-1&2
Natore | 2 | 7:25 | 3 | 22.25 | Due to schedule outage of 132/33 kV Transformer-T1
|  | 6:25 | 4 | 25.6667 | Due to schedule outage of 132/33 kV Transformer-T2
| Total unserved energy : |  |  | 1192.4333 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:February 2016
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 120 | 23 | 2016-02-01 | 11:00
2 | Munsiganj | 84 | 29 | 2016-02-01 | 20:00
3 | Megnaghat | 45 | 23 | 2016-02-01 | 19:00
4 | Shyampur | 130 | 23 | 2016-02-01 | 12:00
5 | Bhulta | 118 | 14 | 2016-02-01 | 21:00
6 | Madanganj | 47 | 20 | 2016-02-01 | 14:00
7 | Shitalakhya | 88 | 23 | 2016-02-01 | 18:30
8 | Rahim steel | 12 | 4 | 2016-02-01 | 15:00
9 | Matuail | 61 | 25 | 2016-02-01 | 10:00
10 | Ghorasal | 84 | 27 | 2016-02-01 | 19:00
11 | Narsingdi | 75 | 12 | 2016-02-01 | 18:30
12 | Haripur (SBU) | 76 | 27 | 2016-02-01 | 19:30
13 | Ullon | 79 | 27 | 2016-02-01 | 18:00
14 | Hasnabad | 136 | 23 | 2016-02-01 | 19:30
15 | Magbazar | 128 | 22 | 2016-02-01 | 15:00
16 | Maniknagar | 70 | 22 | 2016-02-01 | 19:30
17 | Bangabhaban | 38 | 23 | 2016-02-01 | 12:00
18 | Narinda | 72 | 3 | 2016-02-01 | 16:00
19 | Dhanmondi | 118 | 29 | 2016-02-01 | 13:00
20 | Lalbag | 82 | 1 | 2016-02-01 | 12:00
21 | Madartek | 34 | 20 | 2016-02-01 | 22:00
22 | Mirpur | 90 | 13 | 2016-02-01 | 18:30
23 | Kalyanpur | 102 | 29 | 2016-02-01 | 18:30
24 | Gulshan | 112 | 23 | 2016-02-01 | 13:00
25 | Uttara | 84 | 23 | 2016-02-01 | 19:00
26 | Kamrangirchar | 80 | 27 | 2016-02-01 | 18:30
27 | Savar | 94 | 22 | 2016-02-01 | 18:30
28 | Bhasantec | 103 | 23 | 2016-02-01 | 19:00
29 | Agargaon | 23 | 23 | 2016-02-01 | 19:30
30 | Satmosjid | 48 | 9 | 2016-02-01 | 9:00
31 | Tongi | 97 | 28 | 2016-02-01 | 18:30
32 | Kabirpur | 177 | 18 | 2016-02-01 | 15:00
33 | Basundhara | 110 | 28 | 2016-02-01 | 18:00
34 | Manikganj | 80 | 18 | 2016-02-01 | 21:00
35 | Joydevpur | 219 | 27 | 2016-02-01 | 18:30
36 | New Tongi | 98 | 28 | 2016-02-01 | 12:00
37 | Tangail | 131 | 10 | 2016-02-01 | 21:00
38 | Mymensing | 147 | 23 | 2016-02-01 | 20:00
39 | Kishorganj | 57 | 10 | 2016-02-01 | 19:00
40 | Netrokona | 65 | 7 | 2016-02-01 | 18:00
41 | Jamalpur | 77 | 18 | 2016-02-01 | 7:00
42 | Sherpur | 53 | 12 | 2016-02-01 | 18:00
43 | Srimongal | 24 | 20 | 2016-02-01 | 18:30
44 | Shahjibazar | 52 | 18 | 2016-02-01 | 18:30
45 | Fenchuganj | 25 | 20 | 2016-02-01 | 19:00
46 | Khulawara | 27 | 20 | 2016-02-01 | 18:30
47 | Sylhet | 119 | 20 | 2016-02-01 | 19:00
48 | Chatak | 42 | 22 | 2016-02-01 | 19:00
49 | Comilla (S) | 145 | 28 | 2016-02-01 | 18:30
50 | Comilla(N) | 80 | 19 | 2016-02-01 | 21:00
51 | Chandpur | 80 | 18 | 2016-02-01 | 19:00
52 | Feni | 72 | 7 | 2016-02-01 | 20:00
53 | Chowmuhani | 148 | 23 | 2016-02-01 | 20:00
54 | Ashuganj | 53 | 23 | 2016-02-01 | 21:00
55 | Daudkandi | 60 | 23 | 2016-02-01 | 18:30
56 | B.Baria | 78 | 22 | 2016-02-01 | 20:00
57 | Madanhat | 43 | 24 | 2016-02-01 | 20:00
58 | Hathazari | 85 | 27 | 2016-02-01 | 18:30
59 | Khulshi | 155 | 19 | 2016-02-01 | 12:00
60 | Halishahar | 115 | 29 | 2016-02-01 | 19:30
61 | Baraulia | 109 | 27 | 2016-02-01 | 9:00
62 | Sikalbaha | 34 | 4 | 2016-02-01 | 19:30
63 | Dohazari | 66 | 3 | 2016-02-01 | 19:30
64 | Cox'sbazar | 62 | 20 | 2016-02-01 | 20:00
65 | Chandraghona | 28 | 22 | 2016-02-01 | 19:30
66 | Kaptai | 4 | 11 | 2016-02-01 | 18:30
67 | A. Khaer Stl. | 30.4 | 7 | 2016-02-01 | 11:00
68 | Bakulia | 100 | 29 | 2016-02-01 | 19:00
69 | Julda | 28 | 15 | 2016-02-01 | 6:00
70 | TK chemical | 9 | 1 | 2016-02-01 | 12:00
71 | Modern Steel | 19 | 25 | 2016-02-01 | 9:00
72 | Shahmirpur | 30.3 | 15 | 2016-02-01 | 18:00
73 | Abul Khair 230 | 193 | 29 | 2016-02-01 | 3:00
74 | BSRM | 68 | 18 | 2016-02-01 | 12:00
75 | Goalpara | 42 | 25 | 2016-02-01 | 19:00
76 | Central s/s | 72 | 20 | 2016-02-01 | 18:30
77 | Noapara | 53 | 20 | 2016-02-01 | 19:00
78 | Jessore | 116 | 28 | 2016-02-01 | 18:30
79 | Jhenida | 66 | 17 | 2016-02-01 | 19:00
80 | Bottail | 74 | 15 | 2016-02-01 | 19:00
81 | G.K Project | 34 | 15 | 2016-02-01 | 19:30
82 | Faridpur | 100 | 8 | 2016-02-01 | 19:30
83 | Madaripur | 89 | 21 | 2016-02-01 | 21:00
84 | Gopalganj | 39.8 | 21 | 2016-02-01 | 20:00
85 | Bagerhat | 61 | 20 | 2016-02-01 | 20:00
86 | Mongla | 29 | 9 | 2016-02-01 | 10:00
87 | Satkhira | 62.2 | 20 | 2016-02-01 | 20:00
88 | Gallamari | 43 | 24 | 2016-02-01 | 12:00
89 | Magura | 30 | 27 | 2016-02-01 | 19:00
90 | Chuadanga | 46 | 6 | 2016-02-01 | 18:00
91 | Barisal | 86 | 25 | 2016-02-01 | 20:00
92 | Patuakhali | 47 | 6 | 2016-02-01 | 20:00
93 | Bhandaria | 30 | 29 | 2016-02-01 | 18:30
94 | Ishurdi | 36 | 24 | 2016-02-01 | 19:00
95 | Natore | 77 | 18 | 2016-02-01 | 19:00
96 | Bogra | 186 | 23 | 2016-02-01 | 19:30
97 | Noagaon | 101 | 20 | 2016-02-01 | 19:00
98 | Rajshahi | 99 | 29 | 2016-02-01 | 19:00
99 | C.Nawabganj | 53 | 4 | 2016-02-01 | 18:30
100 | Amnura | 23 | 29 | 2016-02-01 | 19:00
101 | Pabna | 72 | 18 | 2016-02-01 | 19:00
102 | Shahjadpur | 65 | 21 | 2016-02-01 | 19:30
103 | Serajganj | 69 | 20 | 2016-02-01 | 10:00
104 | Niyamatpur | 71 | 3 | 2016-02-01 | 18:00
105 | Joypurhat | 35 | 4 | 2016-02-01 | 18:30
106 | Rangpur | 83 | 10 | 2016-02-01 | 19:00
107 | Lalmonirhat | 61 | 23 | 2016-02-01 | 18:30
108 | Saidpur | 90 | 29 | 2016-02-01 | 19:00
109 | Purbasadipur | 71 | 3 | 2016-02-01 | 20:00
110 | Thakurgaon | 54 | 24 | 2016-02-01 | 19:00
111 | Palashbari | 72 | 23 | 2016-02-01 | 19:00
112 | Barapukuria | 42 | 6 | 2016-02-01 | 9:00
113 | Panchagar | 34 | 25 | 2016-02-01 | 19:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month: February 2016
Area | MW | Date | Hour | Remarks
Dhaka | 2865 | 23.02.16 | 19:00
Chittagong | 890 | 24.02.16 | 21:00
Khulna | 861 | 22.02.16 | 19:00
Rajshahi | 831 | 23.02.16 | 19:30
Comilla | 653 | 27.02.16 | 20:00
Mymensingh | 511 | 24.02.16 | 10:00
Sylhet | 284 | 20.02.16 | 19:30
Barisal | 158 | 23.02.16 | 20:00
Rangpur | 463 | 25.02.16 | 19:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: February 2016
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 234 | 5 | 2016-02-01 | 14:00 | 218 | 12 | 2016-02-01 | 1:00
2 | Ishurdi | 230 | 237 | 8 | 2016-02-01 | 3:00 | 220 | 17 | 2016-02-01 | 13:00
3 | Ashuganj | 230 | 239 | 29 | 2016-02-01 | 1:00 | 230 | 21 | 2016-02-01 | 1:00
4 | Serajganj | 230 | 235 | 22 | 2016-02-01 | 13:00 | 215 | 24 | 2016-02-01 | 12:00
5 | Baghabari | 230 | 228 | 5 | 2016-02-01 | 14:00 | 218 | 11 | 2016-02-01 | 7:00
6 | Barapukuria | 230 | 230 | 21 | 2016-02-01 | 14:00 | 215 | 5 | 2016-02-01 | 9:00
7 | Bogra | 230 | 227 | 4 | 2016-02-01 | 3:00 | 208 | 13 | 2016-02-01 | 9:00
8 | Khulna South | 230 | 237 | 8 | 2016-02-01 | 23:00 | 217 | 1 | 2016-02-01 | 7:00
9 | Rampura | 230 | 235 | 1 | 2016-02-01 | 22:00 | 209 | 22 | 2016-02-01 | 10:00
10 | Haripur | 230 | 222 | 5 | 2016-02-01 | 15:00 | 210 | 22 | 2016-02-01 | 10:00
11 | Hasnabad | 230 | 229 | 5 | 2016-02-01 | 10:00 | 207 | 22 | 2016-02-01 | 10:00
12 | Aminbazar | 230 | 226 | 5 | 2016-02-01 | 13:00 | 205 | 22 | 2016-02-01 | 11:00
13 | Tongi | 230 | 232 | 8 | 2016-02-01 | 16:00 | 202 | 18 | 2016-02-01 | 18:00
14 | Comilla (N) | 230 | 233 | 5 | 2016-02-01 | 21:00 | 215 | 22 | 2016-02-01 | 15:00
15 | Hathazari | 230 | 226 | 5 | 2016-02-01 | 18:30 | 203 | 14 | 2016-02-01 | 1:00
16 | Megnaghat | 230 | 230 | 5 | 2016-02-01 | 15:00 | 211 | 22 | 2016-02-01 | 15:00
17 | Fenchuganj | 230 | 239 | 4 | 2016-02-01 | 6:00 | 220 | 25 | 2016-02-01 | 16:00
18 | Siddhirganj | 230 | 234 | 5 | 2016-02-01 | 18:30 | 210 | 20 | 2016-02-01 | 11:00
19 | Maniknagar | 230 | 233 | 5 | 2016-02-01 | 18:30 | 207 | 3 | 2016-02-01 | 12:00
20 | Old Airport | 230 | 226 | 5 | 2016-02-01 | 10:00 | 205 | 22 | 2016-02-01 | 10:00
21 | Barisal | 230 | 242 | 2 | 2016-02-01 | 24:00: | 205 | 26 | 2016-02-01 | 13:00
22 | AKSML | 230 | 228 | 5 | 2016-02-01 | 19:00 | 199 | 14 | 2016-02-01 | 1:00
23 | BSRM | 230 | 229 | 5 | 2016-02-01 | 19:00 | 203 | 14 | 2016-02-01 | 1:00
132 kV Substation
1 | Siddhirganj | 132 | 141 | 5 | 2016-02-01 | 18:30 | 128 | 20 | 2016-02-01 | 10:00
2 | Munsiganj | 132 | 141 | 5 | 2016-02-01 | 18:30 | 127 | 3 | 2016-02-01 | 12:00
3 | Megnaghat | 132 | 139 | 5 | 2016-02-01 | 18:00 | 125 | 3 | 2016-02-01 | 12:00
4 | Shyampur | 132 | 137 | 24 | 2016-02-01 | 12:00 | 119 | 16 | 2016-02-01 | 12:00
5 | Bhulta | 132 | 129 | 5 | 2016-02-01 | 18:00 | 117 | 3 | 2016-02-01 | 11:00
6 | Madanganj | 132 | 141 | 5 | 2016-02-01 | 18:00 | 125 | 3 | 2016-02-01 | 11:00
7 | Shitalakhya | 132 | 138 | 5 | 2016-02-01 | 17:00 | 119 | 22 | 2016-02-01 | 10:00
8 | Rahim Steal | 132 | 140 | 5 | 2016-02-01 | 18:00 | 128 | 20 | 2016-02-01 | 9:00
9 | Matuail | 132 | 140 | 5 | 2016-02-01 | 18:30 | 126 | 20 | 2016-02-01 | 11:00
10 | Ghorasal | 132 | 142 | 5 | 2016-02-01 | 16:00 | 124 | 21 | 2016-02-01 | 15:00
11 | Narsinghdi | 132 | 142 | 5 | 2016-02-01 | 13:00 | 125 | 20 | 2016-02-01 | 11:00
12 | Haripur (SBU) | 132 | 140 | 5 | 2016-02-01 | 18:30 | 127 | 3 | 2016-02-01 | 12:00
13 | Ullon | 132 | 140 | 24 | 2016-02-01 | 12:00 | 125 | 3 | 2016-02-01 | 12:00
14 | Hasnabad | 132 | 138 | 24 | 2016-02-01 | 12:00 | 120 | 22 | 2016-02-01 | 15:00
15 | Magbazar | 132 | 135 | 7 | 2016-02-01 | 1:00 | 120 | 28 | 2016-02-01 | 15:00
16 | Maniknagar | 132 | 136 | 24 | 2016-02-01 | 13:00 | 120 | 28 | 2016-02-01 | 15:00
17 | Bangabhaban | 132 | 135 | 2 | 2016-02-01 | 6:00 | 113 | 28 | 2016-02-01 | 14:00
18 | Narinda | 132 | 136 | 6 | 2016-02-01 | 4:00 | 120 | 22 | 2016-02-01 | 8:00
19 | Dhanmondi | 132 | 137 | 2 | 2016-02-01 | 6:00 | 123 | 16 | 2016-02-01 | 12:00
20 | Lalbag | 132 | 134 | 5 | 2016-02-01 | 17:00 | 113 | 28 | 2016-02-01 | 14:00
21 | Madartek | 132 | 136 | 6 | 2016-02-01 | 4:00 | 120 | 22 | 2016-02-01 | 8:00
22 | Mirpur | 132 | 134 | 2 | 2016-02-01 | 7:00 | 119 | 23 | 2016-02-01 | 11:00
23 | Kalyanpur | 132 | 137 | 5 | 2016-02-01 | 3:00 | 120 | 11 | 2016-02-01 | 12:00
24 | Gulshan | 132 | 135 | 7 | 2016-02-01 | 5:00 | 120 | 22 | 2016-02-01 | 10:00
25 | Uttara | 132 | 134 | 6 | 2016-02-01 | 2:00 | 119 | 28 | 2016-02-01 | 10:00
26 | Kamrangirchar | 132 | 134 | 12 | 2016-02-01 | 5:00 | 114 | 22 | 2016-02-01 | 10:00
27 | Savar | 132 | 135 | 6 | 2016-02-01 | 3:00 | 121 | 15 | 2016-02-01 | 11:00
28 | Bhasantec | 132 | 136 | 6 | 2016-02-01 | 4:00 | 122 | 22 | 2016-02-01 | 12:00
29 | Agargaon | 132 | 136 | 6 | 2016-02-01 | 2:00 | 123 | 22 | 2016-02-01 | 12:00
30 | Satmosjid | 132 | 136 | 7 | 2016-02-01 | 4:00 | 122 | 22 | 2016-02-01 | 10:00
31 | Tongi | 132 | 138 | 2 | 2016-02-01 | 6:00 | 124 | 9 | 2016-02-01 | 8:00
32 | Kabirpur | 132 | 140 | 1 | 2016-02-01 | 22:00 | 122 | 20 | 2016-02-01 | 15:00
33 | Basundhara | 132 | 139 | 11 | 2016-02-01 | 2:00 | 115 | 28 | 2016-02-01 | 15:00
34 | Manikganj | 132 | 137 | 24 | 2016-02-01 | 3:00 | 123 | 10 | 2016-02-01 | 12:00
35 | Joydevpur | 132 | 141 | 6 | 2016-02-01 | 19:30 | 124 | 22 | 2016-02-01 | 9:00
36 | New Tongi | 132 | 135 | 1 | 2016-02-01 | 1:00 | 121 | 15 | 2016-02-01 | 12:00
37 | Tangail | 132 | 134 | 25 | 2016-02-01 | 1:00 | 110 | 16 | 2016-02-01 | 19:00
38 | Mymensing | 132 | 134 | 12 | 2016-02-01 | 4:00 | 115 | 20 | 2016-02-01 | 18:30
39 | Kishorganj | 132 | 135 | 5 | 2016-02-01 | 6:00 | 120 | 29 | 2016-02-01 | 19:30
40 | Netrokona | 132 | 135 | 12 | 2016-02-01 | 2:00 | 110 | 23 | 2016-02-01 | 14:00
41 | Jamalpur | 132 | 131 | 12 | 2016-02-01 | 3:00 | 110 | 11 | 2016-02-01 | 11:00
42 | Sherpur | 132 | 132 | 1 | 2016-02-01 | 6:00 | 108 | 20 | 2016-02-01 | 9:00
43 | Srimongal | 132 | 143 | 1 | 2016-02-01 | 2:00 | 140 | 16 | 2016-02-01 | 9:00
44 | Shahjibazar | 132 | 143 | 26 | 2016-02-01 | 8:00 | 138 | 3 | 2016-02-01 | 12:00
45 | Fenchuganj | 132 | 141 | 2 | 2016-02-01 | 2:00 | 124 | 16 | 2016-02-01 | 13:00
46 | Khulawara | 132 | 141 | 10 | 2016-02-01 | 4:00 | 135 | 20 | 2016-02-01 | 18:30
47 | Sylhet | 132 | 139 | 4 | 2016-02-01 | 17:00 | 134 | 20 | 2016-02-01 | 20:00
48 | Chattak | 132 | 139 | 2 | 2016-02-01 | 3:00 | 133 | 22 | 2016-02-01 | 19:00
49 | Comilla(South) | 132 | 140 | 5 | 2016-02-01 | 13:00 | 125 | 13 | 2016-02-01 | 19:30
50 | Comilla (North) | 132 | 140 | 5 | 2016-02-01 | 22:00 | 126 | 28 | 2016-02-01 | 19:30
51 | Chandpur | 132 | 140 | 24 | 2016-02-01 | 7:00 | 116 | 23 | 2016-02-01 | 22:00
52 | Feni | 132 | 127 | 5 | 2016-02-01 | 11:00 | 112 | 22 | 2016-02-01 | 18:30
53 | Chowmuhani | 132 | 136 | 24 | 2016-02-01 | 9:00 | 114 | 13 | 2016-02-01 | 19:30
54 | Ashuganj | 132 | 140 | 1 | 2016-02-01 | 1:00 | 133 | 20 | 2016-02-01 | 16:00
55 | Daudkandi | 132 | 140 | 5 | 2016-02-01 | 18:30 | 125 | 22 | 2016-02-01 | 12:00
56 | Brahminbaria | 132 | 141 | 6 | 2016-02-01 | 14:00 | 132 | 26 | 2016-02-01 | 18:00
57 | Madanhat | 132 | 141 | 1 | 2016-02-01 | 21:00 | 120 | 16 | 2016-02-01 | 1:00
58 | Hathazari | 132 | 137 | 5 | 2016-02-01 | 19:00 | 123 | 14 | 2016-02-01 | 1:00
59 | Khulshi | 132 | 141 | 6 | 2016-02-01 | 19:00 | 122 | 14 | 2016-02-01 | 1:00
60 | Halishahar | 132 | 138 | 5 | 2016-02-01 | 19:00 | 120 | 12 | 2016-02-01 | 24:00
61 | Baraulia | 132 | 136 | 5 | 2016-02-01 | 19:00 | 121 | 27 | 2016-02-01 | 1:00
62 | Sikalbaha | 132 | 138 | 5 | 2016-02-01 | 19:00 | 120 | 12 | 2016-02-01 | 24:00
63 | Dohazari | 132 | 137 | 2 | 2016-02-01 | 21:00 | 120 | 12 | 2016-02-01 | 24:00
64 | Cox'sbazar | 132 | 135 | 1 | 2016-02-01 | 19:00 | 117 | 12 | 2016-02-01 | 24:00
65 | Chandraghona | 132 | 137 | 1 | 2016-02-01 | 19:00 | 123 | 14 | 2016-02-01 | 01:00
66 | Kaptai | 132 | 137 | 6 | 2016-02-01 | 18:00 | 121 | 27 | 2016-02-01 | 12:00
67 | A. Khaer Stl. | 132 | 135 | 5 | 2016-02-01 | 18:30 | 122 | 13 | 2016-02-01 | 19:30
68 | Bakulia | 132 | 136 | 3 | 2016-02-01 | 22:00 | 118 | 14 | 2016-02-01 | 1:00
69 | Julda | 132 | 137 | 5 | 2016-02-01 | 19:00 | 117 | 14 | 2016-02-01 | 1:00
70 | TK Chemical | 132 | 140 | 5 | 2016-02-01 | 19:00 | 120 | 14 | 2016-02-01 | 1:00
71 | Modern Steel | 132 | 137 | 5 | 2016-02-01 | 19:00 | 119 | 14 | 2016-02-01 | 2:00
72 | Shahmirpur | 132 | 137 | 5 | 2016-02-01 | 19:00 | 118 | 14 | 2016-02-01 | 1:00
73 | Goalpara | 132 | 140 | 1 | 2016-02-01 | 4:00 | 131 | 10 | 2016-02-01 | 7:00
74 | Khulna Central | 132 | 140 | 2 | 2016-02-01 | 22:00 | 131 | 22 | 2016-02-01 | 8:00
75 | Noapara | 132 | 138 | 1 | 2016-02-01 | 21:00 | 119 | 5 | 2016-02-01 | 18:30
76 | Jessore | 132 | 136 | 1 | 2016-02-01 | 22:00 | 119 | 21 | 2016-02-01 | 19:00
77 | Jhenida | 132 | 135 | 6 | 2016-02-01 | 23:00 | 113 | 21 | 2016-02-01 | 19:30
78 | Bottail | 132 | 138 | 6 | 2016-02-01 | 3:00 | 121 | 1 | 2016-02-01 | 13:00
79 | G.K.Project | 132 | 140 | 25 | 2016-02-01 | 5:00 | 128 | 11 | 2016-02-01 | 8:00
80 | Faridpur | 132 | 137 | 1 | 2016-02-01 | 3:00 | 123 | 4 | 2016-02-01 | 9:00
81 | Madaripur | 132 | 139 | 9 | 2016-02-01 | 2:00 | 115 | 25 | 2016-02-01 | 13:00
82 | Gopalganj | 132 | 142 | 2 | 2016-02-01 | 23:00 | 123 | 16 | 2016-02-01 | 12:00
83 | Bagerhat | 132 | 140 | 24 | 2016-02-01 | 14:00 | 125 | 14 | 2016-02-01 | 20:00
84 | Mongla | 132 | 139 | 24 | 2016-02-01 | 9:00 | 112 | 10 | 2016-02-01 | 7:00
85 | Satkhira | 132 | 141 | 24 | 2016-02-01 | 5:00 | 127 | 19 | 2016-02-01 | 18:30
86 | Gallamari | 132 | 141 | 24 | 2016-02-01 | 24:00 | 131 | 1 | 2016-02-01 | 19:00
87 | Magura | 132 | 140 | 1 | 2016-02-01 | 22:00 | 120 | 19 | 2016-02-01 | 19:30
88 | Chuadanga | 132 | 139 | 12 | 2016-02-01 | 23:00 | 112 | 21 | 2016-02-01 | 19:30
89 | Barisal | 132 | 145 | 24 | 2016-02-01 | 9:00 | 119 | 1 | 2016-02-01 | 19:30
90 | Patuakhali | 132 | 138 | 25 | 2016-02-01 | 3:00 | 125 | 16 | 2016-02-01 | 12:00
91 | Bhandaria | 132 | 140 | 24 | 2016-02-01 | 9:00 | 121 | 14 | 2016-02-01 | 18:30
92 | Ishurdi | 132 | 139 | 2 | 2016-02-01 | 17:00 | 125 | 1 | 2016-02-01 | 19:00
93 | Natore | 132 | 137 | 1 | 2016-02-01 | 18:00 | 125 | 15 | 2016-02-01 | 12:00
94 | Bogra | 132 | 136 | 1 | 2016-02-01 | 14:00 | 119 | 22 | 2016-02-01 | 8:00
95 | Noagaon | 132 | 135 | 1 | 2016-02-01 | 3:00 | 115 | 22 | 2016-02-01 | 9:00
96 | Rajshahi | 132 | 137 | 2 | 2016-02-01 | 17:00 | 122 | 14 | 2016-02-01 | 8:00
97 | C.Nawabganj | 132 | 136 | 1 | 2016-02-01 | 12:00 | 117 | 8 | 2016-02-01 | 8:00
98 | Amnura | 132 | 141 | 18 | 2016-02-01 | 18:00 | 120 | 8 | 2016-02-01 | 8:00
99 | Pabna | 132 | 128 | 18 | 2016-02-01 | 19:00 | 125 | 4 | 2016-02-01 | 8:00
100 | Shahjadpur | 132 | 138 | 14 | 2016-02-01 | 3:00 | 135 | 15 | 2016-02-01 | 9:00
101 | Serajganj | 132 | 138 | 1 | 2016-02-01 | 1:00 | 121 | 24 | 2016-02-01 | 1:00
102 | Niyamatpur | 132 | 131 | 8 | 2016-02-01 | 4:00 | 109 | 22 | 2016-02-01 | 8:00
103 | Joypurhat | 132 | 134 | 10 | 2016-02-01 | 5:00 | 114 | 25 | 2016-02-01 | 9:00
104 | Rangpur | 132 | 129 | 5 | 2016-02-01 | 5:00 | 112 | 13 | 2016-02-01 | 9:00
105 | Lalmonirhat | 132 | 125 | 8 | 2016-02-01 | 24:00 | 106 | 13 | 2016-02-01 | 9:00
106 | Saidpur | 132 | 132 | 2 | 2016-02-01 | 3:00 | 111 | 13 | 2016-02-01 | 9:00
107 | Purbasadipur | 132 | 130 | 5 | 2016-02-01 | 4:00 | 112 | 13 | 2016-02-01 | 9:00
108 | Thakurgaon | 132 | 122 | 1 | 2016-02-01 | 19:30 | 113 | 23 | 2016-02-01 | 19:30
109 | Palashbari | 132 | 130 | 4 | 2016-02-01 | 1:00 | 114 | 25 | 2016-02-01 | 8:00
110 | Barapukuria | 132 | 130 | 1 | 2016-02-01 | 3:00 | 115 | 5 | 2016-02-01 | 9:00
111 | Panchagar | 132 | 124 | 10 | 2016-02-01 | 18:30 | 101 | 25 | 2016-02-01 | 19:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month: February 2016
| Name of the | Auto transofrmer |  | Recorded maximum load
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kv side ) | Date | Time | Remarks
|  | TR1 | 225 | 105 | 325
IP-299421 | Hasnabad | TR2 | 225 | 90 | 315 | 26.02.16 | 9:00
|  | TR3 | 225 | 90 | 310
|  | TR1 | 225 | 140 | 435
IP-299866 | Tongi | TR2 | 225 | 140 | 435 | 16.02.16 | 18:00
|  | TR3 | 225 | 140 | 435
|  | TR1 | 225 | 109 | 320
IP-299427 | Haripur | TR2 | 225 | 109 | 320 | 03.02.16 | 24:00
|  | TR3 | 225 | 109 | 320
|  | TR1 | 225 | 165 | 520
IP-299728 | Rampura | TR2 | 225 | 165 | 520 | 29.02.16 | 12:00
|  | TR3 | 225 | 165 | 520
|  | TR1 | 225 | 116 | 331
IP-299264 | Aminbazar | TR2 | 225 | 116 | 331 | 29.02.16 | 19:00
|  | TR3 | 225 | 121 | 345
| Maniknagar | TR1 | 300 | 81 | 260 | 28.02.16 | 12:00
|  | TR2 | 300 | 81 | 260
IP-399266 | Comilla(N) | TR1 | 225 | 160 | 450 | 22.02.16 | 24:00
|  | TR2 | 225 | 156 | 431
| Fenchuganj | TR1 | 300 | 288 | 744 | 08.02.16 | 11:00
|  | TR1 | 150 | 92 | 245
| Hathazari | TR2 | 150 | 92 | 245 | 05.02.16 | 24:00
IP-399428 |  | TR3 | 150 | 92 | 245
|  | TR4 | 150 | 92 | 245
|  | TR1 | 225 | 160 | 450
| Ishurdi | TR2 | 225 | 160 | 450 | 16.02.16 | 08:00
IP-499474 |  | TR3 | 225 | 160 | 450
| Khulna(S) | TR1 | 225 | 143 | 371 | 22.02.16 | 02:00
IP-58001/58002 |  | TR2 | 225 | 143 | 371
| Bogra | TR1 | 225 | 163 | 512 | 11.02.16 | 20:00
IP-43002/499264 |  | TR2 | 225 | 163 | 512
IP-499224 | Baghabari | TR1 | 225 | 100 | 300 | 11.02.16 | 9:00
| Barapukuria | TR1 | 225 | 161 | 805 | 26.02.16 | 21:00
IP-499228 |  | TR2 | 225 | 161 | 805
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month: February 2016 | [6 empty] | (For Evening Peak) | [7 empty] | Month: February 2016 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-02-16 | 7024 | 7024 | 0 | 19:30 | - | - | - | - | - | - | - | - | - | - | 01-02-16 | 5837 | 5837 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
02-02-16 | 7042 | 7042 | 0 | 19:30 | - | - | - | - | - | - | - | - | - | - | 02-02-16 | 5813 | 5813 | 0 | 9:00 | - | - | - | - | - | - | - | - | - | -
03-02-16 | 7041 | 7041 | 0 | 18:30 | - | - | - | - | - | - | - | - | - | - | 03-02-16 | 5901 | 5901 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
04-02-16 | 6881 | 6881 | 0 | 19:00 | - | - | - | - | - | - | - | - | - | - | 04-02-16 | 5662 | 5662 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
05-02-16 | 6300 | 6300 | 0 | 20:00 | - | - | - | - | - | - | - | - | - | - | 05-02-16 | 4836 | 4836 | 0 | 9:00 | - | - | - | - | - | - | - | - | - | -
06-02-16 | 7074 | 7074 | 0 | 19:00 | - | - | - | - | - | - | - | - | - | - | 06-02-16 | 5338 | 5338 | 0 | 9:00 | - | - | - | - | - | - | - | - | - | -
07-02-16 | 7127 | 7127 | 0 | 19:00 | - | - | - | - | - | - | - | - | - | - | 07-02-16 | 5755 | 5755 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
08-02-16 | 7155 | 7155 | 0 | 19:00 | - | - | - | - | - | - | - | - | - | - | 08-02-16 | 5692 | 5692 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
09-02-16 | 7214 | 7214 | 0 | 19:00 | - | - | - | - | - | - | - | - | - | - | 09-02-16 | 5868 | 5868 | 0 | 11:00 | - | - | - | - | - | - | - | - | - | -
10-02-16 | 7194 | 7194 | 0 | 19:00 | - | - | - | - | - | - | - | - | - | - | 10-02-16 | 5726 | 5726 | 0 | 9:00 | - | - | - | - | - | - | - | - | - | -
11-02-16 | 7153 | 7153 | 0 | 19:30 | - | - | - | - | - | - | - | - | - | - | 11-02-16 | 5885 | 5885 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
12-02-16 | 6584 | 6584 | 0 | 19:00 | - | - | - | - | - | - | - | - | - | - | 12-02-16 | 4745 | 4745 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
13-02-16 | 7160 | 7160 | 0 | 19:00 | - | - | - | - | - | - | - | - | - | - | 13-02-16 | 5679 | 5679 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
14-02-16 | 7314 | 7314 | 0 | 19:00 | - | - | - | - | - | - | - | - | - | - | 14-02-16 | 6001 | 6001 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
15-02-16 | 7525 | 7525 | 0 | 19:30 | - | - | - | - | - | - | - | - | - | - | 15-02-16 | 6040 | 6040 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
16-02-16 | 7521 | 7521 | 0 | 19:00 | - | - | - | - | - | - | - | - | - | - | 16-02-16 | 6333 | 6333 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
17-02-16 | 7448 | 7448 | 0 | 19:30 | - | - | - | - | - | - | - | - | - | - | 17-02-16 | 5938 | 5938 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
18-02-16 | 7474 | 7474 | 0 | 19:00 | - | - | - | - | - | - | - | - | - | - | 18-02-16 | 6342 | 6342 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
19-02-16 | 7055 | 7055 | 0 | 20:00 | - | - | - | - | - | - | - | - | - | - | 19-02-16 | 5410 | 5410 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
20-02-16 | 7497 | 7497 | 0 | 19:30 | - | - | - | - | - | - | - | - | - | - | 20-02-16 | 5748 | 5748 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
21-02-16 | 7130 | 7130 | 0 | 19:30 | - | - | - | - | - | - | - | - | - | - | 21-02-16 | 5524 | 5524 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
22-02-16 | 7679 | 7679 | 0 | 19:00 | - | - | - | - | - | - | - | - | - | - | 22-02-16 | 6192 | 6192 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
23-02-16 | 7628 | 7628 | 0 | 19:00 | - | - | - | - | - | - | - | - | - | - | 23-02-16 | 6689 | 6689 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
24-02-16 | 7147 | 7147 | 0 | 20:00 | - | - | - | - | - | - | - | - | - | - | 24-02-16 | 5656 | 5656 | 0 | 11:00 | - | - | - | - | - | - | - | - | - | -
25-02-16 | 7475 | 7475 | 0 | 19:00 | - | - | - | - | - | - | - | - | - | - | 25-02-16 | 6076 | 6076 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
26-02-16 | 7010 | 7010 | 0 | 19:30 | - | - | - | - | - | - | - | - | - | - | 26-02-16 | 5071 | 5071 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
27-02-16 | 7614 | 7614 | 0 | 20:00 | - | - | - | - | - | - | - | - | - | - | 27-02-16 | 5915 | 5915 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
28-02-16 | 7617 | 7617 | 0 | 20:00 | - | - | - | - | - | - | - | - | - | - | 28-02-16 | 6597 | 6597 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
29-02-16 | 7729 | 7729 | 0 | 19:30 | - | - | - | - | - | - | - | - | - | - | 29-02-16 | 6469 | 6469 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month: February 2016
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 7729 | 29/02/16 | 19:30
2 | Maximum day peak Genaration | MW | 6689 | 23/02/16 | 12:00
3 | Peak Demand | MW | 7729 | 29/02/16 | 19:30
4 | Minimum Generation | MW | 3727 | 06/02/16 | 4:00
5 | Average of the daily evening peak Genaration | MW | 7234.8966
6 | Average of the daily day peak Genaration | MW | 5818.5517
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 29 days in the month) | MW | -
11 | Total Generation | MKWH | 3908.7077
12 | Total Generation by IPP | MKWH | 362.5806 | % of total Gen. | 9.2762
13 | Total Generation by BPDB | MKWH | 1676.0588 | " | 42.8801
14 | A) Total Generation by RPCL | MKWH | 102.3787 |  | 2.6192
| B) Total Generation by REB | MKWH | 108.8198 | " | 2.784
| C) Total Generation by RENTAL | MKWH | 1380.5695 | " | 35.3204
| D) Total Generation by HVDC (Import from India) | MKWH | 278.3004 | " | 7.12
15 | Fuel wise Generation.
| A) Gas | MKWH | 2756.5889 | % of total Gen. | 70.52%
| B) Oil | MKWH | 738.3502 | '' | 18.89%
| C) Hydro | MKWH | 48.9778 | '' | 1.253%
| D) Coal | MKWH | 86.4904 | '' | 2.213%
| E) HVDC (Import from India) | MKWH | 278.3004 | '' | 7.12%
16 | Maximun of the daily total Generation . | MKWH | 149.5141 | 23/02/16
17 | Monthly Load factor | % | 72.6609
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 9180.7283
| A) Gas | M.Taka | 1609.6246
| B) Liquid fuel | M.Taka | 7127.4081
| C) Coal | M.Taka | 443.6956
| D) HVDC (Import from India) | M.Taka | 807.0711
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 417.6475 | 29/02/16
| A) Gas | M.Taka | 67.4381 | 22/02/16
| B) Liquid fuel | M.Taka | 333.6565 | 29/02/16
| C) Coal | M.Taka | 21.1095 | 04/02/16
| D) HVDC (Import from India) | M.Taka | 32.577 | 27/02/16
20 | Fuel cost of per unit Generation
| A) Including Hydro | Taka/KWHR | 3.1698
| B) Excluding Hydro | Taka/KWHR | 3.2101
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 93 | 29/02/16 | 06:00
b) | Actual | FT (MSL) | 93.66 | 29/02/16 | 06:00
22 | Peak Genaration of February 2015 | MW | 7022 | 26/02/15 | 19:30
23 | Peak Demand of February 2015 | MW | 7022 | 26/02/15 | 19:30
24 | Maximum peak Generation recorded upto 29/02/16 | MW | 8177 | 13/08/15 | 21:00
25 | Maximum peak Demand recorded upto 29/02/16 | MW | 8177 | 13/08/15 | 21:00
26 | Maximum load shed recorded upto 29/02/16 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.