## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-11-18 | Saturday
|  | Date (day): | 2023-11-18 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10723.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13121 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-11-17 | 2023-11-18 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 160 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 72 | 60 | 72 | 36 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 299 | 399 | 360 | 412
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 141 | 297 | 160 | 300 | 60 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 170 | 0 | 0 | 225 | 225 |  | GT-1 under S/D due to Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 80 | 85 |  | 15 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | GT-1 under S/D due to Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 65 | 85 |  | 17 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 15 | 25 | 30 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 30 | 30 | 45 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 18 | 18 |  | 4 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 92 | 92 |  | 8 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 160 | 0 | 0 | 200 | 135 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 80 | 90 |  | 12 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 0 | 17 | 37 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 32 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 0 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 0 | 55
| Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
25 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 19 | 19 | 31 | 31 |  | 49 | Engine problem
26 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 17 | 33 | 33
27 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 17 | 25 | 25 |  | 8 | Engine problem
28 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 0 | 8 | 25 | 27 |  | Fuel shortage
29 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
30 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 80 | 130 | 170 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
31 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 0 | 17 | 100 | 49 |  | Fuel shortage
32 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 30 | 105
33 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 0 | 17 | 71 | 33 |  | Fuel shortage
34 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 17 | 35 | 127 |  | Fuel shortage
35 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 13 | 0 | 35 | 0
36 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 17 | 35 | 20 |  | Fuel shortage
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 0 | 0 | 0 | 0
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 5763 | 5422 | 987 | 1001 | 1482 | 2660 | 1715 | 1053
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
38 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 0 | 8 | 17 | 8 |  | Fuel shortage
39 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 0 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 6 | 19 | 31 |  | Fuel shortage
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 86 | 86 | 86 | 144 |  | Low water lavel
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 143 | 188 | 200 | 200
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 17 | 17 | 88 |  | Fuel shortage
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 40 | 50 | 48 |  | Fuel shortage
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 | 102 |  | Fuel shortage
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 0 | 12 | 12 | 88 |  | Fuel shortage
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 12 | 12 | 88 |  | Fuel shortage
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 8 | 12 | 12 | 10 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 0 | 7 | 10
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 0 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 245 | 245 | 55 |  | Fuel shortage+Engine problem
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 17 | 17 | 37 |  | Fuel shortage
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 17 | 17 | 93 |  | Fuel shortage
55 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 12 | 12 | 88 |  | Fuel shortage
56 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 17 | 17 | 99 |  | Fuel shortage
57 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 0 | 17 | 17 | 146 |  | Fuel shortage
58 | SS Power I |  | Coal | SS Power | 1*612 | 612 | 612 | 265 | 400 | 420 | 480 |  | 132
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 6 | 6 | 10 | 10 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 210 | 210 | 560 | 560 |  |  | On test.
| Chattogram area Total |  |  |  |  | 3217 | 3157 | 672 | 898 | 1740 | 1810 | 1413 | 462
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 0 | 0 | 0 |  | 221 | Under maint.
60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 295 | 280 | 300 | 60 |  | Gas shortage
61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 0 | 0 | 0 |  | 360 | Under maint.
62 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 230 | 380 | 350 | 360 | 40 |  | Gas shortage
63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 49 | 51 | 51
| Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortae
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 51 | 51 | 51
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 12 | 130 |  | 20 | Engine problem
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 17 | 17 | 183 |  | Fuel shortage
70 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 15 | 17 |  | 5 | Engine problem
71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 10 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 58 | 32 | 128 | 140
72 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33
73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 0 | 0 | 12 | 12 |  | 13 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 17 | 114
76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 28 | 55 | 58 |  | Fuel shortage
77 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 0 | 17 | 17 |  | 37 | Engine problem
78 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 34 | 95 | 20 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2896 | 893 | 807 | 1107 | 1455 | 556 | 819
79 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 32 | 101 | 100 | 100 | 102 |  | Gas shortage
80 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Contract Expired
| Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 0 | 0 | 84 | 100 | 100 |  | Fuel shortage
83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 0 | 0 | 47 | 85 | 30 |  | Fuel shortage
84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 24 | 0 | 50 | 0
85 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 57 | 101 | 288.6 | 291 | 102 | 22
86 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 35 | 43 | 43 | 43 |  | 27 | Machine problem.
87 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Engine problem
88 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
89 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
90 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 50 | 50 | 50
91 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0
92 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 2 | 2 |  | 9 | Engine problem
93 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 20 | 32 | 32 | 32 |  | 33 | GT-8 Under maint.
94 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 0 | 0 | 0 | 86 |  | Gas shortage
95 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
96 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 190 | 194 | 200 | 200 |  | 31 | Machine problem
97 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 18 | 17 | 18
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 0 | 16 | 16 | 9 |  | Gas shortage
99 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 280 | 290 | 300 |  |  | FGMO
100 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 365 | 367 | 400 | 400 |  |  | FGMO
101 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 10 | 10
102 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 285 | 400 | 350 | 383
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1190 | 1394 | 1410 | 1454 | 258 | 620
103 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 675 | 333 | 700 | 918
104 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 0 | 66 | 49 |  | Fuel shortage
105 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 50
106 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
107 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 70 | 39 |  | Fuel shortage
108 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
109 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 | 40 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
110 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105
111 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 15 | 32 | 73 |  | Fuel shortage
112 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 4 | 0 | 100 | 0
113 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0
114 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 355 | 408 | 400 | 400 |  | 217 | Machine problem
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 1034 | 741 | 1320 | 1641 | 857 | 217
115 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 16 | 110
116 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 9 | 3 | 21 | 25 |  | 15 | Engine problem
117 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 60 | 0 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 500 | 490 | 622 | 622 |  | 622 | Unit-2 S/D.
119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 110 | 110 | 110 | 110 |  | 110 | GT-1 Under maint.
120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 38 | 150
121 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 140 | 0 | 140 | 140 | 167 |  | Coal shortage
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 819 | 603 | 1077 | 1287 | 167 | 811
122 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
123 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 35 | 17 |  | Fuel shortage
124 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 20 |  | 51 | Engine problem
125 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 28 | 28
126 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 34 | 42 |  | 8 | Engine problem
127 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 40 |  | 10 | Engine problem
128 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
129 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
130 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
131 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 250 | 370 | 400 | 414
132 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 24 | 38 | 12 |  | Fuel shortage
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
133 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11
134 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 8 | 52
135 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 40 | 85 |  | 19 | Engine problem
136 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
137 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 35 | 50 | 63 |  | Fuel shortage
138 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 35 | 55 | 58 |  | Fuel shortage
139 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 2 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 816 | 812 | 1200 | 1300
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 1068 | 1182 | 1851 | 2170 | 1171 | 88
140 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
141 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
142 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
143 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
144 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 40 | 113
145 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
146 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 0 | 70 | 70
147 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 20 | 0 | 30 | 0
148 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 183 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 378 | 170 | 448 | 353 | 125 | 189
| Total |  |  |  |  | 25339 | 24599 | 7098 | 6897 | 10723.6 | 13121 | 6364 | 4281
A. |  | 2023-11-17 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 8827 | MW at | 1:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 6845 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 6897 | MW
3 | Day peak Generation : |  |  | 7098 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 6620.37 | MW
4 | Evening peak Generation : |  |  | 6897 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 167.053 | MKWHr | By Solar | 1.4427 | MKWHr
| By Gas : | 86.7525 | MKWHr |  | By Oil: | 0.26326 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 63.9067 | MKWHr |  | By Hydro: | 1.5225 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.2592 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6364 | MW | Dhaka | 2779.97 | 2779.97 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 4281 | MW | Chittagong | 708.6 | 708.6 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 10645 | MW | Khulna | 845.3 | 845.3 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 631.22 | MMCFD |  |  | Rajshahi | 822.4 | 822.4 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 85007123.648 | ii) Oil : | Taka | 3359823.05 | Comilla | 100 | 100 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 413305865 | Total | Taka | 501672811.698 | Mymensingh | 619 | 619 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 153 | 153 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 316 | MW (W to E) at | 21:00 | hrs | Barisal | 69.1 | 69.1 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 160 | MW at | 17:00 | hrs | Rangpur | 523 | 523 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 22.6°C |  |  | Total | 6620.37 | 6620.37 |  | 0
B. |  | 2023-11-18 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 22.6°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13121 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8500 | MW
4 | Reserve(Generation end) |  |  |  | 2621 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 198.715 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5719 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.3644 | MKWHr. | ii) HVDC Flow at Peak Time |  | 333 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.5418 | MKWHr. | iii) Maximum HVDC Flow : |  | 912 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 98.79 |  | (b) Today: | 98.86 |  | (c) Rule Curve: |  | 107.4
.

## YesterdayGen
2023-11-17 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 289 | 120 |  | 0 | 225 | 132 | 0 | 17 | 0 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 25 | 25 | 0 | 0 | 92 | 40 | 0 | 0 | 0 | 188 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 280 | 270 | 0 | 0 | 0 | 51 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 6 | 116 | 86 | 0 | 0 | 0 | 43 | 0 | 47 | 0 | 0 | 0 | 32 | 0 | 0 | 204 | 0 | 0 | 10 | 270 | 16 | 5 | 0 | 0 | 0 | 0 | 16 | 0 | 17 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 10 | 370 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 377 | 10 | 562 | 0 | 0 |  | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 140 | 904 | 0 | 0 |  | 5272 | 3555 | 8827 | 3144 | 912 | 1367 | 0 | 94 | 3052 | 132 | 0 | 0 | 116 | 0 | 10 | 0 | 98.81
2:00 | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 266 | 112 |  | 0 | 180 | 132 | 0 | 17 | 0 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 12 | 25 | 25 | 0 | 0 | 92 | 40 | 0 | 0 | 0 | 188 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12 | 0 | 0 | 0 | 280 | 270 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 112 | 86 | 0 | 0 | 0 | 43 | 0 | 10 | 0 | 0 | 0 | 20 | 0 | 0 | 204 | 0 | 0 | 10 | 260 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 335 | 10 | 562 | 0 | 0 |  | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 140 | 852 | 0 | 0 |  | 4790 | 3439 | 8229 | 2914 | 912 | 1222 | 0 | 17 | 2910 | 132 | 0 | 0 | 112 | 0 | 10 | 0 | 98.8
3:00 | 0 | 0 | 0 | 180 | 0 | 42 | 0 | 257 | 112 |  | 0 | 180 | 129 | 0 | 17 | 0 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 19 | 12 | 25 | 25 | 0 | 0 | 92 | 40 | 0 | 0 | 0 | 188 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12 | 0 | 0 | 0 | 280 | 270 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 6 | 106 | 86 | 0 | 0 | 0 | 43 | 0 | 10 | 0 | 0 | 0 | 20 | 0 | 0 | 204 | 0 | 0 | 0 | 270 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 335 | 9 | 564 | 0 | 0 |  | 733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 140 | 829 | 0 | 0 |  | 4757 | 3232 | 7989 | 2927 | 733 | 1175 | 0 | 17 | 2890 | 132 | 0 | 0 | 106 | 0 | 9 | 0 | 98.8
4:00 | 0 | 0 | 0 | 180 | 0 | 13 | 0 | 253 | 106 |  | 0 | 180 | 111 | 0 | 16 | 0 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 25 | 0 | 0 | 0 | 92 | 40 | 0 | 0 | 0 | 188 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 25 | 0 | 0 | 0 | 270 | 240 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 6 | 98 | 86 | 0 | 0 | 0 | 43 | 0 | 10 | 0 | 0 | 0 | 20 | 0 | 0 | 204 | 0 | 0 | 0 | 260 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 336 | 6 | 554 | 0 | 0 |  | 581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 140 | 814 | 0 | 0 |  | 4605 | 3005 | 7610 | 2838 | 581 | 1072 | 0 | 16 | 2867 | 132 | 0 | 0 | 98 | 0 | 6 | 0 | 98.79
5:00 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 252 | 105 |  | 0 | 180 | 110 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 25 | 25 | 0 | 0 | 92 | 40 | 0 | 0 | 0 | 188 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 270 | 240 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 102 | 88 | 0 | 0 | 0 | 43 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 204 | 0 | 0 | 0 | 250 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 325 | 3 | 556 | 0 | 0 |  | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 140 | 825 | 0 | 0 |  | 4519 | 2882 | 7401 | 2806 | 480 | 1010 | 0 | 0 | 2868 | 132 | 0 | 0 | 102 | 0 | 3 | 0 | 98.79
6:00 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 241 | 112 |  | 0 | 170 | 112 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 25 | 8 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 188 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 260 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 84 | 88 | 0 | 0 | 0 | 43 | 20 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 204 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 307 | 6 | 548 | 0 | 0 |  | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 140 | 829 | 0 | 0 |  | 4260 | 2728 | 6988 | 2665 | 330 | 970 | 0 | 0 | 2847 | 86 | 0 | 0 | 84 | 0 | 6 | 0 | 98.79
7:00 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 233 | 112 |  | 0 | 170 | 112 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 12 | 25 | 8 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 260 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 90 | 73 | 0 | 0 | 0 | 42 | 20 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 204 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 306 | 9 | 548 | 0 | 0 |  | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 140 | 823 | 2 | 0 |  | 4158 | 2719 | 6877 | 2635 | 329 | 886 | 0 | 0 | 2840 | 86 | 0 | 0 | 90 | 2 | 9 | 0 | 98.78
8:00 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 233 | 112 |  | 0 | 170 | 112 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 12 | 25 | 8 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 260 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 80 | 71 | 0 | 0 | 0 | 42 | 20 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 204 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 230 | 0 | 0 | 305 | 4 | 555 | 0 | 0 |  | 522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 500 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 3 | 140 | 827 | 29 | 0 |  | 4114 | 2932 | 7046 | 2637 | 522 | 871 | 0 | 2 | 2850 | 46 | 0 | 0 | 80 | 34 | 4 | 0 | 98.78
9:00 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 234 | 107 |  | 0 | 170 | 112 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 12 | 25 | 8 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 285 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 76 | 32 | 0 | 0 | 0 | 43 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 204 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 230 | 0 | 0 | 295 | 20 | 282 | 0 | 0 |  | 571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 500 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 23 | 140 | 832 | 115 | 0 |  | 3766 | 3079 | 6845 | 2572 | 571 | 836 | 0 | 0 | 2577 | 46 | 0 | 0 | 76 | 147 | 20 | 0 | 98.78
10:00 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 240 | 121 |  | 0 | 170 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 12 | 25 | 8 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 295 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 70 | 32 | 0 | 0 | 1 | 35 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 186 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 7 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 230 | 0 | 0 | 275 | 20 | 280 | 0 | 0 |  | 580 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 500 | 110 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 353 | 31 | 140 | 833 | 128 | 0 |  | 3636 | 3116 | 6752 | 2580 | 580 | 729 | 0 | 0 | 2551 | 46 | 0 | 0 | 70 | 176 | 20 | 0 | 98.78
11:00 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 286 | 142 |  | 0 | 170 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 12 | 25 | 17 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 285 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 32 | 0 | 0 | 1 | 35 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 186 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 22 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 230 | 0 | 0 | 265 | 3 | 210 | 0 | 0 |  | 533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 500 | 110 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 354 | 19 | 140 | 814 | 185 | 0 |  | 3659 | 3142 | 6801 | 2584 | 533 | 859 | 0 | 0 | 2453 | 46 | 0 | 0 | 80 | 243 | 3 | 0 | 98.79
12:00 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 299 | 141 |  | 0 | 170 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 25 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 310 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 32 | 0 | 0 | 1 | 35 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 190 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 24 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 230 | 0 | 0 | 265 | 6 | 210 | 0 | 0 |  | 675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 500 | 110 | 0 | 0 | 2 | 4 | 0 | 0 | 0 | 355 | 20 | 140 | 816 | 183 | 0 |  | 3799 | 3299 | 7098 | 2628 | 675 | 977 | 0 | 0 | 2456 | 46 | 0 | 0 | 58 | 252 | 6 | 0 | 98.79
13:00 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 299 | 141 |  | 0 | 170 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 25 | 15 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 290 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 33 | 0 | 0 | 1 | 37 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 195 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 19 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 330 | 0 | 0 | 264 | 23 | 208 | 0 | 0 |  | 675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 530 | 110 | 0 | 0 | 3 | 10 | 0 | 0 | 0 | 383 | 23 | 140 | 814 | 175 | 0 |  | 3992 | 3427 | 7419 | 2774 | 675 | 1059 | 0 | 0 | 2509 | 46 | 0 | 0 | 84 | 249 | 23 | 0 | 98.79
14:00 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 254 | 132 |  | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 25 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 275 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 34 | 0 | 0 | 1 | 37 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 195 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 13 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 230 | 0 | 0 | 260 | 3 | 206 | 0 | 0 |  | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 500 | 110 | 0 | 0 | 1 | 8 | 0 | 0 | 0 | 353 | 29 | 109 | 812 | 168 | 0 |  | 3362 | 2881 | 6243 | 2340 | 382 | 775 | 0 | 0 | 2410 | 20 | 0 | 0 | 80 | 233 | 3 | 0 | 98.79
15:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 232 | 156 |  | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 34 | 0 | 0 | 1 | 43 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 195 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 230 | 0 | 0 | 263 | 3 | 202 | 0 | 0 |  | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 490 | 110 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 355 | 18 | 54 | 830 | 63 | 0 |  | 2962 | 2475 | 5437 | 2000 | 163 | 729 | 0 | 0 | 2364 | 0 | 0 | 0 | 62 | 116 | 3 | 0 | 0
16:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 231 | 177 |  | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 34 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 165 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238 | 0 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 230 | 0 | 0 | 261 | 3 | 202 | 0 | 0 |  | 231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 300 | 110 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 353 | 11 | 0 | 803 | 26 | 0 |  | 2706 | 2191 | 4897 | 1740 | 231 | 748 | 0 | 0 | 2089 | 0 | 0 | 0 | 36 | 50 | 3 | 0 | 0
17:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 232 | 152 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 34 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 166 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 270 | 29 | 204 | 0 | 0 |  | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 805 | 2 | 0 |  | 2570 | 2219 | 4789 | 1780 | 245 | 673 | 0 | 0 | 2055 | 0 | 0 | 0 | 4 | 3 | 29 | 0 | 0
18:00 | 0 | 0 | 0 | 180 | 0 | 18 | 0 | 316 | 231 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 43 | 0 | 23 | 0 | 0 | 0 | 32 | 0 | 0 | 165 | 0 | 0 | 8 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 330 | 24 | 210 | 0 | 0 |  | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 802 | 0 | 0 |  | 3555 | 2553 | 6108 | 2469 | 347 | 1047 | 0 | 0 | 2221 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 54 | 0 | 343 | 277 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 12 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 86 | 0 | 0 | 0 | 43 | 0 | 20 | 0 | 0 | 0 | 32 | 0 | 0 | 164 | 0 | 0 | 10 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 350 | 15 | 210 | 0 | 0 |  | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 810 | 0 | 0 |  | 3793 | 2597 | 6390 | 2549 | 343 | 1103 | 0 | 0 | 2372 | 0 | 0 | 0 | 8 | 0 | 15 | 0 | 0
19:30 | 0 | 0 | 0 | 180 | 0 | 59 | 0 | 334 | 297 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 12 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 85 | 0 | 0 | 0 | 43 | 0 | 20 | 0 | 0 | 0 | 32 | 0 | 0 | 183 | 0 | 0 | 10 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 350 | 8 | 210 | 0 | 0 |  | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 810 | 0 | 0 |  | 3950 | 2657 | 6607 | 2614 | 343 | 1236 | 0 | 0 | 2392 | 0 | 0 | 0 | 14 | 0 | 8 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 352 | 297 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 13 | 17 | 17 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 188 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 101 | 0 | 0 | 0 | 43 | 0 | 20 | 0 | 0 | 0 | 32 | 0 | 0 | 203 | 0 | 0 | 10 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 400 | 8 | 208 | 0 | 0 |  | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 810 | 0 | 0 |  | 4123 | 2647 | 6770 | 2647 | 278 | 1274 | 0 | 0 | 2451 | 86 | 0 | 0 | 26 | 0 | 8 | 0 | 0
21:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 399 | 297 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 17 | 17 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 188 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 101 | 0 | 0 | 0 | 43 | 0 | 50 | 0 | 0 | 0 | 32 | 0 | 0 | 194 | 18 | 0 | 10 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 400 | 6 | 210 | 0 | 0 |  | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 812 | 0 | 0 |  | 4201 | 2696 | 6897 | 2707 | 333 | 1243 | 0 | 0 | 2490 | 86 | 0 | 0 | 32 | 0 | 6 | 0 | 0
22:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 418 | 297 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 13 | 17 | 17 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 102 | 0 | 0 | 0 | 43 | 0 | 50 | 0 | 0 | 0 | 33 | 0 | 0 | 203 | 18 | 0 | 10 | 285 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 400 | 14 | 210 | 0 | 0 |  | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 802 | 0 | 0 |  | 4224 | 2698 | 6922 | 2758 | 344 | 1250 | 0 | 0 | 2472 | 46 | 0 | 0 | 38 | 0 | 14 | 0 | 98.82
23:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 419 | 297 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 13 | 17 | 17 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 100 | 0 | 0 | 0 | 43 | 0 | 50 | 0 | 0 | 0 | 20 | 0 | 0 | 203 | 18 | 0 | 10 | 275 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 400 | 6 | 210 | 0 | 0 |  | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 813 | 0 | 0 |  | 4204 | 2630 | 6834 | 2762 | 344 | 1168 | 0 | 0 | 2476 | 46 | 0 | 0 | 32 | 0 | 6 | 0 | 98.82
24:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 385 | 297 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 13 | 17 | 17 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 100 | 0 | 0 | 0 | 43 | 0 | 50 | 0 | 0 | 0 | 20 | 0 | 0 | 200 | 18 | 0 | 10 | 290 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 392 | 5 | 208 | 0 | 0 |  | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 814 | 0 | 0 |  | 4059 | 2611 | 6670 | 2649 | 344 | 1186 | 0 | 0 | 2404 | 46 | 0 | 0 | 36 | 0 | 5 | 0 | 98.83
KWH | 0 | 0 | 0 | 3869000 | 0 | 646090 | 0 | 7057410 | 4118000 |  | 0 | 2553500 | 1151505 | 0 | 57437 | 0 | 2879392 | 0 | 63000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95112 | 456000 | 204840 | 547200 | 279300 | 0 | 0 | 1138500 | 384000 | 0 | 0 | 0 | 4033876 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 76896 | 259680 | 0 | 0 | 0 | 7204600 | 3837000 | 0 | 0 | 0 | 337680 | 0 | 0 | 384312 | 0 | 0 | 0 | 0 | 8100 | 61000 | 62800 | 1541760 | 1530240 | 0 | 0 | 6200 | 976000 | 0 | 358200 | 0 | 0 | 0 | 448128 | 0 | 0 | 3962640 | 93000 | 0 | 92160 | 5562000 | 61344 | 25104 | 0 | 0 | 0 | 0 | 36000 | 0 | 23040 | 13230 | 0 | 0 | 0 | 8316000 | 4800 | 0 | 0 | 2277 | 0 | 0 | 24254 | 0 | 0 | 13440 | 7931800 | 0 | 104590 | 0 | 25091 | 0 | 79200 | 48080 | 0 | 0 | 6678000 | 0 | 0 | 7581817 | 259200 | 8967272 | 0 | 0 |  | 11364363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1044000 | 118300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62064 | 0 | 0 | 4190000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6723527 | 0 | 0 | 0 | 0 | 0 | 0 | 37736 | 0 | 12736700 | 2583736 | 0 | 0 | 9420 | 46800 | 0 | 0 | 0 | 8865455 | 177413 | 2072700 | 19492731 | 997000 | 0 |  | 96531097 | 70521945 | 167053042 | 62201526 | 11364363 | 24551010 | 0 | 263262 | 63906675 | 1522500 | 0 | 0 | 1541760 | 1442746 | 259200 | 0
Fuel Cost | 0 | 0 | 0 | 5764810 | 0 | 859299.7 | 0 | 7410280.5 | 4447440 |  | 0 | 2783315 | 1278170.55 | 0 | 761040.25 | 0 | 3224919.04 | 0 | 110250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71334 | 342000 | 0 | 0 | 0 | 0 | 0 | 307395 | 103680 | 0 | 0 | 0 | 4195231.04 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 97657.92 | 864734.4 | 0 | 0 | 0 | 7997106 | 4182330 | 0 | 0 | 0 | 381578.4 | 0 | 0 | 641801.04 | 0 | 0 | 0 | 0 | 6075 | 106750 | 47100 | 11069836.8 | 1667961.6 | 0 | 0 | 98828 | 1337120 | 0 | 623268 | 0 | 0 | 0 | 869368.32 | 0 | 0 | 4002266.4 | 199950 | 0 | 182476.8 | 5562000 | 46008 | 19079.04 | 0 | 0 | 0 | 0 | 485280 | 0 | 319104 | 154658.7 | 0 | 0 | 0 | 7650720 | 58368 | 0 | 0 | 35430.12 | 0 | 0 | 257820.02 | 0 | 0 | 158323.2 | 7297256 | 0 | 1511325.5 | 0 | 285535.58 | 0 | 1034352 | 574556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 34093089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1169280 | 229502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46982.448 | 0 | 0 | 35531200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6656291.73 | 0 | 0 | 0 | 0 | 0 | 0 | 416982.8 | 0 | 105714610 | 2635410.72 | 0 | 0 | 106540.2 | 548964 | 0 | 0 | 0 | 80586985.95 | 0 | 24810219 | 166662850.05 | 0 | 0 |  | 91485189.92 | 459208907.898 | 550694097.818 | 58243413.708 | 34093089 | 26763709.94 | 0 | 3359823.05 | 413305865 | 411075 | 0 | 0 | 11069836.8 | 3447285.32 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 299 | 141 |  | 0 | 170 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 25 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 310 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 32 | 0 | 0 | 1 | 35 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 190 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 24 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 230 | 0 | 0 | 265 | 6 | 210 | 0 | 0 |  | 675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 500 | 110 | 0 | 0 | 2 | 4 | 0 | 0 | 0 | 355 | 20 | 140 | 816 | 183 | 0 |  | 7098 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 399 | 297 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 17 | 17 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 101 | 0 | 0 | 0 | 43 | 0 | 50 | 0 | 0 | 0 | 32 | 0 | 0 | 194 | 18 | 0 | 10 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 400 | 6 | 210 | 0 | 0 |  | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 812 | 0 | 0 |  | 6897 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 412 | 300 |  | 0 | 225 | 0 | 85 | 85 | 25 | 200 | 0 | 0 | 92 | 90 | 149 | 30 | 0 | 0 | 0 | 17 | 35 | 55 | 18 | 19 | 12 | 33 | 25 | 25 | 0 | 46 | 40 | 0 | 0 | 17 | 200 | 0 | 0 | 0 |  | 6 | 50 | 0 | 12 | 0 | 19 | 12 | 10 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 51 | 0 | 0 | 52 | 17 | 11 | 33 | 12 | 140 | 100 | 0 | 0 | 0 | 43 | 0 | 50 | 0 | 0 | 0 | 32 | 0 | 0 | 200 | 18 | 0 | 10 | 300 | 16 | 2 | 0 | 130 | 0 | 0 | 100 | 0 | 100 | 0 | 12 | 17 | 130 | 400 | 85 | 105 | 17 | 0 | 245 | 17 | 17 | 114 | 55 | 12 | 383 | 71 | 0 | 35 | 17 | 0 | 17 | 0 | 95 | 35 | 360 | 17 | 0 | 480 | 10 | 560 | 0 | 0 |  | 918 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 50 | 70 | 0 | 130 | 25 | 110 | 0 | 0 | 0 | 35 | 20 | 85 | 28 | 42 | 40 | 52 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 105 | 0 | 50 | 32 | 113 | 0 | 0 | 55 | 622 | 110 | 0 | 150 | 0 | 0 | 70 | 0 | 0 | 400 | 0 | 140 | 1300 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 60 | 0 | 360 | 160 | 0 | 0 | 0 | 0 | 80 | 65 | 15 | 0 | 0 | 0 | 92 | 80 | 32 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 33 | 25 | 8 | 0 | 46 | 40 | 0 | 0 | 8 | 200 |  | 0 | 0 | 0 | 6 | 40 | 0 | 12 | 0 | 6 | 12 | 7 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 51 | 0 | 0 | 52 | 15 | 10 | 33 | 12 | 128 | 100 | 0 | 0 | 1.6 | 43 | 0 | 50 | 0 | 0 | 0 | 32 | 0 | 0 | 200 | 17 | 0 | 10 | 290 | 16 | 2 | 0 | 80 | 0 | 0 | 84 | 0 | 17 | 20 | 12 | 17 | 12 | 400 | 47 | 30 | 17 | 5 | 245 | 17 | 17 | 17 | 28 | 12 | 350 | 17 | 50 | 17 | 17 | 0 | 17 | 35 | 34 | 17 | 350 | 17 |  | 420 | 10 | 560 | 0 | 0 |  | 700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 28 | 34 | 30 | 8 | 24 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 105 | 0 | 35 | 15 | 40 | 0 | 8 | 35 | 622 | 110 |  | 38 | 6 | 100 | 70 | 0 |  | 400 | 30 | 140 | 1200 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 58 | 0 | 420 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 12 | 17 | 8 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 156 | 0 | 0 | 0 | 43 | 0 | 10 | 0 | 0 | 0 | 32 | 0 | 0 | 200 | 17 | 0 | 10 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 10 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 8 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 350 | 0 | 0 | 355 | 0 | 208 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 330 | 110 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 403 | 13 | 0 | 821 | 80 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
[8 empty] | 299430 | [13 empty] | 299565 | [26 empty] | 399366 | 399587 | [8 empty] | 299280 | [26 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 |  | 399747 |  |  |  | 399575 |  | 399337 | 399589 | 299230 | [7 empty] | 399245 |  | 299282 | 399274 |  | 399223 |  | 399630 | [12 empty] | 599468 | [32 empty] | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 | [8 empty] | 599726 | [9 empty] | 292.3904
| Minimum Generation |  | 6845 | 9:00 | [202 empty] | 86752536
| Highest Generation |  | 8827 | 1:00 | [202 empty] | 86.7525 |  |  |  |  | 1.4427
| Day Peak Generation |  | 7098 | 12:00 | [202 empty] | 263262
| Evening Peak Generation |  | 6897 | 21:00 | [202 empty] | 0.26326 |  |  | 24551010 |  | 1.5225
| HVDC Max Flow |  | 912 | 1:00 | [202 empty] | 11.3644 |  |  |  |  | 0.2592
| HVDC EvPeak Flow |  | 333 | 21:00 | [200 empty] | 167053042 |  | 1.5418 |  | 63.9067
| Load factor L.F |  | 78.86% | [166 empty] | 1275.5 | [36 empty] | 167.053

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-11-18
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-11-17 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 7098 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5719
Evening Peak Generation : |  |  | 6897 | MW Hour : | 21:00 | Available Max Generation : |  | 13121
E.P. Demand (at gen end) : |  |  | 6897 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 10500
Maximum Generation : |  |  | 8827 | MW Hour : | 1:00 | Reserve(Generation end) |  | 2621
Total Gen. (MKWH) : |  |  | 167.053 | System Load Factor : | 78.86% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 160 | MW at | 17:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-11-18
Actual : |  | 98.86 | Ft.(MSL) , | Rule curve : | 107.4 | Ft.( MSL )
Gas Consumed : |  | Total = | 631.22 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 85007123.648
: |  |  | Coal : | 413305865 | Oil : | 3359823.05 | Total : | 501672811.698
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4049.3685 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1109.504 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1553.2499 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1349.182 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1110.5832 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 825.5327 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 463.2298 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 385.5962 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 754.1689 |  |  | 0 | 0%
Total |  | 0 |  | 11600.4152 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:44 | 10:12 | BIPTC S/S 20DF21 Forced S/D
09:07 | 15:18 | Matuail-Siddhirganj 132kV Ckt-1 Project Work S/D from Siddhirganj 132/33kV end Due to 132/33 kV T-3
Transformer jack bus connection with Bus-A
09:08 | 17:05 | AKSML-Khulshi 132kV Ckt-1 Scheduled S/D from AKS 132/33kV end Due to AKSPL-Khulshi 132 kv Line
& AKSPL-Baraulia 132 kv Line Shutdown due to Baraulia Line CT (R-Phase) Replace.
09:10 | 17:05 | AKSML-Baroaulia 132kV Ckt-1 Scheduled S/D from AKS 132/33kV end Due to AKSPL-Khulshi 132 kv Line
& AKSPL-Baraulia 132 kv Line Shutdown due to Baraulia Line CT (R-Phase) Replace.
09:13 | 09:21 | Bhandaria 132/33kV S/S Transformer-1 LT Tripped showing OC/EF-50 frequency Relay relays Due to |  |  |  |  | 2.0MW load interruption.
T-1A trip due to Rajapur 33kv feeder.
09:13 | 09:21 | Bhandaria 132/33kV S/S Transformer-2 LT Tripped showing OC/EF-50Frequency Relay relays
Due to T-1A trip due to Rajapur 33kv feeder.
09:15 | 11:58 | Haripur-Siddirganj 230kV Ckt-2 Forced S/D from Siddhirganj 132/33kV end Due to Corrective
maintenance of DS 676M
| 09:25 | Madaripur 132/33kV S/S T2-415T HT is restored.
09:36 | 15:09 | Siddhirganj 132/33kV S/S 132kV Bus A Project Work S/D Due to 132/33 kV T-3 Transformer
jack bus connection with Bus-A
09:54 | 11:58 | Haripur 230/132kV S/S Auto TR-1 HT Tripped showing Buchholz Relay, LOR (86T). relays.
09:54 | 11:58 | Haripur 230/132kV S/S Auto TR-1 LT Tripped showing Buchholz Relay, LOR (86T). relays.
09:55 |  | Meghnaghat Summit CCPP 305MW was shutdown due to gas shortage.
10:09 |  | Cumilla(N)-Daudkandi 132kV ckt-1&2 were switched on from Cumilla(N) end. Previously, both ckts were in charged
condition from Daudkandi end.
| 10:13 | Moghbazar-Rampura 132kV Ckt-2 is restored.
10:52 |  | Ashuganj-Brahmanbaria 132kV Ckt-2 Scheduled S/D from Brahmanbaria 132/33kV end Due to NLDC AE.
11:35 |  | Beanibazar 132/33kV S/S 132 KV BUS-2 Forced S/D Due to Interlock test for New line-2 Bay with BUS Coupler.
11:46 |  | Barishal-Bhandaria 132 kV Ckt-1 Tripped from Bhandaria 132/33kV end showing No relay relays Due to Barisal line |  |  |  |  | 2.0MW load interruption.
trip from Barisal end. and from Barishal 132/33kV end showing Distance, B phase, SOTF. relays Due to Methily cyclone.
11:52 | 17:27 | Barishal-Bhandaria 132 kV Ckt-1 Forced S/D from Barishal 132/33kV end Due to Line faulty.
12:00 |  | Day peak generation: 7098 MW
12:01 | 12:50 | Saidpur 132/33kV S/S TR-01 HT Scheduled S/D Due to For testing Black start drill .
14:07 | 19:14 | Maniknagar-Matuail 132kV Ckt-1 Tripped from Maniknagar 132/33kV end showing 1. Distance Relay(C-Ph)
,2. MVAJ (Main protection trip). relays.
14:46 |  | Bhola CCPP 225 MW GT-2 was shut down due to low demand.
15:02 | 15:54 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Tripped showing MiCOM P441: PH B, Z1, Dist. SEND. relays. |  |  |  |  | 15.0MW load interruption.
15:05 | 17:04 | Hasnabad 132/33kV S/S 132/33kV 424 T-5 LT Tripped showing Trip relay MVAJM-25, TCS. relays Due to T-1 33 kv incoming |  |  |  |  | 20.0MW load interruption.
CB exploded.
15:05 |  | Hasnabad 132/33kV S/S 132/33kV 404 T-1 HT Tripped showing Differential Relay, Trip relay relays Due to 33kv incoming
CB exploded.
15:05 |  | Hasnabad 132/33kV S/S 132/33kV 404 T-1 LT Tripped showing Trip relay MVAJM-25, TCS. relays Due
to Earth fault, 33 kv incoming CB exploded
15:08 |  | Bhola CCPP 225 MW GT-1 was shut down due to low demand.
15:20 | 16:05 | Shyampur 230/132kV S/S Auto TR-1 HT Tripped showing Over voltage alarm (59-1) relays Due to Over
voltage due to stormy weather.
15:26 | 16:01 | Shyampur 230/132kV S/S Auto TR-2 HT Tripped showing Over voltage alarm (59-1) relays Due
to Over voltage due to stormy weather
15:31 | 16:14 | Fenchuganj-Kulaura 132 kV Ckt-1 Tripped from Kulaura 132/33kV end showing Distance
protection Relay operated relays Due to due to 33kv PDB-2 feeder fault
15:46 |  | Siddirganj CCPP was shut down due low demand.
15:48 |  | Payra Unit-2 was Shut down due to low demand.
15:48 | 15:57 | Patuakhali 132/33kV S/S 415T (T-2) LT Tripped showing O/C relays Due to 33kv incomers tripped
due to patuakhali 33kv feeder fault. i.e. there is no load in substation then. Substation load was zero.
15:48 | 15:57 | Patuakhali 132/33kV S/S 405T (T-1) LT Tripped showing O/C relays Due to 33kv incomers tripped due to
patuakhali 33kv feeder fault. i.e. there is no load in substation then. Substation load was zero.
15:48 | 15:57 | Patuakhali 132/33kV S/S 425T (T-3) LT Tripped showing O/C relays Due to 33kv incomers tripped
due to patuakhali 33kv feeder fault. i.e. there is no load in substation then. Substation load was zero.
15:53 | 19:44 | Tangail 132/33kV S/S Tr-2 LT Forced S/D Due to 33kv bus loop and connector are damaged.(Responsible for BPDB & PBS)
15:53 | 19:44 | Tangail 132/33kV S/S Tr-2 HT Forced S/D Due to 33kv bus loop and connector are damaged.(Responsible for BPDB & PBS)
15:55 | 17:35 | Siddhirganj 230/132kV S/S 335MW EGCB 2 Tripped showing Multilin L30, Multilin L90 relays Due to Over Voltage
15:55 | 17:33 | Siddhirganj 230/132kV S/S 335MW EGCB 1 Tripped showing Multilin L30,Multilin L90 relays Due to Over voltage
16:10 | 17:27 | Saidpur 132/33kV S/S TR-01 LT Forced S/D Due to Gt black outTest.
16:11 | 17:25 | Saidpur 132/33kV S/S TR-01 HT Forced S/D
| 16:17 | Baghabari-Sirajganj 132 kV Ckt-1 is restored.
| 16:19 | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-2 is restored.
| 16:20 | Sirajganj 132/33kV S/S Sherpur-2 is restored.
16:30 | 16:49 | Bashundhara-Rampura 132 kV Ckt-1 Tripped from Rampura 230/132kV end showing Distance protection 21/1Z3, BN
relays Due to Unknown
16:33 | 16:50 | Baroirhat-Feni 132 kV Ckt-2 Tripped from Feni 132/33kV end showing Power swing B, CB1 A/R fail relays. and from
Baroirhat 132/33kV end showing K32,k34 and k34x relays Due to Distance trip
16:38 | 17:55 | Cumilla(N)-Daudkandi 132 kV Ckt-1 Tripped from Cumilla(N) 230/132/33kV end showing Dist. Relay relays Due to
Heavy Rain and from Daudkandi 132/33kV end showing Distance Protection Relay relays Due to Bad Weather
16:48 |  | Meghnaghat CCPP GT-2 was SD due to low demand.
16:54 | 18:57 | Baroirhat-Hathazari 132 kV Ckt-1 Tripped from Baroirhat 132/33kV end showing K31,k32,k33,k34 and
k34x relays Due to Distance Trip
17:32 |  | Dohazari-Sikalbaha 132 kV Ckt-1 Tripped from Shikalbaha 230/132kV end showing Distance Relay relays Due to
Distance Protection Trip and from Dohazari 132/33kV end showing Distance Relay-A, Aided Trip relays.
17:57 | 20:24 | Cumilla(N)-Daudkandi 132 kV Ckt-1 Tripped from Daudkandi 132/33kV end showing Distance Protection
Relay relays Due to Bad Weather and from Cumilla(N) 230/132/33kV end showing Dist. Relay relays Due to Heavy Rain
18:31 | 00:51 | Fenchuganj-Kulaura 132 kV Ckt-2 Tripped from Kulaura 132/33kV end showing no relay operated relays Due to for
heavy rain
18:44 | 18:58 | Baroirhat-Hathazari 132 kV Ckt-2 Tripped from Baroirhat 132/33kV end showing K31,k32,k33,k34 & k34x relays Due to |  |  |  |  | 6.0MW load interruption.
Distance Trip
18:49 |  | Godda - Rohanpur 400 kv L-1 was switched on.
20:43 | 21:10 | Halishahar 132/33kV S/S 413T(TR-2) LT Forced S/D Due to PDB taken shutdown for emergency work.
20:52 | 21:03 | Halishahar 132/33kV S/S 403T(TR-1) LT Forced S/D Due to PDB taken shutdown for emergency work.
21:00 |  | Evening Peak Gen. 6897 MW
22:11 | 23:29 | Halishahar 132/33kV S/S 403T(TR-1) LT Scheduled S/D Due to due to pdb maintenance work
22:35 |  | Siddhirganj (2*120 MW GTPP) GT-2 was sync.
23:10 |  | Bhola CCPP GT-2 was sync.
00:19 |  | Fenchuganj-Kulaura 132 kV Ckt-2 Scheduled S/D from Fenchuganj 230/132/33kV end Due to CB maintenance at Kulaora end
05:00 |  | Minimum Generation: 6857 MW (Cyclone Midhili)
06:26 |  | Adani-Rahanpur ckt-2 was S/D for D/W
06:52 |  | Rampura 230/132kV S/S Auto Transformer - 02 LT Project Work S/D Due to Clamp Change work of 132kV Bus-2
DS 639(B Phase), due to temperature rise in new Interim Transformer ds clamp connection.
06:53 |  | Rampura 230/132kV S/S Auto Transformer - 02 HT Project Work S/D Due to Clamp Change work of 132kV Bus-2
DS 639(B Phase), due to temperature rise in new Interim Transformer ds clamp connection.
06:55 |  | Rampura 230/132kV S/S 132 kV Busbar-2 Project Work S/D Due to Clamp Change work of 132kV Bus-2 DS 639
(B Phase), due to temperature rise in new Interim Transformer ds clamp connection.
07:04 |  | Baghabari-Sirajganj 132 kV Ckt-1 Project Work S/D from Sirajganj 132/33kV end Due to Project
work and annual maintenance.
07:18 |  | Sirajganj 132/33kV S/S Sherpur-2 Project Work S/D Due to project work .
07:22 |  | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-2 Project Work S/D from Bog-Sherpur 132/33kV end Due to
project work related schedule shutdown
07:35 |  | Siddhirganj 132/33kV S/S 132kV Bus B Project Work S/D Due to G2G PROJECT WORK.
07:45 |  | Bogura-Sirajganj 230 kV Ckt-1 Scheduled S/D from Bogura 230/132kV end Due to Annual Maintenance.
07:48 |  | Shahjadpur 132/33kV S/S T-1(405T) HT Scheduled S/D Due to Annual maintenance
07:49 |  | Bakulia 132/33kV S/S T-1 (402T) LT Scheduled S/D Due to FOR Annual Maintenance 2023-2024.
07:50 |  | Bakulia 132/33kV S/S T-1 (402T) HT Scheduled S/D Due to FOR Annual Maintenance 2023-2024.
07:56 |  | Kaliakoir 400/230/132kV S/S 400kV Bus 1 Scheduled S/D Due to annual maintenance

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-11-17 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 3869000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 72 | 646090 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 399 | 7057410
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 297 | 4118000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 2553500 | GT-1 under S/D due to gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 0 | 0 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 1151505 | GT-1 under S/D due to gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 57437 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 95112 | Reserve
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 63000
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 2879392 | Low demand
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 0 | Reserve
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 19 | 660840 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 547200
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 279300
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 23040 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 0 | Reserve
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 0 | Reserve
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | Reserve
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 48080
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Reserve
| Meghnaghat Unique power |  | IPP | 586 | 0 | 0 | 0 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5422 | 1001 | 24048906
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 0 | Reserve
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 13230
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | Reserve
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 86 | 1522500 | Unit-2 under maint.
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 188 | 4033876
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Reserve
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 0 | Reserve
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Reserve
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 8 | 76896 | Reserve
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 0 | 259680
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 2277
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 24254 | Reserve
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 13440 | Reserve
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 25091 | Reserve
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 0 | 0 | Reserve
| SS Power I |  | SS Power | 1*612 | 612 | 400 | 7581817
| Cox's Bazar Wind |  | IPP | 66 | 0 | 6 | 259200 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 210 | 8967272 | On test.
| Chattogram area Total |  |  |  | 3157 | 898 | 22779533
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 0 | Under maint.
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 295 | 7204600 | Under maint.
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 3837000
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 380 | 6678000
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 49 | 337680
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 384312
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Under maint.
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 0 | Reserve
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Reserve
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 8100 | Reserve
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 32 | 1541760 | Low demand
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 0 | 61000 | Reserve
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 0 | 62800 | Reserve
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Reserve
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 0 | 79200 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2896 | 807 | 20194452
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 101 | 1530240 | Low demand
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Contract Expired
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 6200
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 0 | 36000 | Reserve
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 0 | 4800 | Reserve
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 104590
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 101 | 1681830
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 976000 | Under maint.
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Reserve
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 358200
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 25104 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 32 | 448128 | Low demand
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 0 | 0 | Gas shortage
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 194 | 3962640 | Low demand
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 93000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 0 | 61344 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 5562000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 367 | 8316000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 92160
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 7931800
| Sylhet Area Total |  |  |  | 2427 | 1394 | 27826376
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 333 | 11364363
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 0 | Reserve
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Reserve
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 46800
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 408 | 8865455 | Low demand
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 741 | 20276618
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 3 | 118300 | Low demand
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 1044000 | Low demand
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 490 | 12736700 | Low demand
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 110 | 2583736
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve
| Barisal 307 MW |  | IPP | 307*1 | 307 | 0 | 2072700 | Low demand
| Barisal Area Total |  |  |  | 2265 | 603 | 18555436
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 370 | 6723527 | Low demand
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
135 | Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 0 | 62064 | Reserve
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | Reserve
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Reserve
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 9420
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 812 | 19492731 | Low demand
| Rajshahi Area Total |  |  |  | 3631 | 1182 | 26287742
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4190000 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | Reserve
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 37736
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 0 | 0 | Reserve
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 177413
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 997000
| Rangpur Area Total |  |  |  | 950 | 170 | 5402149
| Total |  |  |  | 24599 | 6897 | 167053042
| Eastern Grid Total |  |  |  | 14516 | 4201 | 96531097
| Western Grid Total |  |  |  | 10083 | 2696 | 70521945
| National Grid Total |  |  |  | 24599 | 6897 | 167053042
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-11-17
| (a) ENTIRE EASTERN GRID : |  | 4360.57 | MW | (b) ENTIRE WESTERN GRID : |  | 2259.8 | MW
| i) Dhaka area |  | 2779.97 | MW | i) Khulna area |  | 845.3 | MW
| ii) Chittagong area |  | 708.6 | MW | ii) Rajshahi area |  | 822.4 | MW
| iii) Comilla area |  | 100 | MW | iii) Barisal area |  | 69.1 | MW
| iv) Mymensingh area |  | 619 | MW | iv) Rangpur area |  | 523 | MW
| v) Sylhet area |  | 153 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 6620.37 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 6 | 20:00 | Chhatak | 23 | 00:00 | Kamrangirchar | 39 | 04:00 | Narinda | 38 | 00:00 | Sherpur | 84 | 18:00
2 | AKSML | 11 | 19:00 | Chowmuhani | 112 | 00:00 | Kaptai | N/A | N/A | Narshingdi | 140 | 00:00 | Shikalbaha | 23 | 00:00
3 | Aftabnagar | 26 | 00:00 | Chuadanga | 62 | 18:00 | Kazla | 67 | 02:00 | Natore | 84 | 18:00 | Shikalbaha-230 | N/A | N/A
4 | Agargaon | 56 | 11:00 | Coxsbazar | 85 | 21:00 | Keranigonj | 54 | 19:00 | Nawabganj | 29 | 20:00 | Shitalakhya | 67 | 00:00
5 | Agrabad | 52 | 22:00 | Cumilla(N) | 90 | 01:00 | Khagrachori | 16 | 00:00 | Netrakona | 81 | 18:00 | Sholosohor | 24 | 14:00
6 | Amnura | 31 | 18:00 | Cumilla(S) | 128 | 00:00 | Khulna | 68 | 13:00 | New | 43.6 | 00:00 | Shyampur | 148 | 00:00
7 | Ashuganj | 69 | 00:00 | Daudkandi | 95 | 00:00 | Khulshi | 141 | 00:00 | Niamatpur | 44 | 18:30 | Siddhirganj | 88 | 00:00
8 | BIPTC | N/A | N/A | Dhaka | 14 | 11:00 | Kishoreganj | 80 | 02:00 | Noapara | 26 | 00:00 | Sirajganj | 59 | 18:00
9 | BSRM | 135 | 15:00 | Dhamrai | 76 | 00:00 | Kodda | 195 | 00:00 | PHP | 5 | 07:00 | Sonargaon | 75 | 01:00
10 | Bagerhat | 46 | 22:00 | Dhanmondi | 72 | 13:00 | Kulaura | 26 | 00:00 | Pabna | 68 | 18:00 | Sreemongol | 39 | 00:00
11 | Bakulia | 66 | 00:00 | Dohazari | 50 | 21:00 | Kurigram | 45 | 18:00 | Palashbari | 72 | 18:00 | Sreepur | 43 | 00:00
12 | Banani | 15 | 00:00 | Faridpur | 93 | 20:00 | Kushtia | 90 | 18:30 | Panchagarh | 39 | 19:00 | Srinagar | 25.67 | 21:00
13 | Bangabhaban | 5 | 11:00 | Fatullah | 58 | 00:00 | Lalbag | 76 | 00:00 | Patuakhali | 51 | 00:00 | Sunamganj | 31 | 00:00
14 | Barapukuria | 40 | 18:00 | Fenchuganj | 24 | 01:00 | Lalmonirhat | 32 | 18:30 | Payra | 12 | 20:00 | Sylhet | 14 | 00:00
15 | Barguna | 10 | 01:00 | Feni | 71 | 00:00 | MI_Cement | 19 | 08:00 | Postogola | 45 | 00:00 | Sylhet-132 | 88 | 00:00
16 | Barishal | 55 | 00:00 | GPH | 94 | 14:00 | Madanganj | 32 | 00:00 | Purbachal | 14 | 00:00 | TK | 18.5 | 00:00
17 | Barishal-230 | 36 | 00:00 | Ghorashal | 45 | 00:00 | Madaripur | 49 | 00:00 | Purbasadipur | 85 | 19:30 | Tangail | 140 | 22:00
18 | Baroaulia | 58 | 00:00 | Goalpara | 24 | 00:00 | Madartek | 62.6 | 13:00 | Rahim | 42 | 00:00 | Thakurgaon | 64 | 18:00
19 | Baroirhat | 26 | 00:00 | Gollamari | 33 | 00:00 | Madunaghat | 32 | 22:00 | Rajbari | 40 | 19:00 | Tongi | 60 | 00:00
20 | Bashundhara | 104 | 13:00 | Gopalganj | 50.3 | 21:00 | Magura | 40 | 18:00 | Rajendrapur | 74 | 00:00 | Ullon | 42 | 13:00
21 | BashundharaCement | 0 | 00:00 | Gulshan | 60 | 12:00 | Mahasthangarh | 46 | 18:00 | Rajshahi | 92 | 13:00 | Uttara | 43 | 12:00
22 | Beanibazar | 40 | 00:00 | Halishahar | 58 | 00:00 | Manikganj | 76 | 00:00 | Rajshahi-230 | 24 | 00:00 | UttaraNew | 41 | 12:00
23 | Benapole | 36 | 18:00 | HaripurSBU | 141 | 00:00 | Maniknagar | 42 | 00:00 | Ramganj | 52 | 00:00 | Zigatola | 68 | 00:00
24 | Bhaluka | 102 | 00:00 | Hasnabad | 84 | 00:00 | Matarbari | 15 | 00:00 | Rampur | 24 | 23:00
25 | Bhandaria | 30 | 00:00 | Hathazari | 51 | 12:00 | Matuail | 57 | 01:00 | Rangamati | 12 | 13:00
26 | Bhangura | 19 | 18:00 | Ishurdi | 48 | 18:00 | Millgate | 71 | 00:00 | Rangpur | 95 | 13:00
27 | Bheramara(GK) | 34 | 18:00 | Jaldhaka | 47 | 18:00 | Mirpur | 92 | 13:00 | Ruppur | 4.4 | 10:00
28 | Bhulta | 211 | 00:00 | Jamalpur | 99 | 18:00 | Mirsorai | 2 | 11:00 | SSM | 6 | 06:00
29 | Bog-Sherpur | 46 | 18:00 | Jashore | 85 | 18:00 | Mirzapur | 0 | 00:00 | Saidpur | 68 | 18:30
30 | Bogura | 101 | 19:30 | Jhenaidah | 78 | 18:00 | Mithapukur | 28 | 18:00 | Satkhira | 67 | 19:00
31 | Borhanuddin | 29 | 01:00 | Joydebpur | 112 | 00:00 | Modern | 0 | 00:00 | Satmasjid | 72 | 14:00
32 | Brahmanbaria | 114 | 00:00 | Joypurhat | 36 | 19:00 | Mogbazar | 64.6 | 00:00 | Savar | 122 | 12:00
33 | Cantonment | 94 | 13:00 | Juldah | 15 | 23:00 | Mongla | 25 | 08:00 | SevenRings | 8.21 | 01:00
34 | Chandpur | 39 | 00:00 | KSRM | 25 | 03:00 | Motijheel | 23 | 13:00 | ShahCement | 18 | 00:00
35 | Chandraghona | 21 | 12:00 | Kabirpur | 189 | 00:00 | Munshiganj | 70 | 00:00 | Shahjadpur | 66 | 18:30
36 | Chapai | 47 | 19:30 | Kachua | 40 | 00:00 | Mymensingh | 135 | 08:00 | Shahjibazar | 81 | 00:00
37 | Charsaidpur | 25 | 02:00 | Kallyanpur | 72 | 00:00 | Naogaon | 77 | 20:00 | Shahmirpur | 32.5 | 00:00
38 | Chauddagram | 25 | 00:00 | Kalurghat | 20 | 00:00 | Narail | 27 | 18:00 | Shariatpur | 40 | 00:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-11-17 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 418 | 16:00 | 388 | 00:00 | Gopalganj | 421 | 16:00 | 402 | 00:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 406 | 17:00 | 382 | 02:00
| Bhulta | 422 | 16:00 | 396 | 00:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bibiana | 417 | 17:00 | 398 | 00:00 | Payra | 424 | 16:00 | 413 | 00:00
| BIPTC | 407 | 14:00 | 396 | 10:00 | Rahanpur | 414 | 03:00 | 395 | 18:00
| Bogura | N/A | N/A | N/A | N/A | Rampal | 419 | 16:00 | 404 | 00:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 249 | 16:00 | 231 | 00:00 | Hasnabad | 248 | 16:00 | 236 | 22:00
| AKSML | 234 | 17:00 | 220 | 23:00 | Hathazari | 239 | 16:00 | 221 | 14:00
| Aminbazar | 246 | 16:00 | 232 | 00:00 | Ishurdi | 238 | 16:00 | 226 | 18:00
| Ashuganj | 242 | 16:00 | 232 | 19:30 | Jhenaidah | 237 | 16:00 | 224 | 18:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 241 | 06:00 | 235 | 02:00
| Baghabari | 230 | 06:00 | 223 | 18:30 | Keranigonj | 247 | 16:00 | 231 | 00:00
| Barapukuria | 228 | 05:00 | 214 | 18:00 | Khulna(S) | 243 | 16:00 | 231 | 19:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 246 | 16:00 | 140 | 22:00 | Maniknagar | 246 | 15:00 | 234 | 00:00
| Bheramara | 239 | 16:00 | 227 | 18:00 | Meghnaghat | 251 | 15:00 | 240 | 00:00
| Bhulta | 247 | 15:00 | 234 | 00:00 | Mirsorai | 233 | 16:00 | 223 | 01:00
| Bibiana | 237 | 17:00 | 228 | 01:00 | Rajshahi | 237 | 16:00 | 223 | 19:30
| BIPTC | 237 | 16:00 | 223 | 18:00 | Rampal | 240 | 16:00 | 229 | 19:00
| Bogura | 237 | 04:00 | 226 | 18:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 250 | 16:00 | 241 | 00:00 | Rampura | 246 | 15:00 | 234 | 00:00
| BSRM | 237 | 16:00 | 223 | 00:00 | Shikalbaha | 231 | 17:00 | 218 | 00:00
| Cumilla(N) | 243 | 16:00 | 229 | 00:00 | Shyampur | 246 | 15:00 | 232 | 00:00
| Fenchuganj | 241 | 16:00 | 231 | 01:00 | Siddhirganj | 247 | 15:00 | 235 | 00:00
| Ghorashal | 248 | 15:00 | 238 | 00:00 | Sirajgonj | 241 | 16:00 | 233 | 18:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 239 | 16:00 | 230 | 18:00
| GPH | 237 | 16:00 | 220 | 00:00 | Tongi | 241 | 15:00 | 228 | 00:00
| Haripur | 246 | 15:00 | 233 | 00:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 142 | 14:00 | 133 | 20:00 | Lalbag | 140 | 14:00 | 130 | 19:30
| Agargaon | 141 | 16:00 | 133 | 19:30 | Lalmonirhat | 134 | 05:00 | 123 | 18:00
| Agrabad | 143 | 16:00 | 129 | 01:00 | Madanganj | 142 | 15:00 | 132 | 00:00
| AKS | 133 | 18:30 | 125 | 22:00 | Madaripur | 138 | 18:00 | 129 | 00:00
| Aminbazar | 146 | 16:00 | 134 | 00:00 | Madartek | 141 | 14:00 | 131 | 19:30
| Amnura | 137 | 02:00 | 128 | 18:00 | Madunaghat | 141 | 16:00 | 129 | 00:00
| Ashuganj | 145 | 15:00 | 139 | 00:00 | Magura | 139 | 16:00 | 130 | 18:00
| Bagerhat | 135 | 15:00 | 125 | 18:30 | Mahasthangarh | 138 | 05:00 | 130 | 18:00
| Bakulia | 142 | 16:00 | 129 | 00:00 | Manikganj | 138 | 16:00 | 126 | 00:00
| Banani | 140 | 07:00 | 133 | 19:00 | Maniknagar | 143 | 14:00 | 136 | 19:00
| Bangabhaban | 143 | 14:00 | 136 | 00:00 | Matarbari | 140 | 16:00 | 122 | 07:00
| Barapukuria | 142 | 05:00 | 130 | 18:00 | Matuail | 142.3 | 14:00 | 131.7 | 00:00
| Barguna | 138 | 14:00 | 134 | 00:00 | Millgate | 140 | 06:00 | 132 | 19:30
| Barishal | 142 | 17:00 | 131 | 00:00 | Mirpur | 142 | 14:00 | 133 | 00:00
| Barishal-230 | 140 | 15:00 | 135 | 00:00 | Mirzapur | 142 | 16:00 | 129 | 00:00
| Baroaulia | 142 | 16:00 | 130 | 00:00 | Mithapukur | 137 | 04:00 | 125 | 18:00
| Baroirhat | 142 | 16:00 | 126 | 00:00 | MI_Cement | 142.5 | 16:00 | 132 | 00:00
| Bashundhara | 143 | 15:00 | 132 | 19:30 | Modern | 139 | 17:00 | 130 | 01:00
| BashundharaCement | 142 | 15:00 | 132 | 00:00 | Mogbazar | 143 | 15:00 | 131 | 09:00
| Beanibazar | 132 | 17:00 | 127 | 00:00 | Mongla | 135 | 05:00 | 125 | 19:30
| Benapole | 135 | 02:00 | 127 | 18:00 | Motijheel | 143 | 14:00 | 136 | 00:00
| Bhaluka | 136 | 14:00 | 128 | 19:30 | Munshiganj | 142 | 15:00 | 134 | 03:00
| Bhandaria | 139 | 11:00 | 130 | 12:00 | Mymensingh | 137 | 16:00 | 124 | 13:00
| Bhangura | 142 | 03:00 | 135 | 18:30 | Naogaon | 136 | 06:00 | 127 | 18:30
| Bheramara | 138 | 15:00 | 131 | 18:00 | Narail | 139 | 06:00 | 130 | 18:30
| Bheramara(GK) | 138 | 16:00 | 130 | 18:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bhulta | 135 | 15:00 | 118 | 00:00 | Narshingdi | 136 | 14:00 | 126 | 00:00
| Bog-Sherpur | 139 | 03:00 | 131 | 18:00 | Natore | 138 | 15:00 | 128 | 12:00
| Bogura | 139 | 04:00 | 132 | 18:00 | Nawabganj | 141 | 14:00 | 130 | 19:30
| Bogura-230 | 139 | 04:00 | 131 | 18:00 | Netrakona | 133 | 14:00 | 124 | 07:00
| Brahmanbaria | 137 | 16:00 | 123 | 00:00 | New | 141 | 16:00 | 133 | 20:00
| Cantonment | 140 | 16:00 | 133 | 19:00 | Niamatpur | 135 | 06:00 | 125 | 18:00
| Chandpur | 146 | 16:00 | 122 | 00:00 | Noapara | 136 | 15:00 | 127 | 19:00
| Chandraghona | 142 | 16:00 | 130 | 00:00 | Pabna | 140 | 16:00 | 133 | 18:00
| Chapai | 136 | 05:00 | 129 | 18:00 | Palashbari | 137 | 06:00 | 124 | 18:00
| Charsaidpur | 142 | 15:00 | 131 | 00:00 | Panchagarh | 134 | 04:00 | 115 | 18:00
| Chauddagram | 145 | 16:00 | 127 | 00:00 | Patuakhali | 137 | 14:00 | 133 | 00:00
| Chhatak | 134 | 20:00 | 127 | 00:00 | Payra | 137 | 14:00 | 134 | 00:00
| Chowmuhani | 145 | 17:00 | 122 | 00:00 | PHP | 143 | 16:00 | 125 | 00:00
| Chuadanga | 137 | 05:00 | 128 | 18:00 | Postogola | 145 | 16:00 | 134 | 00:00
| Coxsbazar | 137 | 16:00 | 124 | 22:00 | Purbachal | 143 | 14:00 | 133 | 18:30
| Cumilla(N) | 145 | 16:00 | 131 | 00:00 | Purbasadipur | 135 | 03:00 | 117 | 18:00
| Cumilla(S) | 144 | 16:00 | 130 | 00:00 | Rahanpur | 137 | 02:00 | 132 | 08:00
| Daudkandi | 143 | 15:00 | 124 | 00:00 | Rahim | 142 | 16:00 | 131 | 00:00
| Dhaka | 143 | 15:00 | 133 | 20:00 | Rajbari | 136 | 16:00 | 129 | 00:00
| Dhamrai | 142 | 16:00 | 132 | 18:30 | Rajendrapur | 139 | 16:00 | 126 | 00:00
| Dhanmondi | 142 | 15:00 | 132.4 | 00:00 | Rajshahi | 138 | 06:00 | 131 | 18:00
| Dohazari | 140 | 17:00 | 130 | 00:00 | Rajshahi-230 | 139 | 16:00 | 127 | 18:00
| Faridpur | 135 | 15:00 | 130 | 00:00 | Ramganj | 142 | 16:00 | 121 | 00:00
| Fatullah | 144 | 16:00 | 133 | 00:00 | Rampur | 143 | 16:00 | 128 | 00:00
| Fenchuganj | 137 | 18:00 | 131 | 01:00 | Rampura | 143 | 15:00 | 134 | 18:30
| Feni | 143 | 16:00 | 125 | 00:00 | Rangamati | 142 | 16:00 | 129 | 00:00
| Ghorashal | 146 | 15:00 | 139 | 00:00 | Rangpur | 136 | 05:00 | 127 | 18:00
| Goalpara | 136 | 06:00 | 129 | 18:30 | Ruppur | 141 | 15:00 | 134 | 18:00
| Gollamari | 136 | 16:00 | 129 | 19:00 | Saidpur | 136 | 06:00 | 122 | 18:00
| Gopalganj | 135 | 16:00 | 128 | 00:00 | Satkhira | 134 | 06:00 | 120 | 23:00
| Gopalganj-400 | 135 | 16:00 | 129 | 00:00 | Satmasjid | 141 | 16:00 | 133 | 19:00
| Gulshan | 142 | 15:00 | 133 | 19:30 | Savar | 142 | 15:00 | 132 | 00:00
| Halishahar | 142 | 16:00 | 129 | 00:00 | SevenRings | 148 | 16:00 | 139 | 00:00
| Haripur | 142 | 15:00 | 131 | 00:00 | ShahCement | 143 | 16:00 | 131 | 00:00
| HaripurSBU | 142 | 15:00 | 131 | 00:00 | Shahjadpur | 145 | 15:00 | 139 | 18:00
| Hasnabad | 142 | 14:00 | 134 | 00:00 | Shahjibazar | 135 | 18:30 | 124 | 00:00
| Hathazari | 142 | 16:00 | 130 | 00:00 | Shahmirpur | 141 | 16:00 | 130 | 00:00
| Ishurdi | 140 | 05:00 | 133 | 18:00 | Shariatpur | 136 | 15:00 | 129 | 00:00
| Jaldhaka | 136 | 05:00 | 119 | 18:00 | Sherpur | 128 | 11:00 | 118 | 13:00
| Jamalpur | 130 | 11:00 | 120 | 13:00 | Shikalbaha | 131 | 16:00 | 112 | 13:00
| Jashore | 136 | 16:00 | 128 | 18:00 | Shikalbaha-230 | 142 | 17:00 | 132 | 00:00
| Jhenaidah | 140 | 16:00 | 132 | 18:00 | Shitalakhya | 142.5 | 16:00 | 132 | 00:00
| Jhenaidah-230 | 140 | 16:00 | 131 | 18:30 | Sholosohor | 142 | 16:00 | 129 | 00:00
| Joydebpur | 145 | 15:00 | 134 | 19:30 | Shyampur | 141 | 15:00 | 135 | 00:00
| Joypurhat | 135 | 03:00 | 128 | 12:00 | Shyampur-230 | 142 | 15:00 | 134 | 00:00
| Juldah | 143 | 16:00 | 131 | 00:00 | Siddhirganj | 142 | 15:00 | 132 | 00:00
| Kabirpur | 140 | 16:00 | 130 | 00:00 | Sirajganj | 140 | 02:00 | 132 | 18:00
| Kachua | 145 | 17:00 | 125 | 00:00 | Sonargaon | 143 | 16:00 | 129 | 00:00
| Kaliakoir | 136 | 05:00 | 133 | 02:00 | Sreemongol | 135 | 15:00 | 126 | 00:00
| Kallyanpur | 145 | 14:00 | 135 | 00:00 | Sreepur | 138 | 06:00 | 131 | 18:00
| Kalurghat | 140 | 17:00 | 129 | 00:00 | Srinagar | 141 | 14:00 | 131 | 19:00
| Kamrangirchar | 142 | 15:00 | 131 | 19:00 | SSM | 145 | 16:00 | 133 | 00:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 132 | 18:30 | 127 | 00:00
| Kazla | 142 | 07:00 | 135 | 19:30 | Sylhet | 133 | 15:00 | 129 | 00:00
| Keranigonj | 140 | 14:00 | 131 | 19:00 | Sylhet-132 | 132 | 16:00 | 129 | 00:00
| Khagrachori | 141 | 16:00 | 129 | 00:00 | Tangail | 140 | 16:00 | 127 | 00:00
| Khulna | 135 | 16:00 | 127 | 18:00 | Thakurgaon | 134 | 04:00 | 114 | 18:00
| Khulna(S) | 136 | 16:00 | 128 | 19:00 | TK | 140 | 17:00 | 130 | 00:00
| Khulshi | 140 | 17:00 | 127 | 00:00 | Tongi | 142 | 15:00 | 134 | 21:00
| Kishoreganj | 140 | 09:00 | 132 | 19:30 | Ullon | 142 | 15:00 | 132 | 19:30
| Kodda | 143 | 13:00 | 126 | 00:00 | Uttara | 141 | 16:00 | 132 | 20:00
| KSRM | 141 | 16:00 | 129 | 00:00 | UttaraNew | 143 | 14:00 | 134 | 00:00
| Kulaura | 136 | 16:00 | 130 | 00:00 | Zigatola | 140 | 15:00 | 131 | 18:30
| Kurigram | 135 | 06:00 | 120 | 18:00
| Kushtia | 138 | 16:00 | 130 | 18:30

## L-Curve
Date | 2023-11-17
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 230 | 4059 | 2611 | 6670 |  |  |  | QF-LDC-11
0:30 | 515 | 4665.5 | 3083 | 7748.5 | Date: | 2023-11-17
1:00 | 800 | 5272 | 3555 | 8827
1:30 | 780 | 5031 | 3497 | 8528
2:00 | 760 | 4790 | 3439 | 8229
2:30 | 690 | 4773.5 | 3335.5 | 8109 | [5 empty] | Gen. at Eve. Peak | 6897 | 6897 MW (21:00 )
3:00 | 620 | 4757 | 3232 | 7989 | [6 empty] | 21:00
3:30 | 615 | 4681 | 3118.5 | 7799.5 | [5 empty] | Gen. at Day Peak | 7098 | 7098 MW (12:00 )
4:00 | 610 | 4605 | 3005 | 7610 | [6 empty] | 12:00
4:30 | 545 | 4562 | 2943.5 | 7505.5 | [5 empty] | Highest Generation | 8827
5:00 | 480 | 4519 | 2882 | 7401 | [6 empty] | 1:00
5:30 | 400 | 4389.5 | 2805 | 7194.5
6:00 | 320 | 4260 | 2728 | 6988
6:30 | 260 | 4209 | 2723.5 | 6932.5
7:00 | 200 | 4158 | 2719 | 6877
7:30 | 300 | 4136 | 2825.5 | 6961.5
8:00 | 400 | 4114 | 2932 | 7046
8:30 | 515 | 3940 | 3005.5 | 6945.5
9:00 | 630 | 3766 | 3079 | 6845
9:30 | 650 | 3701 | 3097.5 | 6798.5
10:00 | 670 | 3636 | 3116 | 6752
10:30 | 680 | 3647.5 | 3129 | 6776.5
11:00 | 690 | 3659 | 3142 | 6801
11:30 | 695 | 3729 | 3220.5 | 6949.5
12:00 | 700 | 3799 | 3299 | 7098
12:30 | 675 | 3895.5 | 3363 | 7258.5
13:00 | 650 | 3992 | 3427 | 7419
13:30 | 590 | 3677 | 3154 | 6831
14:00 | 530 | 3362 | 2881 | 6243
14:30 | 423 | 3162 | 2678 | 5840
15:00 | 316 | 2962 | 2475 | 5437
15:30 | 273 | 2834 | 2333 | 5167
16:00 | 230 | 2706 | 2191 | 4897
16:30 | 195 | 2638 | 2205 | 4843
17:00 | 160 | 2570 | 2219 | 4789
17:30 | 237 | 3062.5 | 2386 | 5448.5
18:00 | 314 | 3555 | 2553 | 6108
18:30 | 289 | 3674 | 2575 | 6249
19:00 | 264 | 3793 | 2597 | 6390
19:30 | 290 | 3950 | 2657 | 6607
20:00 | 340 | 4123 | 2647 | 6770 |  |  |  | Executive Engineer
20:30 | 328 | 4162 | 2671.5 | 6833.5 |  |  |  | Network Operation Division
21:00 | 316 | 4201 | 2696 | 6897
21:30 | 288 | 4212.5 | 2697 | 6909.5
22:00 | 260 | 4224 | 2698 | 6922 |  |  |  |  | Page 6 of 7
22:30 | 255 | 4214 | 2664 | 6878
23:00 | 250 | 4204 | 2630 | 6834
23:30 | 240 | 4131.5 | 2620.5 | 6752
24:00 | 230 | 4059 | 2611 | 6670
6897 MW (21:00 )
7098 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-11-17 |  | Energy |  | 167053042
QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 2649 | 344 | 1186 | 0 | 0 | 2404 | 46 | 0 | 0 | 36 | 0 | 5 | 0
0:30 | 2896.5 | 628 | 1276.5 | 0 | 47 | 2728 | 89 | 0 | 0 | 76 | 0 | 7.5 | 0 |  | Date: | 43785
1:00 | 3144 | 912 | 1367 | 0 | 94 | 3052 | 132 | 0 | 0 | 116 | 0 | 10 | 0
1:30 | 3029 | 912 | 1294.5 | 0 | 55.5 | 2981 | 132 | 0 | 0 | 114 | 0 | 10 | 0 | [8 empty] | Total Energy | 167.053 | 167.053 | Total Energy Gen 167.053 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 167.053 MKWHr
2:00 | 2914 | 912 | 1222 | 0 | 17 | 2910 | 132 | 0 | 0 | 112 | 0 | 10 | 0 | [8 empty] | Energy not Served | 0 | 0
2:30 | 2920.5 | 822.5 | 1198.5 | 0 | 17 | 2900 | 132 | 0 | 0 | 109 | 0 | 9.5 | 0 | [8 empty] | Energy Requirement | 167.053 | 167.053
3:00 | 2927 | 733 | 1175 | 0 | 17 | 2890 | 132 | 0 | 0 | 106 | 0 | 9 | 0
3:30 | 2882.5 | 657 | 1123.5 | 0 | 16.5 | 2878.5 | 132 | 0 | 0 | 102 | 0 | 7.5 | 0 | [7 empty] | Shortage
4:00 | 2838 | 581 | 1072 | 0 | 16 | 2867 | 132 | 0 | 0 | 98 | 0 | 6 | 0
4:30 | 2822 | 530.5 | 1041 | 0 | 8 | 2867.5 | 132 | 0 | 0 | 100 | 0 | 4.5 | 0
5:00 | 2806 | 480 | 1010 | 0 | 0 | 2868 | 132 | 0 | 0 | 102 | 0 | 3 | 0
5:30 | 2735.5 | 405 | 990 | 0 | 0 | 2857.5 | 109 | 0 | 0 | 93 | 0 | 4.5 | 0
6:00 | 2665 | 330 | 970 | 0 | 0 | 2847 | 86 | 0 | 0 | 84 | 0 | 6 | 0
6:30 | 2650 | 329.5 | 928 | 0 | 0 | 2843.5 | 86 | 0 | 0 | 87 | 1 | 7.5 | 0 | [6 empty] | Coal
7:00 | 2635 | 329 | 886 | 0 | 0 | 2840 | 86 | 0 | 0 | 90 | 2 | 9 | 0
7:30 | 2636 | 425.5 | 878.5 | 0 | 1 | 2845 | 66 | 0 | 0 | 85 | 18 | 6.5 | 0 | [5 empty] | Oil
8:00 | 2637 | 522 | 871 | 0 | 2 | 2850 | 46 | 0 | 0 | 80 | 34 | 4 | 0
8:30 | 2604.5 | 546.5 | 853.5 | 0 | 1 | 2713.5 | 46 | 0 | 0 | 78 | 90.5 | 12 | 0
9:00 | 2572 | 571 | 836 | 0 | 0 | 2577 | 46 | 0 | 0 | 76 | 147 | 20 | 0
9:30 | 2576 | 575.5 | 782.5 | 0 | 0 | 2564 | 46 | 0 | 0 | 73 | 161.5 | 20 | 0
10:00 | 2580 | 580 | 729 | 0 | 0 | 2551 | 46 | 0 | 0 | 70 | 176 | 20 | 0
10:30 | 2582 | 556.5 | 794 | 0 | 0 | 2502 | 46 | 0 | 0 | 75 | 209.5 | 11.5 | 0
11:00 | 2584 | 533 | 859 | 0 | 0 | 2453 | 46 | 0 | 0 | 80 | 243 | 3 | 0
11:30 | 2606 | 604 | 918 | 0 | 0 | 2454.5 | 46 | 0 | 0 | 69 | 247.5 | 4.5 | 0
12:00 | 2628 | 675 | 977 | 0 | 0 | 2456 | 46 | 0 | 0 | 58 | 252 | 6 | 0
12:30 | 2701 | 675 | 1018 | 0 | 0 | 2482.5 | 46 | 0 | 0 | 71 | 250.5 | 14.5 | 0
13:00 | 2774 | 675 | 1059 | 0 | 0 | 2509 | 46 | 0 | 0 | 84 | 249 | 23 | 0
13:30 | 2774 | 675 | 1059 | 0 | 0 | 2509 | 46 | 0 | 0 | 84 | 249 | 23 | 0
14:00 | 2774 | 675 | 1059 | 0 | 0 | 2509 | 46 | 0 | 0 | 84 | 249 | 23 | 0
14:30 | 2387 | 419 | 894 | 0 | 0 | 2436.5 | 23 | 0 | 0 | 73 | 182.5 | 13 | 0
15:00 | 2000 | 163 | 729 | 0 | 0 | 2364 | 0 | 0 | 0 | 62 | 116 | 3 | 0
15:30 | 1870 | 197 | 738.5 | 0 | 0 | 2226.5 | 0 | 0 | 0 | 49 | 83 | 3 | 0
16:00 | 1740 | 231 | 748 | 0 | 0 | 2089 | 0 | 0 | 0 | 36 | 50 | 3 | 0
16:30 | 1760 | 238 | 710.5 | 0 | 0 | 2072 | 0 | 0 | 0 | 20 | 26.5 | 16 | 0
17:00 | 1780 | 245 | 673 | 0 | 0 | 2055 | 0 | 0 | 0 | 4 | 3 | 29 | 0
17:30 | 2124.5 | 296 | 860 | 0 | 0 | 2138 | 0 | 0 | 0 | 2 | 1.5 | 26.5 | 0
18:00 | 2469 | 347 | 1047 | 0 | 0 | 2221 | 0 | 0 | 0 | 0 | 0 | 24 | 0
18:30 | 2509 | 345 | 1075 | 0 | 0 | 2296.5 | 0 | 0 | 0 | 4 | 0 | 19.5 | 0
19:00 | 2549 | 343 | 1103 | 0 | 0 | 2372 | 0 | 0 | 0 | 8 | 0 | 15 | 0
19:30 | 2614 | 343 | 1236 | 0 | 0 | 2392 | 0 | 0 | 0 | 14 | 0 | 8 | 0
20:00 | 2647 | 278 | 1274 | 0 | 0 | 2451 | 86 | 0 | 0 | 26 | 0 | 8 | 0
20:30 | 2677 | 305.5 | 1258.5 | 0 | 0 | 2470.5 | 86 | 0 | 0 | 29 | 0 | 7 | 0
21:00 | 2707 | 333 | 1243 | 0 | 0 | 2490 | 86 | 0 | 0 | 32 | 0 | 6 | 0
21:30 | 2732.5 | 338.5 | 1246.5 | 0 | 0 | 2481 | 66 | 0 | 0 | 35 | 0 | 10 | 0
22:00 | 2758 | 344 | 1250 | 0 | 0 | 2472 | 46 | 0 | 0 | 38 | 0 | 14 | 0
22:30 | 2760 | 344 | 1209 | 0 | 0 | 2474 | 46 | 0 | 0 | 35 | 0 | 10 | 0
23:00 | 2762 | 344 | 1168 | 0 | 0 | 2476 | 46 | 0 | 0 | 32 | 0 | 6 | 0
23:30 | 2705.5 | 344 | 1177 | 0 | 0 | 2440 | 46 | 0 | 0 | 34 | 0 | 5.5 | 0 |  | Max Temp. in Dhaka |  | 22.6°C
24:00 | 2649 | 344 | 1186 | 0 | 0 | 2404 | 46 | 0 | 0 | 36 | 0 | 5 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 167.053 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 167.053 MKWHr
Note on W13: Author:

## Generation
g | 2023-11-17
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 92 | 92 | 92 | 92 | 92 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 20 | [7 empty] | 46 | 46 | 46 | 46 | 46 | 1138500
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 0 | [13 empty] | 40 | 40 | 0 |  |  | 384000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 0 | 0 | 0 |  |  | 0 | 3 | 1 | 3 | 1 | [10 empty] | 13230
6 | Sikalbaha 225MW CCPP (Gas) | 188 | 188 | 188 | 188 | 188 | 188 | 162 | 162 | 137 | 142 | 143 | 143 | 174 | 142 | 142 | 142 | 142 | 188 |  | 188 | 188 | 188 | 188 | 188 | 188 | 186 | 4033876
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [25 empty] | 0 | 0
12 | Hathazari 100 MW peaking PP | [26 empty] | 0
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [24 empty] | 39 | 41 | 63000
17 | Siddhirganj 335 MW CCPP | 231 | 222 | 216 | 216 | 216 | 170 | 170 | 170 | 160 | 160 | 160 | 160 | 170 | 140 | 140 | [10 empty] | 0 | 2879392
18 | Kodda 300 MW PP Unit-2 (Summit) | [25 empty] | 0 | 0
19 | Ashuganj 195 MW PP (APSCL-United) | [25 empty] | 0 | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 110 | 110 | 110 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 3869000
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 377 | 335 | 335 | 336 | 325 | 307 | 306 | 305 | 295 | 275 | 265 | 265 | 264 | 260 | 263 | 261 | 270 | 330 |  | 350 | 350 | 400 | 400 | 400 | 400 | 392 | 7581817
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 51 | 10 | 10 | 10 | 5 | [14 empty] | 10 | 10 | 32 | 49 | 47 | 50 | 51 | 337680
33 | Ashuganj 225 MW CCPP
34 | Ashuganj 450 MW CCPP(South) | 270 | 270 | 270 | 240 | 240 | 240 | 240 | 240 | 260 | 280 | 270 | 295 | 270 | 245 | [11 empty] | 0 | 3837000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 270 | 270 | 260 | 260 | 260 | 285 | 295 | 285 | 310 | 290 | 275 | 270 | 270 | 280 | 310 |  | 310 | 360 | 320 | 295 | 280 | 300 | 280 | 7204600
| Ashuganj 420 MW CCPP(East) | 250 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 330 | 230 | 230 | 230 | 215 | 375 |  | 330 | 330 | 355 | 380 | 385 | 350 | 320 | 6678000
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 289 | 266 | 257 | 253 | 252 | 241 | 233 | 233 | 234 | 240 | 286 | 299 | 299 | 254 | 232 | 231 | 232 | 316 |  | 343 | 334 | 352 | 399 | 418 | 419 | 385 | 7057410
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 180 | 180 | 180 | 180 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 150 | 150 | 150 | [9 empty] | 0 | 2553500
41 | Haripur 360 MW CCPP(HPL) | 120 | 112 | 112 | 106 | 105 | 112 | 112 | 112 | 107 | 121 | 142 | 141 | 141 | 132 | 156 | 177 | 152 | 231 |  | 277 | 297 | 297 | 297 | 297 | 297 | 297 | 4118000
42 | RPCL 210MW CCPP | 86 | 86 | 86 | 86 | 88 | 88 | 73 | 71 | 32 | 32 | 32 | 32 | 33 | 34 | 34 | 34 | 34 | 56 |  | 86 | 85 | 101 | 101 | 102 | 100 | 100 | 1530240
43 | Sutiakhali 50 MW Solar PP | [9 empty] | 7 | 22 | 24 | 19 | 13 | 11 | 5 | 1 | [9 empty] | 104590
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 43 | 35 | 35 | 35 | 37 | 37 | 43 | 42 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 976000
45 | Fenchugonj CCPP Phase-2 |  |  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 0
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 32 | 20 | 20 | 20 | 20 | 8 | 8 | 8 | 20 | 20 | 20 | 20 | 20 | 5 | 5 | 5 | 5 | 32 |  | 32 | 32 | 32 | 32 | 33 | 20 | 20 | 448128
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 186 | 186 | 190 | 195 | 195 | 195 | 165 | 166 | 165 |  | 164 | 183 | 203 | 194 | 203 | 203 | 200 | 3962640
51 | Sylhet 20 MW GTPP | [22 empty] | 18 | 18 | 18 | 18 | 93000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | [15 empty] | 8 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 92160
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | [20 empty] | 0 | 25104
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 10 | 10 | 10 | [13 empty] | 23 |  | 20 | 20 | 20 | 50 | 50 | 50 | 50 | 358200
56 | Shahjahanulla 25 MW PP | 16 | [22 empty] | 12 | 16 | 16 | 61344
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 260 | 270 | 260 | 250 | 240 | 160 | 160 | 130 | 120 | 180 | 295 | 300 | 200 | 130 | 130 | 130 | 240 |  | 270 | 325 | 300 | 280 | 285 | 275 | 290 | 5562000
| Bibiyana South 400 MW | 370 | 360 | 360 | 340 | 315 | 313 | 330 | 330 | 300 | 285 | 285 | 285 | 320 | 280 | 280 | 238 | 280 | 370 |  | 400 | 400 | 400 | 400 | 400 | 370 | 370 | 7931800
58 | Nababganj 55 MW PP (Southern power ) | [25 empty] | 0 | 0
59 | Tangail Palli Power Gen 22 MW | [25 empty] | 0 | 0
60 | Barabkunda 22 MW PP (Regent) | 10 | 10 | 10 | 10 | 0 | 0 | 0 | [15 empty] | 8 | 8 | 8 | 8 | 76896
61 | Narshingdi 22 MW PP (Doreen) | 18 |  | 13 | 18 | 18 | 18 | [19 empty] | 0 | 95112
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 116 | 112 | 106 | 98 | 102 | 84 | 90 | 80 | 76 | 70 | 80 | 58 | 84 | 80 | 62 | 36 | 4 | 0 |  | 8 | 14 | 26 | 32 | 38 | 32 | 36 | 1541760
64 | Malancha, Ctg. EPZ (United) | 10 | 12 | 12 | 25 | 30 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259680
65 | Feni 22 MW PP (Doreen) | 18 |  | 15 | 18
66 | Feni 11 MW PP (Doreen) | 10 | [24 empty] | 0 | 8100
67 | Jangalia 33 MW PP (Summit) | 33 | [24 empty] | 0 | 61000
68 | Cumilla 25 MW PP (Summit) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | [15 empty] | 0 | 62800
69 | Summit Ashulia | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456000
70 | Summit Madhabdi | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 12 | 13 | 0 | 13 | 13 | 13 | 204840
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 547200
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 0 | 25 | 8 | 8 | 8 | 8 | 8 | 17 | 0 | 15 | 0 | [5 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 279300
73 | Ghorashal 108 MW PP (Regent) | 80 | 80 | 42 | 13 | [13 empty] | 18 |  | 54 | 59 | 70 | 72 | 73 | 73 | 73 | 646090
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | [25 empty] | 0 | 0
| Manikgonj 162MW PP(MPGL) | [25 empty] | 0 | 0
77 | Siddhirganj 100 PP(Dutch Bangla) | [25 empty] | 0 | 0
78 | Gazipur 52 MW PP
79 | Kodda 150 MW PP | [25 empty] | 0 | 0
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [26 empty] | 0
| Gazipur 100 MW PP | [25 empty] | 0 | 0
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 2277
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | 17 | [24 empty] | 0 | 24254
82 | Madanganj 102 PP(Summit) | 17 | 17 | 17 | 16 | [21 empty] | 0 | 57437
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit) | 132 | 132 | 129 | 111 | 110 | 112 | 112 | 112 | 112 | [16 empty] | 0 | 1151505
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [25 empty] | 0 | 0
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44 MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | [16 empty] | 2 |  | 30 | 43 | 51 | 51 | 51 | 51 | 51 | 384312
94 | Gagnagar 102 MW PP (Digital Power) | [25 empty] | 0 | 0
95 | Patenga 50MW PP (Baraka)
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [25 empty] | 0 | 0
100 | Manikganj 55 MW PP (Northern) | [25 empty] | 0 | 0
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | [10 empty] | 6200
103 | Kamalaghat 54 MW PP(Banco Energy) | [25 empty] | 0 | 0
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 16 | [24 empty] | 0 | 36000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | [6 empty] | 2 | [17 empty] | 0 | 23040
115 | Juldah 100 MW PP Unit-3 (Acorn) | [25 empty] | 0 | 0
116 | Chandpur 200 MW (Desh energy)
117 | Ashuganj 150 MW PP (Midland) | [25 empty] | 0
118 | Bibiyana-III 400 MW CCPP | 365 | 365 | 365 | 365 | 365 | 340 | 361 | 365 | 365 | 365 | 365 | 365 | 365 | 247 | 245 | 237 | 237 | 398 |  | 398 | 404 | 375 | 367 | 367 | 384 | 317 | 8316000
| Jamalpur 115 MW PP (United) | [25 empty] | 0 | 4800
| Anwara 300 MW PP (United) | [25 empty] | 0 | 0
| Juldah unit-2 (Acorn) | 10 | [24 empty] | 0 | 13440
| Anlima Energy Ltd. | 17 | [24 empty] | 0 | 25091
| Bhairob 54.5 MW | [26 empty] | 79200
| Spectra Solar Plant Ltd. | [6 empty] | 0 | 1 | 6 | 4 | 7 | 13 | 9 | 6 | 9 | 1 | 0 | [9 empty] | 48080
| Chandpur 115(Doreen) | [25 empty] | 0 | 0
| Kanchan Purbachal Power Generation Ltd. | [25 empty] | 0 | 0
| Mirsharai 150 MW (Oil) | [25 empty] | 0 | 0
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 10 | 10 | 9 | 6 | 3 | 6 | 9 | 4 | 20 | 20 | 3 | 6 | 23 | 3 | 3 | 3 | 29 | 24 |  | 15 | 8 | 8 | 6 | 14 | 6 | 5 | 259200
| Matarbari 2*600 MW (CPGCL) | 562 | 562 | 564 | 554 | 556 | 548 | 548 | 555 | 282 | 280 | 210 | 210 | 208 | 206 | 202 | 202 | 204 | 210 |  | 210 | 210 | 208 | 210 | 210 | 210 | 208 | 8967272
120 | Eastern Zone Total | 5272 | 4790 | 4757 | 4605 | 4519 | 4260 | 4158 | 4114 | 3766 | 3636 | 3659 | 3799 | 3992 | 3362 | 2962 | 2706 | 2570 | 3555 |  | 3793 | 3950 | 4123 | 4201 | 4224 | 4204 | 4059 | 96531097
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [25 empty] | 0 | 0
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [25 empty] | 0 | 0
130 | Mongla Orion 100 MW Solar PP | [9 empty] | 1 | 2 | 4 | 10 | 8 | 7 | 4 | [10 empty] | 46800
131 | Rampal 1320 MW (BIFPCL) | 369 | 351 | 352 | 353 | 352 | 353 | 353 | 353 | 358 | 353 | 354 | 355 | 383 | 353 | 355 | 353 | 356 | 409 |  | 402 | 402 | 403 | 408 | 400 | 403 | 370 | 8865455
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 110 | 110 | 110 | 110 | 110 | 110 | 106 | 110 | 109 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 109 | 110 | 2583736
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 109 | 54 | [11 empty] | 2072700
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 100 | 80 | 80 | 72 | 72 | 72 | 72 | 72 | 52 | 60 | 54 | 60 | 52 | 52 | 30 | [10 empty] | 40 | 1044000
140 | Bhola 33 MW PP (Venture) | 12 | 16 | 10 | 7 | 5 | 4 | 4 | 5 | 6 | 6 | 5 | 9 | 6 | 1 | 1 | 1 | 1 | 1 |  | 2 | 2 | 2 | 3 | 4 | 3 | 5 | 118300
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [26 empty] | 0
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 912 | 912 | 733 | 581 | 480 | 330 | 329 | 522 | 571 | 580 | 533 | 675 | 675 | 382 | 163 | 231 | 245 | 347 |  | 343 | 343 | 278 | 333 | 344 | 344 | 344 | 11364363
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 530 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 530 | 500 | 490 | 300 | 250 | 300 |  | 430 | 450 | 460 | 490 | 490 | 480 | 450 | 12736700
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4190000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 1 | 0 | 0 | [10 empty] | 9420
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 300 | 300 | 300 | 250 | 220 | 220 | 220 | 200 | 200 | 200 | 250 | 250 | 330 | 180 | 180 | 180 | 280 | 414 |  | 330 | 370 | 414 | 370 | 370 | 300 | 300 | 6723527
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | 8 | 8 | 8 | 62064
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [26 empty] | 0
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [26 empty] | 0
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [25 empty] | 0 | 0
172 | Confidence Power Bogura Unit-1 113 MW | [25 empty] | 0 | 0
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [25 empty] | 0 | 0
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 4 | 6 | 5 | 6 | 6 | 4 | 2 | 0 | [9 empty] | 37736
178 | Energypac Power Venture Thakurgaon Ltd.
| Intraco Solar 30 MW | [6 empty] | 0 | 3 | 23 | 31 | 19 | 20 | 23 | 29 | 18 | 11 | 0 | [9 empty] | 177413
| Adani Power Jharkhanda Ltd | 904 | 852 | 829 | 814 | 825 | 829 | 823 | 827 | 832 | 833 | 814 | 816 | 814 | 812 | 830 | 803 | 805 | 802 |  | 810 | 810 | 810 | 812 | 802 | 813 | 814 | 19492731
178 | Teesta Solar Limited | [6 empty] | 2 | 29 | 115 | 128 | 185 | 183 | 175 | 168 | 63 | 26 | 2 | [9 empty] | 997000