## Daily Gen
Hourly Generation & Demand
Date | 2014-06-20
Time | Generation | Demand | Shortage | Remarks
Hour | MW | MW | MW
1:00 | 5909 | 5909 | 0
2:00 | 5545 | 5545 | 0
3:00 | 5462 | 5462 | 0
4:00 | 5129 | 5129 | 0
5:00 | 4988 | 4988 | 0
6:00 | 4405 | 4405 | 0
7:00 | 4134 | 4134 | 0
8:00 | 4109 | 4109 | 0
9:00 | 4348 | 4348 | 0
10:00 | 4425 | 4425 | 0
11:00 | 4545 | 4545 | 0
12:00 | 4564 | 4564 | 0 | Day peak
13:00 | 4698 | 4698 | 0
14:00 | 4657 | 4657 | 0
15:00 | 4882 | 4882 | 0
16:00 | 4843 | 4843 | 0
17:00 | 4713 | 4713 | 0
18:00 | 4875 | 4875 | 0
18:30 | 5068 | 5068 | 0
19:00 | 5739 | 5739 | 0
19:30 | 6201 | 6201 | 0
20:00 | 6194 | 6194 | 0
21:00 | 6207 | 6207 | 0 | Evening Peak
22:00 | 6246 | 6246 | 0
23:00 | 6209 | 6209 | 0
24:00 | 5890 | 5890 | 0

## forecast
[7 empty] | POWER GRID COMPANY OF BANGLADESH LTD. | [6 empty] | QF-LDC-07
SUMMARY OF DAILY ELECTRICITY GENERATION
|  | Month : |  | 2014-06-21 |  |  | Day : | Saturday |  |  |  | Date : | 2014-06-21
| Probable Maximum Generation : |  |  |  | (a) At Day Peak Hour : |  | 4523 | MW |  | (b) At Evening Peak Hour : |  |  | 6575 | MW
| Water Level of Kaptai Lake at 06:00 AM (ft) |  |  |  | (a) Yesterday : |  | 72.86 |  |  | (b) Today: | 75.63 | (c) Rule Curve: |  | 81.3
Sl. | Name of the Power Station |  | Fuel | Producer | Instslled Capacity |  | Derated/ | Actual Generation |  | Available Geneneration |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
[7 empty] | Present | On | 2014-06-20 | On | 2014-06-21 | for Fuel | for Plants S/D | Shut down (Date) / |  | Start up
[7 empty] | Capacity | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | or M/C prob. | Remarks |  | Date
[6 empty] | MW | MW | MW | MW | MW | MW | MW | MW
1a | Ghorasal ST 1 & 2 |  | Gas | PDB | 2X55 | 110 | 78 | 83 | 83 | 83 | 83
1b | Ghorasal ST 3 |  | Gas | PDB | 1x210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | 2014-08-05 |  | Unknown
1c | Ghorasal ST 4 |  | Gas | PDB | 1x210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | 16/6/14 |  | Unknown
1d | Ghorasal ST 5 |  | Gas | PDB | 1x210 | 210 | 190 | 170 | 170 | 170 | 170 |  | 20
1e | Ghorasal ST 6 |  | Gas | PDB | 1x210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | #6 (18/07/2010) |  | Unknown
2 | Ghorashal 100 MW |  | Gas | QRPP | 128X0.85 | 100 | 100 | 76 | 103 | 8 | 100
3 | Ghorashal 45 MW |  | Gas | QRPP | 50X0.85 | 45 | 45 | 46 | 46 | 7 | 45
4 | Ghorashal MAX |  | Gas | QRPP | 4x19.6 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Contract date expired 26/05/2014
5 | Ghorashal Regent |  | Gas | IPP | 34x3.35 |  |  | 0 | 0 | 0 | 0 |  |  | On test
6 | Haripur SBU GT 1, 2 & 3 |  | Gas | PDB | 3x32 | 96 | 60 | 0 | 0 | 0 | 0 | 40 | 20 | #1&#2(22/10/13),#3(18/6/09) |  | Unkhown
7 | Haripur EGCB 412 MW |  | Gas | EGCB | 1x273+1x139 | 412 | 412 | 389 | 386 | 437 | 412
8 | Haripur NEPC |  | HFO | IPP | 8x15 | 110 | 110 | 0 | 55 | 13 | 110
9 | Haripur P. Ltd CCPP |  | Gas | IPP | 235+125 | 360 | 360 | 349 | 353 | 353 | 353 | 7
10 | Meghnaghat P.Ltd CCPP |  | Gas | IPP | 3X150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | 21/04/2014 |  | Unknown
11 | Meghnaghat IEL |  | HFO | RPP | 12x8.9 | 100 | 100 | 14 | 91 | 7 | 91 |  | 9 | 1 Machine problem
12 | Meghnaghat Summit |  | HSD | IPP | 2x110+1x110 |  |  | 0 | 98 | 30 | 110 |  |  | GT-1 under maintenance |  | 21/06/2014
13 | Madanganj 102 MW |  | HFO | QRPP | 6x17.08 | 102 | 100 | 13 | 78 | 13 | 80 |  | 22 | 1 Machine problem
14 | Keraniganj |  | HFO | RPP | 8x14.4 | 100 | 100 | 0 | 52 | 10 | 90 |  | 48 | 1 Machine problem
15 | Narshingdi |  | Gas | SIPP,REB | 8X2.90 | 22 | 22 | 15 | 18 | 18 | 18 |  | 4 | Synchronized at 33KV, 1 Machine problem
16a | Siddhirgonj ST |  | Gas | PDB | 1x210 | 210 | 150 | 105 | 110 | 110 | 110 | 40
16b | Siddhirgonj GT-1, 2 |  | Gas | EGCB | 2x120 | 210 | 210 | 65 | 120 | 160 | 43 | 90
17 | Siddhirganj 100MW |  | HSD | QRPP | 96x1.2 | 96 | 96 | 0 | 0 | 0 | 75 |  | 96 | 22 Machine problem
18 | Dutch Bangla 100 MW |  | HFO | RPP | 12x8.9 | 100 | 100 | 8 | 57 | 8 | 100 |  | 43 | 1 Machine problem
19 | DPA Power 50MW |  | HSD | QRPP | 100X0.5 | 50 | 50 | 20 | 11 | 21 | 45 |  |  | Expired, run as per instruction of DS (Gen)
20 | Gagnagar |  | HFO | IPP | 12*9.2 |  |  | 8 | 50 | 8 | 93
21 | Summit Power (Dhaka) |  | Gas | SIPP,REB |  | 146 | 146 | 108 | 88 | 107 | 105 |  |  | Synchronized at 33KV
22 | Gazipur RPCL |  | HFO | IPP | 6x8.9 | 52 | 52 | 0 | 0 | 0 | 43 |  | 52 | 1 Machine problem
23 | Tongi GT |  | Gas | PDB | 1X 105 | 105 | 105 | 50 | 75 | 50 | 0 | 30
| Dhaka Area Total |  |  |  |  | 3894 | 3664 | 1519 | 2044 | 1613 | 2276 | 207 | 1314
24a | Chittagong Raozan ST 1 |  | Gas | PDB | 1x210 | 210 | 180 | 0 | 100 | 100 | 100 |  | 80
24b | Chittagong Raozan ST 2 |  | Gas | PDB | 1x210 | 210 | 180 | 120 | 100 | 90 | 0 | 80 |  | Gas pressure low
25 | Raozan 25 MW |  | HFO | RPCL | 3x8.9 | 25 | 25 | 0 | 26 | 0 | 26
26 | Patenga 50 MW |  | HFO | IPP | 8x6.9 | 50 | 50 | 6 | 3 | 6 | 48 |  | 47
27 | Kaptai Hydro unit 1,2,3,4 & 5 |  |  | PDB | 2X40+3X50 | 230 | 220 | 33 | 67 | 34 | 67
28a | Sikalbaha ST |  | Gas | PDB | 1X60 | 60 | 40 | 34 | 34 | 34 | 34
28b | Sikalbaha GT |  | Gas | PDB | 1x150 | 150 | 150 | 80 | 130 | 100 | 130 | 20
29 | Sikalbaha |  | HFO | RPP | 4X12.5+2X11.9+1X3+1X1.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | expired 06/05/13 but run as per instr. Of DS (gen)
30 | Hathazari |  | HFO | PDB | 11x8.9 | 98 | 98 | 0 | 78 | 0 | 80 |  | 20 | 2 Machine problem
31 | Dohazari |  | HFO | PDB | 6x17 | 102 | 102 | 0 | 87 | 0 | 102
32 | Juldah |  | HFO | RPP | 8x13.45 | 100 | 100 | 20 | 80 | 15 | 92 |  | 20
33 | Barabkunda |  | Gas | SIPP,PDB | 8X2.90 | 22 | 22 | 16 | 16 | 16 | 16 |  | 6 | Synchronized at 33KV, 2 Machine problem
34 | Malancha, Ctg EPZ |  | Gas |  |  |  |  | 28 | 16 | 14 | 20
| Chittagong area Total |  |  |  |  | 1257 | 1167 | 337 | 737 | 409 | 715 | 100 | 173
35a | Ashuganj ST 1 & 2 |  | Gas | APSCL | 2x64 | 128 | 110 | 90 | 90 | 50 | 90 |  | 20
35b | Ashuganj ST 3 |  | Gas | APSCL | 1x150 | 150 | 140 | 100 | 100 | 100 | 100 |  | 40
35c | Ashuganj ST 4 |  | Gas | APSCL | 1x150 | 150 | 150 | 140 | 140 | 140 | 140 |  | 10
35d | Ashuganj ST 5 |  | Gas | APSCL | 1x152 | 150 | 140 | 130 | 130 | 130 | 130 |  | 10
35e | Ashuganj CCPP |  | Gas | APSCL | 2x56+34 | 146 | 91 | 40 | 40 | 40 | 40 |  | 51 | #1(06/01/14) |  | Unknown
35f | Ashuganj 50 MW TSK |  | Gas | APSCL | 16x3.35 | 53 | 51 | 32 | 30 | 36 | 30 |  | 21 | 6 Machine problem
36 | Ashuganj Precision |  | Gas | RPP | 15x4 | 55 | 55 | 47 | 48 | 16 | 52
37 | Ashuganj Aggrekko |  | Gas | RPP | 82x1.1 | 80 | 80 | 70 | 79 | 68 | 80
38 | Ashuganj UP-53 MW |  | Gas | RPP | 14x4 | 53 | 53 | 0 | 0 | 0 | 0 |  | 53 | 18/06/2014 |  | 25/06/2014
39 | Ashuganj Midland |  | Gas | IPP | 6x9.34 | 51 | 51 | 18 | 46 | 48 | 46 |  | 5
40 | Brahmanbaria 70MW |  | Gas | QRPP | 72x1 | 70 | 70 | 62 | 70 | 56 | 70
41 | Daudkandi 50 MW |  | FO | PDB | 6x8.92 | 52 | 52 | 0 | 41 | 0 | 41 |  | 11 | 1 Machine problem
42 | Chandpur CCPP |  | Gas | PDB | 1x106+1x57 | 163 | 163 | 162 | 161 | 90 | 161
43 | Feni |  | Gas | SIPP,PDB | 8X2.90 | 22 | 22 | 15 | 17 | 17 | 17 |  | 5 | 2 Machine problem
44 | Mahipal,Feni |  | Gas | SIPP,REB | 4X2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Synchronized at 33KV, 1 Machine problem
45 | Jangalia |  | Gas | SIPP,PDB | 4X8.73 | 33 | 33 | 28 | 33 | 15 | 33 |  |  | Synchronized at 33KV
46 | Summit Power (Comilla) |  | Gas | SIPP,REB | 3x3.67+2x6.97 | 25 | 25 | 13 | 14 | 15 | 15 |  | 11 | Synchronized at 33KV, 3 Machine problem
| Comilla Area Total |  |  |  |  | 1392 | 1297 | 955 | 1047 | 829 | 1053 | 0 | 240
47 | RPCL CCPP, Mymensingh |  | Gas | IPP | 4X35+1x70 | 210 | 197 | 168 | 166 | 195 | 166 | 31
48 | Tangail |  | Gas | SIPP,PDB | 8X2.90 | 22 | 22 | 16 | 16 | 16 | 16 |  | 6 | Synchronized at 33KV, 2 Machine problem
| Mymensingh Area Total |  |  |  |  | 232 | 219 | 184 | 182 | 211 | 182 | 31 | 0
49a | Fenchugonj CCPP (old) |  | Gas | PDB | 2x32+1x33 | 97 | 90 | 73 | 77 | 64 | 77 |  | 13
49b | Fenchugonj CCPP (new) |  | Gas | PDB | 2x35+1x35 | 104 | 104 | 85 | 85 | 85 | 85 |  | 19
50 | Fenchugonj BEDL |  | Gas | RPP | 19X2.90 | 51 | 51 | 44 | 52 | 50 | 51
51 | Fenchuganj Prima 50 MW |  | Gas | RPP | 12x3.3+5x2 | 44 | 44 | 21 | 46 | 31 | 44
52 | Hobiganj |  | Gas | SIPP,REB | 4X2.90 | 11 | 11 | 5 | 8 | 8 | 8 |  | 3 | Synchronized at 33KV, 1 Machine problem
53 | Shahjibazar GT 8, 9 |  | Gas | PDB | 2X35 | 70 | 66 | 62 | 62 | 40 | 64
54 | Shahjibazar 86 MW |  | Gas | RPP | 32X2.90 | 86 | 86 | 45 | 85 | 81 | 85
55 | Shahjibazar 50 MW |  | Gas | RPP | 27X2.0 | 50 | 50 | 48 | 48 | 10 | 48
56 | Sylhet 150 MW |  | Gas | PDB | 1x150+1x75 | 142 | 142 | 142 | 144 | 79 | 144
57 | Sylhet GT |  | Gas | PDB | 1X20 | 20 | 20 | 20 | 19 | 0 | 20
58 | Sylhet 50MW |  | Gas | RPP | 29x1.95 | 50 | 50 | 40 | 45 | 43 | 45 |  | 5 | 2 Machine problem
59 | Shahjahanulla 25MW |  | Gas | CIPP | 3x9.34 | 25 | 25 | 8 | 16 | 8 | 16 |  | 9 | 1 Machine problem
60 | Sylhet 11 MW |  | Gas | RPP | 6X1.95 | 10 | 10 | 7 | 5 | 8 | 5 |  | 5 | 2 Machine problem
| Sylhet Area Total |  |  |  |  | 760 | 749 | 600 | 692 | 507 | 692 | 0 | 54
61 | Bheramara GT 1, 2 & 3 |  | HSD | PDB | 3X20 | 60 | 46 | 0 | 16 | 0 | 32 |  | 30 | # 2 (08/06/2014) |  | 25/06/2014
62 | Bheramara |  | HSD | RPP | 12X8.5+2X6+2X13 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | 16 Machine problem |  | Unknown
63 | HVDC C/B Interconnector |  |  | India |  | 500 | 500 | 415 | 372 | 429 | 361
64a | Khulna ST 110MW |  | FO | PDB | 1X110 | 110 | 55 | 0 | 0 | 0 | 0 |  | 55 | 15/05/2014 |  | Unknown
64b | Khulna ST 60 MW |  | FO | PDB | 1X60 | 60 | 30 | 0 | 0 | 0 | 0 |  | 30 | 24/01/2012 |  | Unknown
65 | KPCL ,Khulna. |  | HFO | IPP | 19x6.5 | 110 | 110 | 0 | 71 | 6 | 110
66 | KPCL ,Khulna.(new) |  | HFO | IPP | 7x17 | 115 | 115 | 0 | 100 | 16 | 100 |  | 15 | 1 Machine problem
67 | Faridpur |  | FO | PDB | 8x6.89 | 54 | 54 | 0 | 36 | 23 | 36 |  | 18 | 3 Machine problem
68 | Khulna 150MW |  | HSD | NWZPGCL | 1x150 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | 20/06/2014 |  | 22/06/2014
69 | Gopalganj 110 MW |  | HFO | PDB | 16x6.98 | 109 | 109 | 0 | 67 | 0 | 67 |  | 42 | 6 Machne problem
70 | Noapara (105 MW)Quantam |  | HFO | RPP | 9.9x5+9.5x6+9.2x2 | 101 | 101 | 0 | 0 | 0 | 0 |  | 101 | 13 Machine problem
71 | Noapara (40 MW),KZA |  | HFO | RPP | 5x8 | 40 | 40 | 0 | 32 | 8 | 32 |  |  | 1 Machine problem
72 | Khulna 40 MW |  | HSD | RPP | 50X0.80 |  |  | 0 | 0 | 0 | 0 |  |  | Contact date expired 16/08/13
73 | Khulna 55 MW |  | HSD | QRPP | 71X0.85 | 55 | 55 | 0 | 0 | 0 | 0 |  |  | Expired , run as per instr. of DS (Gen)
| Khulna Area Total |  |  |  |  | 1569 | 1470 | 415 | 694 | 482 | 738 | 0 | 396
74 | Barisal GT 1 & 2 |  | HSD | PDB | 2X20 | 40 | 32 | 0 | 14 | 0 | 15 |  | 18
75 | Bhola |  | Gas | RPP | 1X34.50 | 33 | 33 | 23 | 26 | 17 | 26
| Barisal Area Total |  |  |  |  | 73 | 65 | 23 | 40 | 17 | 41 | 0 | 18
76a | Baghabari GT 1 |  | Gas | SBU,PDB | 1X71 | 71 | 71 | 69 | 70 | 70 | 70
76b | Baghabari GT 2 |  | Gas | SBU,PDB | 1X100 | 100 | 100 | 95 | 92 | 80 | 92
77 | Baghabari 50 MW |  | HFO | PDB | 6x8.9 | 52 | 52 | 0 | 0 | 0 | 30 |  | 52 | 2 Machine problem
78 | Baghabari Westmont |  | Gas | IPP | 2X45 | 90 | 70 | 0 | 0 | 0 | 0 |  | 70 | #1(1/5/12),#2(24/4/13) |  | Unknown
79 | Bera 70 MW |  | HFO | PDB | 9x8.29 | 71 | 71 | 0 | 66 | 0 | 66
80 | Amnura 50 MW |  | HFO | RPP | 7x7.79 | 50 | 50 | 0 | 38 | 0 | 40 |  | 12 | 1 Machine problem
81 | Katakhali NPS 50 MW |  | HFO | RPP | 6x8.92 | 50 | 50 | 8 | 50 | 8 | 50
82 | Katakhali PPP 50 MW |  | HFO | PDB | 6x8.7 | 50 | 50 | 0 | 45 | 0 | 45
83 | Sirajganj 150 MW |  | Gas | NWPGCL | 1x150 | 150 | 150 | 137 | 135 | 80 | 140
84 | Santahar 50 MW |  | HFO | PDB | 6x8.7 | 50 | 50 | 0 | 0 | 0 | 0 |  | 50 | 20/06/2014 |  | 22/06/2014
85 | Bogra GBB |  | Gas | RPP | 6X4 | 20 | 22 | 14 | 18 | 18 | 18 |  | 4 | 1 Machine problem
86 | Bogra 20 MW |  | Gas | RPP | 5x3.3+5x2 | 20 | 20 | 16 | 18 | 17 | 18 |  |  | 1 Machine problem
87 | Summit Power (Ullapara) |  | Gas | SIPP,REB | 4X2.90 | 11 | 11 | 8 | 5 | 5 | 5 |  |  | Synchronized at 33KV
88 | Rajlanka 52 MW |  | FO | IPP | 6*8.9 | 52 | 52 | 0 | 52 | 0 | 52
| Rajshahi Area Total |  |  |  |  | 837 | 819 | 347 | 589 | 278 | 626 | 0 | 188
89a | Barapukuria ST 1 |  | Coal | PDB | 1x125 | 125 | 100 | 90 | 90 | 89 | 90 |  | 10
89b | Barapukuria ST 2 |  | Coal | PDB | 1x125 | 125 | 100 | 94 | 92 | 88 | 92 |  | 8
90 | Rangpur GT |  | HSD | PDB | 1X20 | 20 | 20 | 0 | 0 | 0 | 17 |  | 20
91 | Sayadpur GT |  | HSD | PDB | 1X20 | 20 | 20 | 0 | 0 | 0 | 18
92 | Thakurgaon |  | HSD | RPP | 20X1.5+21X1.1 | 47 | 47 | 0 | 0 | 0 | 35 |  | 47
| Rangpur Area Total |  |  |  |  | 337 | 287 | 184 | 182 | 177 | 252 | 0 | 85
| Total |  |  |  |  | 10351 | 9737 | 4564 | 6207 | 4523 | 6575 | 338 | 2468
| Useable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 3806.4536 | 5693 | 3772.2589 | 5482
A. |  | 2014-06-20 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 6246 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 4109 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 6207 | MW
3 | Day peak Generation : |  |  | 4564 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 5693 | MW
4 | Evening peak Generation : |  |  | 6207 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  |  | 121.9076 | MKWHr |  |  | 15. Area wise Demand ( S/S end), Supply( S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 93.291 | MKWHr |  | By Oil: | 13.8159 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 4.1852 | MKWHr |  | By Hydro: | 0.825 | MKWHr | Area | Demand | Supply | Loadshed | (Duration) |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Gas: | 338 | For Oil: | 0 | MW | Dhaka | 2273 | 2273 | 0 |  |  | Hour |  | MW
|  |  | For Water Shortage: |  |  | 0 | MW | Chittagong | 521 | 521 | 0 |  |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob: |  |  | 2468 | MW | Khulna | 658 | 658 | 0 |  |  | 18:30 |  | 0
7 | Total Gas Supplied : |  | 910.37 | MMCFD |  |  |  | Rajshahi | 571 | 571 | 0 |  |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 76066324.827 | ii) Oil : Taka |  | 167885061.849 | Comilla | 485 | 485 | 0 |  |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 16288650.504 | Total | Taka | 260240037.18 | Mymensingh | 335 | 335 | 0 |  |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 7.8675 | MKWHr. | Sylhet | 324 | 324 | 0 |  |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -400 | MW at | 21:00 | hrs | Barisal | 146 | 146 | 0 |  |  | 22:00 |  | 0
| iii) Maximum : |  |  | -240 | MW at | 9:00 | hrs | Rangpur | 380 | 380 | 0 |  |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 29.8° C |  |  | Total | 5693 | 5693 | 0
B. |  | 2014-06-21 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 29.0° C
Forecast
1 | Maximum Demand (Generation end) |  |  |  | 6550 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 6575 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Shortage (Generation end) |  |  |  | -25 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
4 | Total Energy Generation |  |  |  | 122 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
5 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 4075 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 9.7905 | MKWHr.
ii) During peak Demand : |  |  | 415 | MW at | 21:00 | hrs
iii) Maximum : |  |  | 440 | MW at | 7:00 | hrs
Cost for HVDC energy is not usaually included in the total fuel cost.

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2014-06-21
Till now the maximum generation is : - |  |  | 7356 MW | 20:00 | Hrs on | 2014-03-30
The Summary of Yesterday's ( |  | 2014-06-20 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 4564 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 4075 | MW
Evening Peak Generation : |  | 6207 | MW Hour : | 21:00 | Max Generation : |  | 6575 | MW
E.P. Demand (at gen end) : |  | 6207 | MW Hour : | 21:00 | Max Demand : |  | 6550 | MW
Maximum Generation : |  | 6246 | MW Hour : | 22:00 | Shortage : |  | -25 | MW
Total Gen. (MKWH) : |  | 121.9076 | System L/ Factor : | 78.37% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -240 | MW at | 9:00 | Energy | 7.8675 | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2014-06-21
Actual : | 87.64 | Ft.(MSL) , | Rule curve : | 81.3 | Ft.( MSL )
Gas Consumed : | Total | 910.37 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : Gas : |  |  | 76066324.827
|  | Coal : | 16288650.504 | Oil : | 167885061.849 | Total : | 260240037.18
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand(s/s end) |  | Estimated Shedding (s/s end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | - | 0:00 | 2202 |  |  | - | -
Chittagong Area | - | 0:00 | 561 |  |  | - | -
Khulna Area | - | 0:00 | 611 |  |  | - | -
Rajshahi Area | - | 0:00 | 597 |  |  | - | -
Comilla Area | - | 0:00 | 412 |  |  | - | -
Mymensingh Area | - | 0:00 | 344 |  |  | - | -
Sylhet Area | - | 0:00 | 280 |  |  | - | -
Barisal Area | - | 0:00 | 124 |  |  | - | -
Rangpur Area | - | 0:00 | 351 |  |  | - | -
-
Total | 0 |  | 5482 |  |  | 0
Information of the Generating machines under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
| 1) Haripur SBU GT-3 (18/06/09) |  |  | 1) Ghorasal #6 (18/07/10) |  | 9) Khulna 110 MW (15/05/2014)
|  |  |  | 2) Khulna-60MW (24/1/12) |  | 10) Ghorasal #4(16/6/2014)
|  |  |  | 3) Shahjibazar #5 & 6 (21/7/11) |  | 11) Santahar 50 MW (20/06/2014)
|  |  |  | 4) WMPL #1(1/5/12) |  | 12) Khulna 150 MW (20/06/2014)
5) WMPL #2(24/4/13)
6) Ashuganj GT-1(CCPP) (06/01/14)
7) Meghnaghat 450MW (21/04/2014)
8) Ghorasal #3 (08/05/2014)
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
| Description |  |  | Forced load shaded / Interrupted Areas
a) Tongi-Aminbazar 230 kV Ckt-2 was under shut down from 10:32 to 18:55 due to project work .
b) Aminbazar 230 kV Bus-1 was shut down at 11:06 due to project work .
c) Mirpur-Tongi 132 kV Ckt was under shut down from 11:28 to 17:49 due to project work.
d) Mirpur-Ullon 132 kV Ckt was under shut down from 11:28 to 17:48 due to project work.
e) After maintenance Raozan #1 synchronized at 17:18.
f) After maintenance Comilla (S) 132/33 kV T2 transformer was switched on at 14:04.
g) Sylhet S/S 132/33 kV T1 & T2 transformers were under shut down from 20:24 to 20:44 due to 33/11 kV
transformer maintenance work.
h) Saidpur-Purbasadipur 132 kV Ckt-2 tripped at 04:41 (21/06/2014) due to R-Phase Lightning arrester
burst at Purbasadipur end.
i) Bottail-Jhenida 132 kV Ckt-2 tripped at 04:55 (21/06/2014) showing dist.relay at Jhenida end.

## P2
POWER GRID COMPANY OF BANGLADESH LTD.
Description of the generation of various Power Stations
| Date : | 2014-06-20 | [6 empty] | Page -2
[5 empty] | Present | Peak Hour | Energy
| Name of Power Station |  | Unit | Producer | Generation | Generation | Generated |  | Remarks
Capacity
[5 empty] | MW | MW | KWHr
1 |  |  | 1 | PDB | 48 | 50 | 1960000
2 | Ghorasal Power Station |  | 2 | PDB | 30 | 33
3 |  |  | 3 | PDB | 180 | 0 | 0 | Under maint.on 08/05/14
4 |  |  | 4 | PDB | 180 | 0 | 0 | Under maint.
5 |  |  | 5 | PDB | 190 | 170 | 3969000
6 |  |  | 6 | PDB | 190 | 0 | 0 | Under maint.on 18/07/10.
7 | Ghorashal 100MW QRPP |  | 128x0.85 | QRPP 3yrs | 100 | 103 | 1837270
8 | Ghorashal 45MW QRPP |  | 50x0.85 | QRPP 3yrs | 45 | 46 | 881070
9 | Ghorashal 78 MW MAX |  | 4x19.6 | RPP | 78 | 0 | 0 | Contact Date Expired
| Ghorashal Regent |  |  |  | 0 | 0 | 0 | On test
10 |  |  | GT-1 | SBU, PDB | 20 | 0 | 0 | Gas pressure low
11 | Haripur SBU |  | GT-2 | SBU, PDB | 20 | 0 | 0 | Gas pressure low
12 |  |  | GT-3 | SBU, PDB | 20 | 0 | 0 | Under maint. since 18/06/09
| Haripur EGCB 360 MW |  |  | EGCB | 412 | 386 | 10062100
13 | Haripur NEPC |  | 7 x 15.5 | IPP | 110 | 55 | 612400 | Low demand
14 | Haripur Power Ltd |  | CCPP | IPP | 360 | 353 | 8305000
15 | Meghnaghat Power Ltd |  | CCPP | IPP | 450 | 0 | 0 | under maint since 21/04/2014
16 | Meghnaghat IEL |  | 12x8.9 | 100 | 100 | 91 | 1121280 | Machine problem
| Meghnaghat Summit |  |  |  | 0 | 98 | 1456611 | On test
17 | Madanganj |  | 6x17.08 | QRPP 3yrs | 100 | 78 | 1108660 | Machine problem
18 | Keraniganj |  |  | RPP | 100 | 52 | 633985 | Low demand
19 | Narsingdi (REB) |  | 8 x 2.9 | SIPP, REB | 22 | 18 | 350172 | Synchronized at 33KV, Machine problem
20 | Siddhirgonj Power Station |  | 210MW | PDB | 150 | 110 | 2548350 | Gas pressure low
21 |  |  | GT1 & GT-2 | EGCB | 210 | 120 | 2612000 | Gas pressure low
22 | Siddhirgonj |  | 96x1.2 | QRPP 3yrs | 96 | 0 | 96960 | No demand
23 | Dutch-Bangla 100 MW |  | 12x8.9 | RPP | 100 | 57 | 822720 | Low demand
24 | DPA Power QRPP |  | 100x0.5 | QRPP 3yrs | 50 | 11 | 454800 | Contact expired, run as per instruction of DS (Gen)
| Gaharnagar |  |  |  | 0 | 50 | 620208
25 | Summit Power Ltd (Dhaka) |  |  | SIPP, REB | 146 | 88 | 2543066 | Synchronized at 33KV, Machine problem
26 | Gazipur RPCL |  | 6x8.9 | IPP | 52 | 0 | 56640 | No demand
27 | Tongi Power Station |  | 1 | PDB | 105 | 75 | 1604348 | Gas pressure low
| Dhaka Area Total |  |  |  | 3664 | 2044 | 43656640
28 | Chitagong Power Station |  | 1 | PDB | 180 | 100 | 400000 | under maint.
29 |  |  | 2 | PDB | 180 | 100 | 2800000 | Gas pressure low
30 | Raozan 25 MW |  |  | RPCL | 25 | 26 | 187020
31 | Patenga 50 MW |  |  | IPP | 0 | 3 | 362400 | Machine problem
32 |  |  | 1 | PDB | 30 | 30 | 825000
33 |  |  | 2 | PDB | 40 | 37 | 0
34 | Karnafuli Hydro Power Station |  | 3 | PDB | 50 | 0 | 0
35 |  |  | 4 | PDB | 50 | 0 | 0
36 |  |  | 5 | PDB | 50 | 0 | 0
37 | Shikalbaha Power station |  | Steam | PDB | 40 | 34 | 749200
38 |  |  | GT | PDB | 150 | 130 | 2292930 | Gas pressure low
39 | Hathazari |  | 11x8.9 | PDB | 100 | 78 | 398432 | Machine problem
40 | Dohazari |  | 6x17 | PDB | 100 | 87 | 524941 | Low demand
41 | Juldah |  | 8x13.45 | RPP | 100 | 80 | 1265520 | Machine problem
42 | Shikalbaha RPP |  | 4x12.5+2x11.9+1x3 | RPP 3yrs | 0 | 0 | 0 | Contact expired date (06/05/2013)
43 | Barabkunda RPP |  | 8x2.90 | SIPP, PDB | 22 | 16 | 362880 | Synchronized at 33KV, Machine problem
| Malancha, Ctg EPZ |  |  |  |  | 16 | 543840 | Synchronized at 33KV
44 | Chittagong Area Total |  |  |  | 1117 | 737 | 10712163
45 |  |  | 1 | APSCL | 55 | 40 | 2162199
46 |  |  | 2 | APSCL | 55 | 50 | 0
47 | Ashugonj Power Station |  | 3 | APSCL | 140 | 100 | 2422070 | Machine problem
48 |  |  | 4 | APSCL | 150 | 140 | 3304930 | Machine problem
49 |  |  | 5 | APSCL | 140 | 130 | 3115598 | Machine problem
50 |  |  | GT-1 | APSCL | 35 | 0 | 0 | Under maint.
51 |  |  | GT-2 | APSCL | 40 | 40 | 976148
52 |  |  | ST. | APSCL | 16 | 0 | 0 | Under maint. Since 08/09/13
53 | Ashuganj-50 MW |  | 16x3.35 | APSCL | 51 | 30 | 783720 | Machine problem
54 | Ashugonj RPP |  | 15x4 | RPP 3yrs | 55 | 48 | 936000
55 | Ashuganj Aggekko |  | 82x1.1 | RPP | 80 | 79 | 1507270
| Ashuganj United Power |  | 14x4 | RPP | 53 | 0 | 0 | Under maint.
56 | Ashuganj Midland Power |  |  |  | 51 | 46 | 875044 | Machine problem
57 | Brahmanbaria |  | 72x1 | QRPP 3yrs | 70 | 70 | 1305000
58 | Daudkandi 50 MW |  | 6 x 8.92 | PDB | 52 | 41 | 279092 | Machine problem
59 | Chandpur CCPP |  | 1x106+1x57 | PDB | 163 | 161 | 3634800
60 | Feni SIPP |  | 8 X 2.94 | SIPP, PDB | 22 | 17 | 359856 | Machine problem
61 | Feni (Mohipal) |  | 4x2.9 | SIPP, REB | 11 | 8 | 189000 | Synchronized at 33KV, Machine problem
62 | Jangalia RPP |  | 4x8.73 | SIPP, PDB | 33 | 33 | 777800
| Comilla Summit Power |  |  | SIPP, REB | 25 | 14 | 379680 | Machine problem
63 | Comilla Area Total |  |  |  | 1297 | 1047 | 23008207
64 | RPCL, Mymensingh CCPP |  | GT1-4 | IPP | 197 | 166 | 4168000 | Gas pressure low
| Tangail SIPP |  | 8 x 2.50 | SIPP,PDB | 22 | 16 | 356436 | Synchronized at 33KV, Machine problem
65 | Mymensingh Area Total |  |  |  | 219 | 182 | 4524436
66 | Fenchugonj Comb. Cycle |  | GT-1, 2 & St | PDB | 90 | 77 | 1686000 | Machine problem
67 |  |  | GT-3,4 & St | PDB | 104 | 85 | 2044440 | Machine problem
68 | Fenchugonj RPP (51 MW) |  | 2.9X19 | RPP 15yrs | 51 | 52 | 945600
69 | Fenchuganj Prima 50 MW |  | 12x3.3+5x2 | RPP | 44 | 46 | 1090000
70 | Hobiganj (REB) (11MW) |  | 4x2.9 | SIPP, REB | 11 | 8 | 176640 | Synchronized at 33 kV, Machine problem
71 | Shahjibazar Power Station |  | 5,6 | PDB | 0 | 0 | 0 | Under maint.
72 |  |  | 8,9 | PDB | 66 | 62 | 1156000
73 | Shahjibazar P. co (SPCL) |  | 32X2.88 | RPP 15yrs | 86 | 85 | 1556160
74 | Shahjibazar RPP |  | 1.85X27 | RPP 15yrs | 50 | 48 | 817560
75 | Sylhet 150 MW |  | 1x100+1x50 | PDB | 142 | 144 | 2861120
76 | Sylhet Power Station |  | GT | PDB | 20 | 19 | 443000
| Sylhet 50 MW RPP |  | 27 x 1.95 | RPP 3yrs | 50 | 45 | 766360 | Machine problem
77 | Shahjahanulla 25MW |  | 3 x 9.34 |  | 25 | 16 | 300552 | Machine problem
| Sylhet 11 MW RPP |  | 6x1.95 | RPP 15yrs | 10 | 5 | 167400 | Synchronized at 33KV, Machine problem
78 | Sylhet Area Total |  |  |  | 749 | 692 | 14010832
79 |  |  | GT-1 | PDB | 16 | 0 | 0 | No demand
80 | Bheramara Power Station |  | GT-2 | PDB | 14 | 0 | 131800 | Under maint.
81 |  |  | GT-3 | PDB | 16 | 16 | 0
| Bheramara 110 MW |  | 12x8.5+2x6+2x13 | RPP 3yrs | 105 | 0 | 0 | Machine problem
82 | HVDC C/B Interconnector |  | India |  | 500 | 372 | 9790545
83 | Khulna Power Station |  | 110MW | PDB | 55 | 0 | 0 | Under maint.
84 |  |  | 60MW | PDB | 30 | 0 | 0 | Under S/D Since 24/1/12
85 | Khulna Power Co Ltd. |  | 19x6.5 | IPP | 110 | 71 | 333400
86 | KPCL ,Khulna.(New) |  | 7x17 | IPP | 115 | 100 | 466563 | Machine problem
| Faridpur |  | 8x6.89 | PDB | 54 | 36 | 383080 | Machine problem
87 | Khulna 150 MW |  | 1x150 |  | 150 | 0 | 0 | No demand
88 | Gopalganj 110 MW |  | 16x6.98 | PDB | 109 | 67 | 385600 | Low demand
89 | Noapara (105 MW),Quantam |  | 9.9x5+9.5x6+9.2x2 | RPP | 101 | 0 | 0 | Machine problem
90 | Noapara (40 MW),KZA |  | 5x8 | RPP | 40 | 32 | 172875 | Synchronized at 33KV
91 | Khulna RPP 40MW |  | 50X0.80 | RPP 3yrs | 40 | 0 | 0 | Contact Date Expired
| Khulna RPP 55MW |  | 71X0.85 | QRPP 3yrs | 55 | 0 | 25521 | expired , run as per instr. of DS (Gen)
94 | Khulna Area Total |  |  |  | 1510 | 694 | 11689384
95 | Barisal Power Station |  | GT-1 | PDB | 16 | 0 | 0 | Under maint
96 |  |  | GT-2 | PDB | 16 | 14 | 98690
| Bhola RPP |  | 34.5 | RPP 3yrs | 33 | 26 | 533400 | Synchronized at 33KV
97 | Barisal Area Total |  |  |  | 65 | 40 | 632090
98 | Baghabari Power Station |  | 71 MW | SBU, PDB | 71 | 70 | 1600000
99 |  |  | 100 MW | SBU, PDB | 100 | 92 | 2186000 | Machine problem
100 | Baghabari 50 MW |  | 6x8.9 | PDB | 52 | 0 | 60276 | No demand
101 | Baghabari West Mont (WMPL) |  | GT 1 & 2 | IPP | 70 | 0 | 0 | #1 Under S/D since 1/5/12,#2 Under S/D since 25/4/13
102 | Bera 70 MW |  | 9x8.29 | PDB | 71 | 66 | 496742 | Machine problem
103 | Amnura 50 MW |  | 7x7.79 | RPP | 50 | 38 | 270060 | Machine problem
104 | Katakhali NPS 50 MW |  |  | RPP | 50 | 50 | 406547
105 | Rajshahi PPP 50 MW |  | 6x8.7 | PDB | 50 | 45 | 219235 | Machine problem
106 | Sirajganj 150 MW |  | 1x150 | NWPGCL | 150 | 135 | 2862700
107 | Santahar 50 MW |  | 6x8.7 | PDB | 50 | 0 | 0 | Under maintenance
108 | Bogra RPP |  | 6x4 | RPP 15yrs | 22 | 18 | 399000 | Machine problem
109 | Bogra prima |  | 5x3.3+5x2 | RPP 3yrs | 20 | 18 | 423540
110 | Ullapara Summit |  | 4 X 2.90 | SIPP, REB | 11 | 5 | 200750 | Synchronized at 33KV, Machine problem
| Rajlanka 52 MW |  |  | IPP | 52 | 52 | 363840
| Rajshahi Area Total |  |  |  | 819 | 589 | 9488690
111 | Barapukuria power station |  | ST 1 | PDB | 100 | 90 | 2067490 | Machine problem
112 | Barapukuria power station |  | ST 2 | PDB | 100 | 92 | 2117672 | Machine problem
113 | Rangpur Power Station |  | GT | PDB | 20 | 0 | 0 | No demand
114 | Saidpur Power Station |  | GT | PDB | 20 | 0 | 0 | No demand
115 | Thakurgaon Rental |  | 20x1.5+21x1.1 | RPP 3yrs | 47 | 0 | 0 | Expired, but run as per instruction of DS (Gen)
| Rangpur Area Total |  |  |  | 287 | 182 | 4185162
| Eastern Grid Total |  |  |  | 7046 | 4702 | 95912278
| Western Grid Total |  |  |  | 2681 | 1505 | 25995326
| National Grid Total |  |  |  | 9727 | 6207 | 121907604
* Data collected from respective power station over telephone.

## P3
| POWER GRID COMPANY OF BANGLADESH LTD. | [6 empty] | QF-LDC-09
NATIONAL LOAD DESPATCH CENTER
PEAK HOUR DEMAND (AT S/S END) OF DIFFERENT AREAS
Date: | 2014-06-20
(a) ENTIRE EASTERN GRID : |  |  | 3938 | MW | (b) ENTIRE WESTERN GRID : |  |  | 1755 | MW
i) Dhaka area |  |  | 2273 | MW | i) Khulna area |  |  | 658 | MW
ii) Chittagong area |  |  | 521 | MW | ii) Rajshahi area |  |  | 571 | MW
iii) Comilla area |  |  | 485 | MW | iii) Barisal area |  |  | 146 | MW
iv) Mymensingh area |  |  | 335 | MW | iv) Rangpur area |  |  | 380 | MW
v) Sylhet area |  |  | 324 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 5693 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUBSTATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 102 | 100 | Kishorganj | 48 | 2100 | Jessore | 92 | 1930
Munsiganj | 72 | 100 | Netrokona | 38 | 2100 | Jhenida | 50 | 1930
Megnaghat | 22 | 2000 | Jamalpur | 97 | 1930 | Bottail | 56 | 100
Shyampur | 131 | 2400 | Srimongal | 31 | 2100 | G.K Project | 30 | 100
Bhulta | 111 | 100 | Shahjibazar | 44 | 2100 | Faridpur | 73 | 2200
Madanganj | 30 | 2100 | Fenchuganj | 46 | 2200 | Madaripur | 74 | 2100
Shitalakhya | 76 | 100 | Sylhet | 118 | 2100 | Gopalganj | 32.8 | 2000
Rahim steel | 5 | 1100 | Chatak | 31 | 2300 | Bagerhat | 46 | 1900
Matuail | 37 | 100 | B.Baria | 66 | 1930 | Mongla | 23 | 100
Ghorasal | 70 | 2300 | Comilla(S) | 131 | 2100 | Satkhira | 49 | 2100
Narsingdi | 61 | 2100 | Comilla(N) | 34 | 1800 | Gallamari | 32.2 | 1300
Haripur (SBU) | 49 | 2300 | Chandpur | 71 | 2000 | Magura | 23 | 1930
Ullon | 27 | 2000 | Feni | 71 | 2100 | Chuadanga | 35 | 500
Hasnabad | 144 | 100 | Chowmuhani | 106 | 2100 | Barisal | 76 | 2000
Magbazar | 108 | 2000 | Ashuganj | 39 | 2100 | Patuakhali | 46.5 | 2100
Maniknagar | 80 | 2000 | Daudkandi | 39 | 2000 | Bhandaria | 25 | 2000
Bangabhaban | 18 | 2000 | Madanhat | 36 | 100 | Ishurdi | 31 | 100
Narinda | 70 | 2100 | Hathazari | 74 | 1900 | Natore | 60 | 1930
Dhanmondi | 78 | 1600 | Khulshi | 105 | 100 | Bogra | 134 | 2000
Agargaon | 12 | 2100 | Halishahar | 98 | 1900 | Noagaon | 68 | 1930
Mirpur | 84.5 | 1930 | Baraulia | 63 | 800 | Rajshahi | 85 | 2100
Kalyanpur | 138 | 1930 | Sikalbaha | 28 | 1930 | C.Nawabganj | 57 | 2100
Gulshan | 92.4 | 1930 | Dohazari | 46 | 2200 | Pabna | 56 | 1930
Uttara | 73.3 | 2000 | Cox'sbazar | 47 | 2200 | Shahjadpur | 42 | 1930
Kamrangirchar | 70 | 2000 | Chandraghona | 24.8 | 2000 | Serajganj | 37 | 100
Savar | 74 | 2100 | Kaptai | 3 | 1930 | Niyamatpur | 30 | 2000
Bhasantec | 66 | 1930 | A. Khaer Stl. | 9 | 200 | Joypurhat | 25 | 2000
Tongi | 62 | 1900 | Bakulia | 78 | 2000 | Rangpur | 78 | 2100
Kabirpur | 125 | 1930 | Julda | 18 | 100 | Lalmonirhat | 43 | 2100
Basundhara | 90 | 1900 | TK chemical | 11.2 | 500 | Saidpur | 61 | 1930
Manikganj | 60 | 2200 | Modern Steel | 9 | 400 | Purbasadipur | 59 | 2000
Joydevpur | 171 | 100 | Shahmirpur | 0.8 | 100 | Thakurgaon | 53 | 2000
New Tongi | 80 | 1000 | Goalpara | 14 | 2100 | Palashbari | 44 | 930
Tangail | 102 | 1930 | Central s/s | 69 | 1930 | Barapukuria | 28 | 2100
Mymensing | 114 | 2000 | Noapara | 38.4 | 2000 | Panchagar | 16 | 1930
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## L.curve
Date | 2014-06-20 | [8 empty] | QF-LDC-11
TIME | E-W INT. | EAST GRID | WEST GRID | TOTAL |  | Demand | Hour
0:00 | -820 | 4926 | 1327 | 6253 | -820 | 6253 | 0:00 | DAILY LOAD CURVE | 2014-06-20
0:30 | -630 | 4834.5 | 1246.5 | 6081 | -440 | 6081 | 1:00
1:00 | -440 | 4743 | 1166 | 5909 | -440 | 5909 | 2:00
1:30 | -440 | 4611.5 | 1115.5 | 5727 | -440 | 5727 | 3:00
2:00 | -440 | 4480 | 1065 | 5545 | -430 | 5545 | 4:00
2:30 | -440 | 4436 | 1067.5 | 5503.5 | -390 | 5503.5 | 5:00
3:00 | -440 | 4392 | 1070 | 5462 | -360 | 5462 | 6:00
3:30 | -435 | 4261 | 1034.5 | 5295.5 | -280 | 5295.5 | 7:00
4:00 | -430 | 4130 | 999 | 5129 | -280 | 5129 | 8:00
4:30 | -410 | 4074 | 984.5 | 5058.5 | -240 | 5058.5 | 9:00
5:00 | -390 | 4018 | 970 | 4988 | -280 | 4988 | 10:00
5:30 | -375 | 3748 | 948.5 | 4696.5 | -300 | 4696.5 | 11:00
6:00 | -360 | 3478 | 927 | 4405 | -300 | 4405 | 12:00
6:30 | -320 | 3343 | 926.5 | 4269.5 | -340 | 4269.5 | 13:00
7:00 | -280 | 3208 | 926 | 4134 | -340 | 4134 | 14:00
7:30 | -280 | 3193.5 | 928 | 4121.5 | -310 | 4121.5 | 15:00
8:00 | -280 | 3179 | 930 | 4109 | -310 | 4109 | 16:00
8:30 | -260 | 3275.5 | 953 | 4228.5 | -300 | 4228.5 | 17:00
9:00 | -240 | 3372 | 976 | 4348 | -280 | 4348 | 18:00
9:30 | -260 | 3426 | 960.5 | 4386.5 | -270 | 4386.5 | 18:30
10:00 | -280 | 3480 | 945 | 4425 | -280 | 4425 | 19:00
10:30 | -290 | 3543.5 | 941.5 | 4485 | -400 | 4485 | 19:30
11:00 | -300 | 3607 | 938 | 4545 | -410 | 4545 | 20:00
11:30 | -300 | 3601 | 953.5 | 4554.5 | -400 | 4554.5 | 21:00
12:00 | -300 | 3595 | 969 | 4564 | -360 | 4564 | 22:00
12:30 | -320 | 3668.5 | 962.5 | 4631 | -390 | 4631 | 23:00
13:00 | -340 | 3742 | 956 | 4698 | -440 | 4698 | 24:00
13:30 | -340 | 3743 | 934.5 | 4677.5 |  | 4677.5
14:00 | -340 | 3744 | 913 | 4657 | 128.92 | 4657
14:30 | -325 | 3820.5 | 949 | 4769.5 | 86.5 | 4769.5
15:00 | -310 | 3897 | 985 | 4882 |  | 4882
15:30 | -310 | 3885 | 977.5 | 4862.5 | 7867500 | 4862.5
16:00 | -310 | 3873 | 970 | 4843 |  | 4843
16:30 | -305 | 3825 | 953 | 4778 |  | 4778
17:00 | -300 | 3777 | 936 | 4713 | 700 | 4713
17:30 | -300 | 3777 | 987.5 | 4764.5 | 1800 | 4764.5
18:00 | -300 | 3777 | 1039 | 4816 | 100 | 4816
18:30 | -270 | 3934 | 1134 | 5068 | 1400 | 5068
19:00 | -280 | 4386 | 1353 | 5739 | 100 | 5739
19:30 | -400 | 4713 | 1488 | 6201 | 1800 | 6201
20:00 | -410 | 4706 | 1488 | 6194 | 1800 | 6194
20:30 | -405 | 4704 | 1496.5 | 6200.5 | 1800 | 6200.5
21:00 | -400 | 4702 | 1505 | 6207 | 2100 | 6207
21:30 | -380 | 4737.5 | 1489 | 6226.5 | 1900 | 6226.5
22:00 | -360 | 4773 | 1473 | 6246 | 1900 | 6246
22:30 | -375 | 4810 | 1417.5 | 6227.5 |  | 6227.5
23:00 | -390 | 4847 | 1362 | 6209 |  | 6209
23:30 | -415 | 4780 | 1269.5 | 6049.5 |  | 6049.5
24:00 | -440 | 4713 | 1177 | 5890 |  | 5890
*MAX.GEN.(E.P.) |  | 6246 |  | 0.91667
*MAX.GEN.(D.P.) |  | 4564 |  | 0.5
|  |  |  | min | max
|  | 3063.9 | 3349 | 0.33333 | 0.041667
|  | 2664.1 | 3286.1 | 0.54167 | 0.45833
|  | 2910.2 | 3139.4 | 0.77083 | 24:00
|  | 2664.1 | 3349 | 0.54167 | 0.041667
|  | 282 |  | 0.16667
|  | 276 |  | 0.75
|  | 348 |  | 0.875
|  | 348 |  | 0.875
| Deputy Manager |  |  | Manager |  |  | Deputy General Manager
| Load Despatch Division |  |  | Load Despatch Division |  |  | Load Despatch Circle
NATIONAL LOAD DESPATCH CENTER
3595 MW (09:00 )
4008 MW(05:00 )
.4MW (19:30)
6207MW (21:00)
4564 MW (12:00)

## En.Curve
QF-LDC-12
Date | 2014-06-20 |  | Energy | 121907604
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE |  | DAILY ENERGY CURVE |  | 2014-06-20
0:00 | 1377 | 356 | 2706 | 1226 | 183 | 36 | 368 | 0
0:30 | 1384 | 390.5 | 2710.5 | 1138.5 | 183.5 | 36.5 | 237.5 | 0
1:00 | 1391 | 425 | 2715 | 1051 | 184 | 37 | 107 | 0
1:30 | 1429.5 | 425 | 2752.5 | 871 | 184 | 37 | 57.5 | 0 | [5 empty] | 121.9076
2:00 | 1468 | 425 | 2790 | 691 | 184 | 37 | 8 | 0 | [5 empty] | 2.5704
2:30 | 1491.5 | 430.5 | 2831 | 583.5 | 183 | 37.5 | 8 | 0 | [5 empty] | 124.478
3:00 | 1515 | 436 | 2872 | 476 | 182 | 38 | 8 | 0
3:30 | 1472.5 | 436 | 2844 | 391 | 181.5 | 38 | 8 | 0
4:00 | 1430 | 436 | 2816 | 306 | 181 | 38 | 8 | 0
4:30 | 1412 | 436 | 2806 | 255 | 179.5 | 37.5 | 8 | 0
5:00 | 1394 | 436 | 2796 | 204 | 178 | 37 | 8 | 0
5:30 | 1375.5 | 437.5 | 2583 | 152 | 175.5 | 36.5 | 4 | 0
6:00 | 1357 | 439 | 2370 | 100 | 173 | 36 | 0 | 0
6:30 | 1348.5 | 438.5 | 2250 | 93.5 | 173.5 | 35 | 0 | 0
7:00 | 1340 | 438 | 2130 | 87 | 174 | 34 | 0 | 0
7:30 | 1341 | 438.5 | 2125.5 | 87 | 175 | 33 | 0 | 0
8:00 | 1342 | 439 | 2121 | 87 | 176 | 32 | 0 | 0
8:30 | 1375.5 | 439.5 | 2176.5 | 117 | 175 | 32 | 0 | 0
9:00 | 1409 | 440 | 2232 | 147 | 174 | 32 | 0 | 0
9:30 | 1397.5 | 440 | 2214 | 213 | 174.5 | 33.5 | 0 | 0
10:00 | 1386 | 440 | 2196 | 279 | 175 | 35 | 0 | 0
10:30 | 1356.5 | 440 | 2278 | 288.5 | 175 | 33.5 | 0 | 0
11:00 | 1327 | 440 | 2360 | 298 | 175 | 32 | 0 | 0
11:30 | 1376 | 427.5 | 2427 | 197.5 | 179.5 | 32.5 | 0 | 0
12:00 | 1425 | 415 | 2494 | 97 | 184 | 33 | 0 | 0
12:30 | 1390 | 415.5 | 2539.5 | 155.5 | 182.5 | 31.5 | 0 | 0
13:00 | 1355 | 416 | 2585 | 214 | 181 | 30 | 0 | 0
13:30 | 1353.5 | 415.5 | 2560.5 | 220 | 179.5 | 32.5 | 0 | 0
14:00 | 1352 | 415 | 2536 | 226 | 178 | 35 | 0 | 0
14:30 | 1379.5 | 415.5 | 2572.5 | 270.5 | 181 | 35.5 | 2.5 | 0
15:00 | 1407 | 416 | 2609 | 315 | 184 | 36 | 5 | 0
15:30 | 1403.5 | 416 | 2624.5 | 284.5 | 181.5 | 37 | 2.5 | 0 | Max Temp. in Dhaka |  | 29.8° C
16:00 | 1400 | 416 | 2640 | 254 | 179 | 38 | 0 | 0
16:30 | 1393 | 416 | 2578 | 253 | 179.5 | 38 | 4.5 | 0
17:00 | 1386 | 416 | 2516 | 252 | 180 | 38 | 9 | 0
17:30 | 1411.5 | 416 | 2510 | 273 | 182 | 38.5 | 48 | 0
18:00 | 1437 | 416 | 2504 | 294 | 184 | 39 | 87 | 0
18:30 | 1441 | 368 | 2494 | 435 | 180 | 39 | 201 | 0
19:00 | 1519 | 369 | 2604 | 725 | 179 | 39 | 381 | 0
19:30 | 1547 | 368 | 2790 | 984 | 176 | 37 | 416 | 0
20:00 | 1566 | 367 | 2813 | 944 | 178 | 61 | 421 | 0
20:30 | 1580 | 369.5 | 2793.5 | 944 | 180 | 64 | 418.5 | 0
21:00 | 1594 | 372 | 2774 | 944 | 182 | 67 | 416 | 0
21:30 | 1589.5 | 372 | 2802.5 | 965 | 182.5 | 51.5 | 411.5 | 0
22:00 | 1585 | 372 | 2831 | 986 | 183 | 36 | 407 | 0
22:30 | 1595.5 | 372 | 2833 | 939.5 | 181.5 | 36.5 | 417 | 0
23:00 | 1606 | 372 | 2835 | 893 | 180 | 37 | 427 | 0
23:30 | 1602 | 372 | 2839.5 | 866 | 181 | 38 | 292.5 | 0
24:00 | 1598 | 372 | 2844 | 839 | 182 | 39 | 158 | 0
|  | 1490 |  |  |  |  | 2380 | 0
|  | Deputy / Asstt. Manager |  |  | Manager
|  | Load Despatch Division |  |  | Load Despatch Division
NATIONAL LOAD DESPATCH CENTER

## volt
NATIONAL LOAD DESPATCH CENTER
The Maximum & Minimum Voltages of different Sub-Stations.
Date : | 2014-06-20
| Maxm |  | Minm |  |  | Maxm |  | Minm
Substation | Voltage | Hour | Voltage | Hour | Substation | Voltage | Hour | Voltage | Hour
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Hathazari | 220 | 600 | 214 | 100 | Megnaghat | 210 | 100 | 204 | 1100
Comilla(N) | 225 | 600 | 219 | 1300 | Haripur | 211 | 700 | 205 | 1700
Ashuganj | 227 | 200 | 224 | 1200 | Ishurdi | 235 | 600 | 223 | 1200
Ghorasal | 222 | 200 | 218 | 1200 | Baghabari | 226 | 1800 | 220 | 200
Rampura | 212 | 500 | 206 | 1200 | Serajganj | 226 | 600 | 219 | 100
Tongi | 211 | 700 | 203 | 1200 | Bogra | 229 | 1400 | 223 | 400
Aminbazar | 210 | 500 | 200 | 1500 | Barapukuria | 229 | 1300 | 223 | 2100
Hasnabad | 228 | 700 | 220 | 1200 | Khulna South | 231 | 600 | 209 | 100
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 135 | 100 | 130 | 1200 | Khulshi | 135 | 2000 | 131 | 1500
Munsiganj | 132 | 100 | 127 | 1200 | Halishahar | 132 | 500 | 127 | 1200
Megnaghat | 133 | 400 | 130 | 1200 | Baraulia | 129 | 1930 | 125 | 500
Shyampur | 126 | 300 | 121 | 1200 | Sikalbaha | 130 | 900 | 126 | 1700
Bhulta | 124 | 600 | 120 | 900 | Dohazari | 130 | 700 | 124 | 1830
Madanganj | 130 | 100 | 124 | 1200 | Cox'sbazar | 131 | 700 | 122 | 100
Shitalakhya | 133 | 100 | 126 | 1200 | Chandraghona | 132 | 900 | 127 | 100
Rahim steal | 133 | 100 | 130 | 1300 | Kaptai | 132 | 800 | 127 | 100
Matuail | 132 | 100 | 127 | 1200 | A. Khaer Stl. | 130 | 300 | 126 | 1200
Ghorasal | 134 | 200 | 133 | 100 | Bakulia | 129 | 500 | 125 | 1200
Narsinghdi | 132 | 600 | 128 | 1200 | Julda | 130 | 500 | 126 | 1800
Haripur (SBU) | 133 | 100 | 128 | 1200 | TK Chemical | 134 | 500 | 129 | 1800
Ullon | 133 | 500 | 128 | 1200 | Modern Steel | 130 | 500 | 126 | 100
Hasnabad | 133 | 600 | 121 | 1300 | Shahmirpur | 130 | 2000 | 126 | 1200
Magbazar | 131 | 600 | 125 | 1200 | Goalpara | 137 | 600 | 122 | 100
Maniknagar | 131 | 600 | 126 | 1200 | Central s/s | 137 | 600 | 120 | 100
Bangabhaban | 131 | 600 | 126 | 1200 | Noapara | 135 | 500 | 120 | 100
Narinda | 131 | 600 | 126 | 1200 | Jessore | 130 | 1600 | 115 | 100
Dhanmondi | 133 | 500 | 128 | 1200 | Jhenida | 131 | 1600 | 113 | 100
Agargaon | 134 | 300 | 127 | 1200 | Bottail | 140 | 900 | 131 | 1200
Mirpur | 130 | 600 | 123 | 1200 | G.K.Project | 141 | 1830 | 133 | 1200
Kalyanpur | 133 | 500 | 127 | 1300 | Faridpur | 135 | 700 | 127 | 1900
Gulshan | 132 | 600 | 124 | 1200 | Madaripur | 136 | 300 | 120 | 1200
Uttara | 134 | 500 | 124 | 1200 | Gopalganj | 141 | 600 | 127 | 100
Kamrangirchar | 129 | 500 | 122 | 1200 | Bagerhat | 132 | 1600 | 115 | 1200
Savar | 131 | 600 | 124 | 1200 | Mongla | 137 | 600 | 118 | 1200
Bhasantec | 131 | 200 | 124 | 900 | Satkhira | 137 | 600 | 121 | 1200
Tongi | 136 | 800 | 130 | 1200 | Gallamari | 139 | 600 | 123 | 1200
Kabirpur | 129 | 100 | 123 | 1900 | Magura | 132 | 1600 | 115 | 100
Basundhara | 128 | 400 | 121 | 1200 | Chuadanga | 131 | 1700 | 109 | 100
Manikganj | 130 | 1000 | 120 | 2300 | Barisal | 136 | 600 | 118 | 1200
Joydevpur | 133 | 1300 | 130 | 2100 | Patuakhali | 130 | 400 | 115 | 1200
New Tongi | 133 | 500 | 126 | 2200 | Bhandaria | 137 | 600 | 115 | 1200
Tangail | 132 | 900 | 122 | 2200 | Ishurdi | 140 | 600 | 132 | 1200
Mymensing | 135 | 1500 | 128 | 100 | Natore | 136 | 1800 | 125 | 2100
Kishorganj | 135 | 1400 | 130 | 100 | Bogra | 135 | 1400 | 129 | 2100
Netrokona | 135 | 900 | 129 | 100 | Noagaon | 130 | 600 | 126 | 100
Jamalpur | 129 | 700 | 120 | 1930 | Rajshahi | 136 | 1930 | 126 | 1200
Srimongal | 140 | 100 | 136 | 900 | C.Nawabganj | 135 | 1830 | 125 | 1200
Shahjibazar | 143 | 100 | 139 | 800 | Pabna | 134 | 700 | 131 | 100
Fenchuganj | 137 | 1400 | 135 | 1200 | Shahjadpur | 139 | 300 | 135 | 2100
Sylhet | 136 | 300 | 134 | 800 | Serajganj | 34 | 600 | 130 | 100
Chatak | 135 | 400 | 132 | 2200 | Niyamatpur | 130 | 600 | 126 | 100
B.Baria | 136 | 500 | 132 | 800 | Joypurhat | 133 | 600 | 123 | 1700
Comilla(S) | 135 | 1100 | 130 | 2000 | Rangpur | 128 | 1400 | 122 | 1930
Comilla(N) | 136 | 800 | 132 | 900 | Lalmonirhat | 128 | 500 | 119 | 2100
Chandpur | 136 | 700 | 133 | 100 | Saidpur | 127 | 500 | 119 | 2100
Feni | 126 | 1000 | 124 | 1700 | Purbasadipur | 126 | 100 | 12 | 1200
Chowmuhani | 130 | 1000 | 124 | 2100 | Thakurgaon | 123 | 400 | 112 | 2000
Ashuganj | 143 | 600 | 141 | 1000 | Palashbari | 130 | 500 | 121 | 2100
Daudkandi | 134 | 1830 | 130 | 1200 | Barapukuria | 129 | 1800 | 123 | 2100
Madanhat | 134 | 2000 | 130 | 100 | Panchagar | 122 | 600 | 110 | 1930
Hathazari | 134 | 400 | 129 | 1500