## Daily Gen
Hourly Generation & Demand
Date | 2014-08-14
Time | Generation | Demand | Shortage | Remarks
Hour | MW | MW | MW
1:00 | 5857 | 5857 | 0
2:00 | 5694 | 5694 | 0
3:00 | 5482 | 5482 | 0
4:00 | 5347 | 5347 | 0
5:00 | 5226 | 5226 | 0
6:00 | 4918 | 4918 | 0
7:00 | 4818 | 4818 | 0
8:00 | 4844 | 4844 | 0
9:00 | 5242 | 5242 | 0
10:00 | 5546 | 5546 | 0 | Day peak
11:00 | 5452 | 5452 | 0
12:00 | 5456 | 5456 | 0
13:00 | 5286 | 5286 | 0
14:00 | 5258 | 5258 | 0
15:00 | 5440 | 5440 | 0
16:00 | 5487 | 5487 | 0
17:00 | 5492 | 5492 | 0
18:00 | 5621 | 5621 | 0
18:30 | 6016 | 6016 | 0
19:00 | 6447 | 6447 | 0
19:30 | 6493 | 6493 | 0
20:00 | 6510 | 6510 | 0 | Evening Peak
21:00 | 6370 | 6370 | 0
22:00 | 6271 | 6271 | 0
23:00 | 6190 | 6190 | 0
24:00 | 5854 | 5854 | 0

## forecast
[7 empty] | POWER GRID COMPANY OF BANGLADESH LTD. | [6 empty] | QF-LDC-07
SUMMARY OF DAILY ELECTRICITY GENERATION
|  | Month : |  | 2014-08-15 |  |  | Day : | Friday |  |  |  | Date : | 2014-08-15
| Probable Maximum Generation : |  |  |  | (a) At Day Peak Hour : |  | 4730 | MW |  | (b) At Evening Peak Hour : |  |  | 6730 | MW
| Water Level of Kaptai Lake at 06:00 AM (ft) |  |  |  | (a) Yesterday : |  | 85.81 |  |  | (b) Today: | 87.91 | (c) Rule Curve: |  | 93.48
Sl. | Name of the Power Station |  | Fuel | Producer | Instslled Capacity |  | Derated/ | Actual Generation |  | Available Geneneration |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
[7 empty] | Present | On | 2014-08-14 | On | 2014-08-15 | for Fuel | for Plants S/D | Shut down (Date) / |  | Start up
[7 empty] | Capacity | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | or M/C prob. | Remarks |  | Date
[6 empty] | MW | MW | MW | MW | MW | MW | MW | MW
1a | Ghorasal ST: Unit-1, 2 |  | Gas | PDB | 2X55 | 110 | 85 | 88 | 88 | 88 | 88
1b | Ghorasal ST: Unit-3 |  | Gas | PDB | 1x210 | 210 | 170 | 100 | 100 | 100 | 100 |  | 70
1c | Ghorasal ST: Unit-4 |  | Gas | PDB | 1x210 | 210 | 180 | 180 | 180 | 180 | 180
1d | Ghorasal ST: Unit-5 |  | Gas | PDB | 1x210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | 2014-12-08 |  | 19/8/14
1e | Ghorasal ST: Unit-6 |  | Gas | PDB | 1x210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | #6 (18/07/2010) |  | Long term maint.
2 | Ghorashal 100MW(Aggreko) |  | Gas | QRPP | 128X0.85 | 100 | 100 | 92 | 96 | 94 | 96
3 | Ghorashal 45MW (Aggreko) |  | Gas | QRPP | 58X0.85 | 45 | 45 | 42 | 47 | 46 | 45
4 | Ghorashal 78.5MW (MAX) |  | Gas | QRPP | 4x21.5 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Contract date expired 26/05/14, Long term maint.
5 | Ghorashal (Regent) |  | Gas | IPP | 34x3.35 | 108 | 108 | 101 | 104 | 104 | 104
6 | Haripur GT: Unit-1, 2, 3 |  | Gas | PDB | 3x32 | 96 | 60 | 0 | 0 | 0 | 0 | 40 | 20 | #1&#2(22/10/13),#3(18/6/09) |  | #3 long term maint.
7 | Haripur 412 MW CCPP |  | Gas | EGCB | 1x273+1x139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | 31/07/2014 |  | Unknown
8 | Haripur NEPC (HFO) |  | HFO | IPP | 8x15 | 110 | 110 | 70 | 83 | 40 | 83 |  | 27 | 2 Engine problem
9 | Haripur Power CCPP |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 354 | 336 | 351 | 336
10 | Meghnaghat CCPP |  | Gas | IPP | 2X150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | 21/04/2014 |  | Long term maint.
11 | Meghnaghat (IEL) |  | HFO | RPP | 12x8.9 | 100 | 100 | 90 | 89 | 32 | 89 |  | 11 | 1 Engine problem
12 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2x110+1x110 | 203 | 203 | 101 | 203 | 51 | 203
13 | Madanganj (Summit) |  | HFO | QRPP | 6x17 | 102 | 100 | 77 | 91 | 39 | 91 |  | 21 | 1 Engine problem
14 | Keraniganj (Powerpac) |  | HFO | RPP | 8x13.45 | 100 | 100 | 100 | 100 | 10 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP,REB | 8X2.90 | 22 | 22 | 17 | 17 | 15 | 17 |  | 5 | Synchronized at 33KV, 1 Machine problem
16a | Siddhirgonj ST |  | Gas | PDB | 1x210 | 210 | 150 | 110 | 110 | 110 | 110 | 40
16b | Siddhirgonj GT: Unit-1& 2 |  | Gas | EGCB | 2x105 | 210 | 210 | 60 | 40 | 104 | 100 | 170
17 | Siddhirganj (Desh) |  | HSD | QRPP | 96x1.2 | 96 | 98 | 72 | 68 | 0 | 80 |  | 15 | 12 Engine problem
18 | Siddhirganj (Dutch Bangla) |  | HFO | RPP | 12x8.9 | 100 | 100 | 67 | 75 | 42 | 75 |  | 25 | 3 Engine problem
19 | Pagla (DPA ) |  | HSD | QRPP | 100X0.5 | 50 | 50 | 0 | 0 | 0 | 0 |  | 50 | Contract date expired. 31/07/2014
20 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 102 | 7 | 102
21 | Summit Power, Dhaka |  | Gas | SIPP,REB | 6*3.67+2*6.97+14*8.73 | 146 | 146 | 108 | 77 | 89 | 100 |  |  | Synchronized at 33KV
22 | Gazipur (RPCL) |  | HFO | IPP | 6x8.9 | 52 | 52 | 34 | 34 | 0 | 34 |  | 18 | 2 Machine problem
23 | Tongi GT |  | Gas | PDB | 1X 105 | 105 | 105 | 0 | 0 | 60 | 60 | 105
| Dhaka Area Total |  |  |  |  | 4307 | 4076 | 1965 | 2040 | 1562 | 2193 | 355 | 1504
24a | Chittagong ST: Unit-1 |  | Gas | PDB | 1x210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | 13/8/2014 |  | Unknown
24b | Chittagong ST: Unit-2 |  | Gas | PDB | 1x210 | 210 | 180 | 100 | 110 | 110 | 110
25 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3x8.9 | 25 | 25 | 26 | 26 | 0 | 25
26 | Patenga 50MW (Barakatullah) |  | HFO | IPP | 8x6.89 | 50 | 50 | 0 | 39 | 6 | 40 |  | 11 | 1 Engine problem
27 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2X40, 3X50 | 230 | 230 | 44 | 186 | 46 | 186
28a | Sikalbaha ST |  | Gas | PDB | 1X60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | 2014-03-07 |  | Unknown
28b | Sikalbaha Peaking GT |  | Gas | PDB | 1x150 | 150 | 150 | 113 | 70 | 77 | 120 | 80
29 | Sikalbaha (Energis) |  | HFO | RPP |  | 26 | 26 | 25 | 24 | 25 | 25
30 | Hathazari peaking |  | HFO | PDB | 11x8.9 | 98 | 98 | 0 | 97 | 0 | 98
31 | Dohazari-Kalaish Peaking |  | HFO | PDB | 6x17 | 102 | 102 | 0 | 102 | 0 | 102
32 | Juldah (Acorn) |  | HFO | QRPP | 8x13.45 | 100 | 100 | 80 | 92 | 60 | 92 |  | 8
33 | Barabkunda (Regent) |  | Gas | SIPP,PDB | 8X2.90 | 22 | 22 | 22 | 22 | 22 | 22 |  |  | Synchronized at 33KV
34 | Malancha, Ctg. EPZ (United) |  | Gas |  |  |  |  | 5 | 23 | 52 | 40
| Chittagong area Total |  |  |  |  | 1283 | 1203 | 415 | 791 | 398 | 860 | 260 | 59
35a | Ashuganj ST: Unit- 1 & 2 |  | Gas | APSCL | 2x64 | 128 | 97 | 90 | 50 | 90 | 90
35b | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1x150 | 150 | 135 | 130 | 130 | 0 | 0 |  | 130 | 15/8/14 |  | 17/8/14
35c | Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1x150 | 150 | 129 | 140 | 140 | 140 | 140
35d | Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1x150 | 150 | 134 | 130 | 130 | 130 | 130
35e | Ashuganj CCPP: GT-2 |  | Gas | APSCL | 1x56 | 56 | 40 | 40 | 40 | 40 | 40
35f | Ashuganj Engines |  | Gas | APSCL | 14x3.968 | 53 | 45 | 39 | 39 | 36 | 39 |  | 6 | 1 Engine problem
36 | Ashuganj (Precision) |  | Gas | RPP | 15x4 | 55 | 55 | 49 | 49 | 53 | 49 |  | 6 | 1 Engine problem
37 | Ashuganj (Aggrekko) |  | Gas | QRPP | 82x1.1 | 80 | 80 | 79 | 81 | 83 | 80
38 | Ashuganj (United) |  | Gas | QRPP | 14x4 | 53 | 53 | 49 | 49 | 49 | 49
39 | Ashuganj (Midland) |  | Gas | IPP | 6x9.34 | 51 | 51 | 42 | 42 | 42 | 42 |  | 9 | 1 Machine problem
40 | Brahmanbaria (Aggreko) |  | Gas | QRPP | 72x1.10 | 70 | 70 | 83 | 86 | 85 | 86
41 | Titas (Daudkandi) Peaking |  | HFO | PDB | 6x8.92 | 52 | 52 | 0 | 35 | 0 | 42 |  | 17 | 2 Engine problem
42 | Chandpur CCPP |  | Gas | PDB | 1x106+1x57 | 163 | 163 | 160 | 162 | 160 | 163
43 | Feni (Doreen) |  | Gas | SIPP,PDB | 8X2.90 | 22 | 22 | 14 | 15 | 15 | 15 |  | 7 | 2 Machine problem
44 | Feni, Mohipal (Doreen) |  | Gas | SIPP,REB | 4X2.90 | 11 | 11 | 0 | 8 | 8 | 8 |  | 3 | Synchronized at 33KV , 1 Machine problem
45 | Jangalia (Summit) |  | Gas | SIPP,PDB | 4X8.73 | 33 | 33 | 0 | 34 | 34 | 33 |  |  | Synchronized at 33KV
46 | Summit Power, Comilla |  | Gas | SIPP,REB | 3x3.67+2x6.97 | 25 | 25 | 12 | 15 | 15 | 15 |  | 10 | Synchronized at 33KV, 2 Engine problem
| Comilla Area Total |  |  |  |  | 1302 | 1195 | 1057 | 1105 | 980 | 1021 | 0 | 188
47 | RPCL CCPP |  | Gas | IPP | 4X35+1x70 | 210 | 202 | 150 | 139 | 151 | 139 | 63
48 | Tangail (Doreen) |  | Gas | SIPP, PDB | 8X2.90 | 22 | 22 | 17 | 14 | 0 | 14 |  |  | Synchronized at 33KV
| Mymensingh Area Total |  |  |  |  | 232 | 224 | 167 | 153 | 151 | 153 | 63 | 0
49a | Fenchugonj CCPP-1 |  | Gas | PDB | 2x32+1x33 | 97 | 80 | 33 | 60 | 51 | 60 |  | 20
49b | Fenchugonj CCPP-2 |  | Gas | PDB | 2x35+1x35 | 104 | 90 | 43 | 43 | 43 | 43 |  | 47 | GT-3 (1/8/2014) |  | Unknown
50 | Fenchugonj (Barakatullah) |  | Gas | RPP | 19X2.90 | 51 | 51 | 42 | 50 | 47 | 50
51 | Fenchuganj (Energyprima) |  | Gas | RPP | 12x3.3+5x2 | 44 | 44 | 50 | 45 | 45 | 44
52 | Hobiganj (Confidence-EP) |  | Gas | SIPP, REB | 4X2.90 | 11 | 11 | 11 | 10 | 11 | 10 |  |  | Synchronized at 33KV
53 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2X35 | 70 | 66 | 68 | 66 | 66 | 66
54 | Shahjibazar (Shahjibazar) |  | Gas | RPP | 32X2.90 | 86 | 86 | 84 | 84 | 84 | 84
55 | Shahjibazar (Energyprima) |  | Gas | RPP | 27X2.0 | 50 | 50 | 47 | 48 | 47 | 48
56 | Sylhet 150 MW GT |  | Gas | PDB | 1X142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | 28/07/2014 |  | 25/8/2014
57 | Sylhet 20 MW GT |  | Gas | PDB | 1X20 | 20 | 20 | 20 | 20 | 20 | 20
58 | Sylhet (Energyprima) |  | Gas | RPP | 27X2 | 50 | 50 | 45 | 46 | 44 | 46
59 | Shahjahanulla 25 MW |  | Gas | CIPP, REB | 3x9.34 | 25 | 25 | 18 | 23 | 16 | 24
60 | Sylhet (Desh) |  | Gas | RPP | 6X1.95 | 10 | 10 | 9 | 9 | 9 | 9
| Sylhet Area Total |  |  |  |  | 760 | 725 | 470 | 504 | 483 | 504 | 0 | 209
61 | Bheramara GT: Unit- 1, 2 ,3 |  | HSD | PDB | 3X20 | 60 | 46 | 0 | 46 | 0 | 46
62 | Bheramara (Quantum) |  | HSD | RPP | 12X8.5+2X6+2X13 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | 16 Engine problem |  | Long term maint.
63 | Bheramara HVDC Interconnector |  |  | India |  | 500 | 500 | 400 | 348 | 392 | 348
64a | Khulna ST 110MW |  | HFO | PDB | 1X110 | 110 | 55 | 0 | 0 | 0 | 0
64b | Khulna ST 60 MW |  | HFO | PDB | 1X60 |  |  | 0 | 0 | 0 | 0 |  |  | Plant retired in FY 2013-2014
65 | Khulna (KPCL-1) |  | HFO | IPP | 19x6.5 | 110 | 110 | 23 | 107 | 11 | 110
66 | Khulna (KPCL-2) |  | HFO | QRPP | 7x17 | 115 | 115 | 99 | 99 | 49 | 99 |  | 16 | 1 Engine problem
67 | Faridpur Peaking |  | HFO | PDB | 8x6.89 | 54 | 54 | 0 | 42 | 0 | 42 |  | 12 | 2 Engine problem
68 | Khulna 150MW GT |  | HSD | NWZPGCL | 1x150 | 158 | 158 | 155 | 130 | 60 | 158
69 | Gopalganj Peaking |  | HFO | PDB | 16x6.98 | 109 | 109 | 0 | 70 | 0 | 70 |  | 39 | 5 Engine problem
70 | Noapara (Quantam) |  | HFO | RPP | 5x9.9+6x9.5+2x9.2 | 101 | 101 | 0 | 0 | 0 | 0 |  | 101 | Long term maint.
71 | Noapara (Khanjahan Ali) |  | HFO | QRPP | 5x8.5 | 40 | 40 | 32 | 32 | 32 | 32 |  | 8 | 1 Engine problem
72 | Khulna (Aggreko) 55MW |  | HSD | QRPP | 71X0.85 | 55 | 55 | 37 | 46 | 0 | 46 |  |  | Contract date expired
| Khulna Area Total |  |  |  |  | 1517 | 1448 | 746 | 920 | 544 | 951 | 0 | 281
73 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2X20 | 40 | 30 | 0 | 32 | 0 | 30
74 | Bhola (Venture) |  | Gas | RPP | 1X34.50 | 33 | 33 | 16 | 7 | 24 | 33
| Barisal Area Total |  |  |  |  | 73 | 63 | 16 | 39 | 24 | 63 | 0 | 0
75a | Baghabari GT |  | Gas | PDB | 1X71 | 71 | 71 | 70 | 70 | 70 | 70
75b | Baghabari GT |  | Gas | PDB | 1X100 | 100 | 100 | 98 | 100 | 98 | 100
76 | Baghabari Peaking |  | HFO | PDB | 6x8.9 | 52 | 52 | 0 | 48 | 0 | 48
77 | Westmont GT, Baghabari |  | Gas | IPP |  |  |  | 0 | 0 | 0 | 0 |  |  | Plant Retired in FY 2013-2014
78 | Bera Peaking |  | HFO | PDB | 9x8.29 | 71 | 71 | 0 | 58 | 0 | 65
79 | Amnura |  | HFO | QRPP | 7x7.79 | 50 | 50 | 9 | 36 | 0 | 44 |  | 14 | 2 Engine problem
80 | Katakhali (Northern) |  | HFO | QRPP | 6x8.92 | 50 | 50 | 42 | 42 | 8 | 42 |  | 8 | 1 Engine problem
81 | Katakhali Peaking |  | HFO | PDB | 6x8.7 | 50 | 50 | 0 | 46 | 0 | 46
82 | Sirajganj CCPP |  | Gas | NWPGCL | 1x150+1x75 | 210 | 210 | 213 | 214 | 213 | 210
83 | Santahar Peaking |  | HFO | PDB | 6x8.7 | 50 | 50 | 0 | 46 | 0 | 46
84 | Bogra (GBB) |  | Gas | RPP | 6X4 | 20 | 22 | 18 | 18 | 18 | 18 |  | 4 | 1 Engine problem
85 | Bogra (Energyprima) |  | Gas | RPP | 5x3.3+5x2 | 20 | 20 | 17 | 16 | 16 | 16 |  | 4 | 1 Engine problem
86 | Ullapara (Summit) |  | Gas | SIPP,REB | 4X2.90 | 11 | 11 | 10 | 0 | 0 | 10 |  |  | Synchronized at 33KV
87 | Rajlanka 52 MW |  | HFO | IPP | 6X8.92 | 52 | 52 | 43 | 42 | 8 | 42 |  | 10 | 1 Machine problem
| Rajshahi Area Total |  |  |  |  | 807 | 809 | 520 | 736 | 431 | 757 | 0 | 40
88a | Barapukuria ST: Unit-1 |  | Coal | PDB | 1x125 | 125 | 100 | 70 | 68 | 70 | 74 |  | 32
88b | Barapukuria ST: Unit-2 |  | Coal | PDB | 1x125 | 125 | 100 | 90 | 90 | 87 | 90 |  | 10
89 | Rangpur GT |  | HSD | PDB | 1X20 | 20 | 20 | 0 | 15 | 0 | 15 |  | 5
90 | Syedpur GT |  | HSD | PDB | 1X20 | 20 | 20 | 0 | 18 | 0 | 18
91 | Thakurgaon (RZ) |  | HSD | RPP | 20X1.5+21X1.1 | 47 | 40 | 30 | 31 | 0 | 31 |  | 9 | 5 Engine problem
| Rangpur Area Total |  |  |  |  | 337 | 280 | 190 | 222 | 157 | 228 | 0 | 56
| Total |  |  |  |  | 10618 | 10023 | 5546 | 6510 | 4730 | 6730 | 678 | 2337
| Useable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 4949.7802 | 5994 | 4221.5039 | 6007
A. |  | 2014-08-14 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 6510 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
2 | Minimum Generation : |  |  | 4818 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 6510 | MW
3 | Day peak Generation : |  |  | 5546 | MW at | 10:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 5994 | MW
4 | Evening peak Generation : |  |  | 6510 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  |  | 132.6718 | MKWHr |  |  | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 86.848 | MKWHr |  | By Oil: | 31.4144 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.7937 | MKWHr |  | By Hydro: | 1.4419 | MKWHr | Area | Demand | Supply | Loadshed | (Duration) |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Gas: | 678 | For Oil: | 0 | MW | Dhaka | 2318 | 2318 | 0 |  |  | Hour |  | MW
|  |  | For Water Shortage: |  |  | 0 | MW | Chittagong | 660 | 660 | 0 |  |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob: |  |  | 2337 | MW | Khulna | 752 | 752 | 0 |  |  | 18:30 |  | 0
7 | Total Gas Supplied : |  | 845.54 | MMCFD |  |  |  | Rajshahi | 631 | 631 | 0 |  |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 68135917.712 | ii) Oil : Taka |  | 406274353.941 | Comilla | 484 | 484 | 0 |  |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 14765259.432 | Total | Taka | 489175531.085 | Mymensingh | 366 | 366 | 0 |  |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 7.8675 | MKWHr. | Sylhet | 293 | 293 | 0 |  |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -100 | MW at | 20:00 | hrs | Barisal | 136 | 136 | 0 |  |  | 22:00 |  | 0
| iii) Maximum : |  |  | 140 | MW at | 15:00 | hrs | Rangpur | 354 | 354 | 0 |  |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 28.8° C |  |  | Total | 5994 | 5994 | 0
B. |  | 2014-08-15 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 27.5° C
Forecast
1 | Maximum Demand (Generation end) |  |  |  | 6700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 6730 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Shortage (Generation end) |  |  |  | -30 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
4 | Total Energy Generation |  |  |  | 133 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
5 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 4333 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 9.1738 | MKWHr.
ii) During peak Demand : |  |  | 400 | MW at | 20:00 | hrs
iii) Maximum : |  |  | 402 | MW at | 6:00 | hrs
Cost for HVDC energy is not usaually included in the total fuel cost.

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2014-08-15
Till now the maximum generation is : - |  |  | 7418 MW | 21:00 | Hrs on | 2014-07-18
The Summary of Yesterday's ( |  | 2014-08-14 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 5546 | MW Hour : | 10:00 | Min. Gen. at | 7:00 | 4333 | MW
Evening Peak Generation : |  | 6510 | MW Hour : | 20:00 | Max Generation : |  | 6730 | MW
E.P. Demand (at gen end) : |  | 6510 | MW Hour : | 20:00 | Max Demand : |  | 6700 | MW
Maximum Generation : |  | 6510 | MW Hour : | 20:00 | Shortage : |  | -30 | MW
Total Gen. (MKWH) : |  | 132.6718 | System L/ Factor : | 78.37% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 140 | MW at | 15:00 | Energy | 7.8675 | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2014-08-15
Actual : | 87.64 | Ft.(MSL) , | Rule curve : | 93.48 | Ft.( MSL )
Gas Consumed : | Total | 845.54 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : Gas : |  |  | 68135917.712
|  | Coal : | 14765259.432 | Oil : | 406274353.941 | Total : | 489175531.085
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand(s/s end) |  | Estimated Shedding (s/s end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | - | 0:00 | 2409 |  |  | - | -
Chittagong Area | - | 0:00 | 619 |  |  | - | -
Khulna Area | - | 0:00 | 677 |  |  | - | -
Rajshahi Area | - | 0:00 | 656 |  |  | - | -
Comilla Area | - | 0:00 | 452 |  |  | - | -
Mymensingh Area | - | 0:00 | 373 |  |  | - | -
Sylhet Area | - | 0:00 | 304 |  |  | - | -
Barisal Area | - | 0:00 | 135 |  |  | - | -
Rangpur Area | - | 0:00 | 382 |  |  | - | -
-
Total | 0 |  | 6007 |  |  | 0
Information of the Generating machines under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
| 1) Haripur GT: Unit-3 (18/06/2009) |  |  | 1) Ghorasal ST: Unit-6 (18/07/2010)
2) Megnaghat CCPP (21/04/2014)
3) Sylhet 150 MW GT (28/07/14)
4) Ghorasal-5(12/8/14)
5) Ashuganj-3(14/8/14)
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
| Description |  |  | Forced load shaded / Interrupted Areas
a) Aminbazar 230/132 kV T2 transformer tripped at 10:52 due to Buz bird fallen on tertiaring winding
and was switched on at 11:52.
b) Rangpur-Saidpur 132 kV Ckt-1 was shut down at 11:40 due to 132 kV CB at Rangpur gas leakage
and was switched on at 14:45.
c) Ashuganj #1 was shut down at 14:34 due to drum level high and was synchronized at 23:04.
d) Ishurdi-Bheramara HVDC Ckt-1 tripped at 17:55 showing gen trip, DTIL receive and was switched
on at 20:08.
e) Ghorasal-45 MW tripped at 20:54 due to back feed problem and was synchronized at 21:20.
f) Khulna( C)-Noapara 132 kV Ckt-1 was shut down at 07:33(15/8/14) due to red hot maintenance
at Khulna(C) end.

## P2
POWER GRID COMPANY OF BANGLADESH LTD.
Description of the generation of various Power Stations
| Date : | 2014-08-14 | [6 empty] | Page -2
[5 empty] | Present | Peak Hour | Energy
| Name of Power Station |  | Unit | Producer | Generation | Generation | Generated |  | Remarks
Capacity
[5 empty] | MW | MW | KWHr
1 | Ghorasal ST: Unit-1, 2 |  | 2x55 | PDB | 85 | 45 | 2048000
43
2 | Ghorasal ST: Unit-3 |  | 1x210 | PDB | 170 | 100 | 2237130 | Machine problem
3 | Ghorasal ST: Unit-4 |  | 1x210 | PDB | 180 | 180 | 4233285
4 | Ghorasal ST: Unit-5 |  | 1x210 | PDB | 190 | 0 | 0 | Under maint.
5 | Ghorasal ST: Unit-6 |  | 1x210 | PDB | 190 | 0 | 0 | Long term maint.
6 | Ghorashal 100MW(Agreko) |  | 128x0.85 | QRPP | 100 | 96 | 2257150
7 | Ghorashal 45MW(Agreko) |  | 58x0.85 | QRPP | 45 | 47 | 1010680
8 | Ghorashal 78.5 MW (MAX) |  | 4x21.5 | QRPP | 78 | 0 | 0 | Contract Date Expired, Long term maint
9 | Ghorashal (Regent) |  | 34x3.35 | IPP | 108 | 104 | 2451590
|  |  | 1x32 | PDB | 20 | 0 | 0 | Gas pressure low
10 | Haripur GT: Unit-1, 2, 3 |  | 1x32 | PDB | 20 | 0 | 0 | Gas pressure low
|  |  | 1x32 | PDB | 20 | 0 | 0 | Under maint. since 18/06/09 Long term maint
11 | Haripur EGCB 412 MW CCPP |  | 1x273+1x139 | EGCB | 412 | 0 | 0 | Under maint.
12 | Haripur NEPC(HFO) |  | 8x15 | IPP | 110 | 83 | 1620500 | 2 Engine problem
13 | Haripur Power CCPP |  | 1x235+1x125 | IPP | 360 | 336 | 8244000 | Gas pressure low
14 | Meghnaghat CCPP |  | 2x150+1x150 | IPP | 450 | 0 | 0 | Long term maint.
15 | Meghnaghat (IEL) |  | 12x8.9 | RPP | 100 | 89 | 2002560 | 1 Engine problem
16 | Meghnaghat CCPP(Summit) |  | 2x110+1x110 | IPP | 203 | 203 | 2719185
17 | Madanganj (Summit) |  | 6x17 | QRPP | 100 | 91 | 2010530 | Engine problem
18 | Keraniganj (Powerpac) |  | 8x13.45 | RPP | 100 | 100 | 2002963
19 | Narsingdi (Doreen) |  | 8 x 2.9 | SIPP, REB | 22 | 17 | 351108 | Synchronized at 33KV, 1 Machine problem
20 | Siddhirgonj ST |  | 1x210 | PDB | 150 | 110 | 2573550 | Gas pressure low
21 | Siddhirgonj GT : Unit-1 & 2 |  | 2x105 | EGCB | 210 | 40 | 1607000 | Gas pressure low
22 | Siddhirgonj (Desh) |  | 96x1.2 | QRPP | 98 | 68 | 970560 | 25 Engine problem
23 | Siddhirgonj (Dutch Bangla) |  | 12x8.9 | RPP | 100 | 75 | 1537920 | 3 Engine problem
24 | Pagla (DPA) |  | 100x0.5 | QRPP | 50 | 0 | 0 | Contract expired
25 | Gagnagar (Orion) |  | 12x8.924 | IPP | 102 | 102 | 1828080
26 | Summit Power,Dhaka |  | 6*3.67+2*6.97+14*8.73 | SIPP, REB | 146 | 77 | 2543717 | Synchronized at 33KV, Machine problem
27 | Gazipur (RPCL) |  | 6x8.9 | IPP | 52 | 34 | 535200 | 2 Engine problem.
28 | Tongi GT |  | 1x105 | PDB | 105 | 0 | 239193 | Gas pressure low
| Dhaka Area Total |  |  |  | 4076 | 2040 | 45023901
29 | Chitagong ST:Unit-1 |  | 1x210 | PDB | 180 | 0 | 0 | Gas pressure low
30 | Chitagong ST:Unit-2 |  | 1x210 | PDB | 180 | 110 | 2500000 | Gas pressure low
31 | Raozan 25 MW (RPCL) |  | 3x8.9 | IPP | 25 | 26 | 471600
32 | Patenga 50 MW(Barakatulla) |  | 8x6.89 | IPP | 50 | 39 | 232320 | 1 Engine problem
|  |  | 1x40 | PDB | 40 | 21 | 1146250
|  |  | 1x40 | PDB | 40 | 40 | 0
33 | Karnafuli Hydro Power Station |  | 1x50 | PDB | 50 | 40 | 0 | Water level low
|  |  | 1x50 | PDB | 50 | 45 | 295600
|  |  | 1x50 | PDB | 50 | 40 | 0
34 | Shikalbaha ST |  | 1x60 | PDB | 40 | 0 | 0 | Under maint.
35 | Shikalbaha peaking GT |  | 1x150 | PDB | 150 | 70 | 2505109 | Gas pressure low
36 | Hathazari peaking |  | 11x8.9 | PDB | 98 | 97 | 454200
37 | Dohazari-Kalaish peaking |  | 6x17 | PDB | 102 | 102 | 494008
38 | Juldah (Acorn) |  | 8x13.45 | QRPP | 100 | 92 | 1924200 | Engine problem
39 | Shikalbaha (Energis) |  |  | RPP | 26 | 24 | 564000 | Contract expired date (06/05/2013)
40 | Barabkunda (regent) |  | 8x2.90 | SIPP, PDB | 22 | 22 | 533760 | Synchronized at 33KV
41 | Malancha, Ctg EPZ(United) |  |  |  |  | 23 | 448320 | Synchronized at 33KV
| Chittagong Area Total |  |  |  | 1203 | 791 | 11569367
42 | Ashuganj ST: Unit- 1 & 2 |  | 1x64 | APSCL | 97 | 50 | 1818700
|  |  | 1x64 | APSCL |  | 0 | 0 | Under maint.
43 | Ashuganj ST: Unit- 3 |  | 1x150 | APSCL | 135 | 130 | 3133862
44 | Ashuganj ST: Unit- 4 |  | 1x150 | APSCL | 129 | 140 | 3334615
45 | Ashuganj ST: Unit- 5 |  | 1x150 | APSCL | 134 | 130 | 3125616
46 | Ashuganj CCPP: GT-2 |  | 1x56 | APSCL | 40 | 40 | 974677
47 | Ashuganj-Engines |  | 14x3.968 | APSCL | 45 | 39 | 282720 | 1 Engine problem
48 | Ashugonj (Precision) |  | 15x4 | RPP | 55 | 49 | 1217760 | 1 Engine problem
49 | Ashuganj (Aggrekko) |  | 82x1.1 | RPP | 80 | 81 | 1925640
50 | Ashuganj (United) |  | 14x4 | RPP | 53 | 49 | 1176000
51 | Ashuganj (Midland) |  | 6x9.34 | IPP | 51 | 42 | 1016309 | 1 Engine problem
52 | Brahmanbaria (Aggreko) |  | 72x1.1 | QRPP | 70 | 86 | 2029000
53 | Titas (Daudkandi) Peaking |  | 6 x 8.92 | PDB | 52 | 35 | 276728 | 2 Engine problem
54 | Chandpur CCPP |  | 1x106+1x57 | PDB | 163 | 162 | 3621323
55 | Feni(Doreen) |  | 8 X 2.94 | SIPP, PDB | 22 | 15 | 354168 | 2 Machine problem
56 | Feni Mohipal (Doreen) |  | 4x2.9 | SIPP, REB | 11 | 8 | 140220 | Synchronized at 33 KV, 1 Machine problem
57 | Jangalia (Summit) |  | 4x8.73 | SIPP, PDB | 33 | 34 | 643110
58 | Summit Power,Comilla |  | 3x3.67+2x6.9 | SIPP, REB | 25 | 15 | 356090 | 2 Machine problem
| Comilla Area Total |  |  |  | 1195 | 1105 | 25426538
59 | RPCL CCPP |  | 4x35+1x70 | IPP | 202 | 139 | 3385000 | Gas pressure low
60 | Tangail (Doreen) |  | 8 x 2.9 | SIPP,PDB | 22 | 14 | 373716 | Synchronized at 33KV
| Mymensingh Area Total |  |  |  | 224 | 153 | 3758716
61 | Fenchugonj CCPP-1 |  | 2x32+1x33 | PDB | 80 | 60 | 1139000 | Machine problem
62 | Fenchugonj CCPP-2 |  | 2x35+1x35 | PDB | 90 | 43 | 1044800 | Machine problem
63 | Fenchugonj RPP (51 MW) |  | 2.9X19 | RPP | 51 | 50 | 1185600
64 | Fenchuganj (Energyprima) |  | 12x3.3+5x2 | RPP | 44 | 45 | 1071000
65 | Hobiganj (Confidence-EP) |  | 4x2.9 | SIPP, REB | 11 | 10 | 191520 | Synchronized at 33 KV
66 |  |  |  |  | 0 | 0 | 0
67 | Shahjibazar GT: Unit-8,9 |  | 32x2.9 | PDB | 66 | 66 | 1464000
68 | Shahjibazar (Shahjibazar) |  | 32X2.9 | RPP | 86 | 84 | 2001600
69 | Shahjibazar (Energyprima) |  | 27x2.0 | RPP | 50 | 48 | 1065960
70 | Sylhet 150 MW GT |  | 1x142 | PDB | 142 | 0 | 0 | Under maint.
71 | Sylhet 20 MW GT |  | 1x20 | PDB | 20 | 20 | 469000
72 | Sylhet (Energyprima) |  | 27 x 2.0 | RPP | 50 | 46 | 1092960 | 1 Machine problem
73 | Shahjahanulla 25MW |  | 3 x 9.34 | CIPP,REB | 25 | 23 | 466272
74 | Sylhet (Desh) |  | 6x1.95 | RPP | 10 | 9 | 210780 | Synchronized at 33KV
| Sylhet Area Total |  |  |  | 725 | 504 | 11402492
|  |  | 1x20 | PDB | 16 | 16 | 0
75 | Bheramara GT: Unit-1,2,3 |  | 1x20 | PDB | 14 | 14 | 182700
|  |  | 1x20 | PDB | 16 | 16 | 0
76 | Bheramara (Quantum) |  | 12x8.5+2x6+2x13 | RPP | 105 | 0 | 0 | All Engine problem, Long term maint
77 | Bheramara HVDC Interconnector |  |  | India | 500 | 348 | 9173818
78 | Khulna ST 110 MW |  | 1x110 | PDB | 55 | 0 | 0
79 | Khulna ST 60 MW |  | 1x60 | PDB |  | 0 | 0 | Plant Retired in FY 2013-2014
80 | Khulna (KPCL-1) |  | 19x6.5 | IPP | 110 | 107 | 1511600
81 | Khulna (KPCL-2) |  | 7x17 | QRPP | 115 | 99 | 1939200 | 1 Engine problem
82 | Faridpur Peaking |  | 8x6.89 | PDB | 54 | 42 | 463200 | 2 Engine problem
83 | Khulna 150 MW GT |  | 1x150 | NWZPGCL | 158 | 130 | 2282880 | Machine problem
84 | Gopalganj Peaking |  | 16x6.98 | PDB | 109 | 70 | 613760 | 4 Engine problem
85 | Noapara (Quantam) |  | 9.9x5+9.5x6+9.2x2 | RPP | 101 | 0 | 0 | All Engine problem, Long term maint
86 | Noapara (Khanjahan Ali) |  | 5x8.5 | QRPP | 40 | 32 | 689250 | Synchronized at 33KV, 1 Engine problem
87 | Khulna (Aggreko) 55MW |  | 71X0.85 | QRPP | 55 | 46 | 390910 | Contract Date expired
| Khulna Area Total |  |  |  | 1448 | 920 | 17247318
88 | Barisal GT: Unit-1,2 |  | 1x20 | PDB | 16 | 16 | 0
89 |  |  | 1x20 | PDB | 14 | 16 | 165369
90 | Bhola (Venture) |  | 1x34.5 | RPP | 33 | 7 | 625176 | Synchronized at 33KV
| Barisal Area Total |  |  |  | 63 | 39 | 790545
91 | Baghabari GT |  | 1x71 | PDB | 71 | 70 | 1630000
92 | Baghabari GT |  | 1x100 | PDB | 100 | 100 | 2309000
93 | Baghabari Peaking |  | 6x8.9 | PDB | 52 | 48 | 255948
94 | Westmont GT, Baghabari |  |  | IPP |  | 0 | 0 | Plant Retired in FY 2013-2014
95 | Bera Peaking |  | 9x8.29 | PDB | 71 | 58 | 386247 | 1 Engine problem
96 | Amnura |  | 7x7.79 | QRPP | 50 | 36 | 386850 | 2 Engine problem
97 | Katakhali (Northern) |  | 6x8.92 | QRPP | 50 | 42 | 521890 | 1 Engine problem
98 | Katakhali Peaking |  | 6x8.7 | PDB | 50 | 46 | 356776
99 | Sirajganj CCPP |  | 1x50+1x75 | NWPGCL | 210 | 214 | 5275972
100 | Santahar Peaking |  | 6x8.7 | PDB | 50 | 46 | 281989
101 | Bogra (GBB) |  | 6x4 | RPP | 22 | 18 | 429900 | 1 Engine problem
102 | Bogra (Energyprima) |  | 5x3.3+5x2 | RPP | 20 | 16 | 391536 | 1 Engine problem
103 | Ullapara (Summit) |  | 4 X 2.90 | SIPP, REB | 11 | 0 | 91800 | Synchronized at 33 kV
104 | Rajlanka 52 MW |  | 6x8.92 | IPP | 52 | 42 | 888480 | 1 Engine problem
| Rajshahi Area Total |  |  |  | 809 | 736 | 13206388
105 | Barapukuria ST: Unit-1 |  | 1x125 | PDB | 100 | 68 | 1676073 | Machine problem
106 | Barapukuria ST: Unit-2 |  | 1x125 | PDB | 100 | 90 | 2117673 | Machine problem
107 | Rangpur GT |  | 1x20 | PDB | 20 | 15 | 50000 | Engine problem
108 | Saidpur GT |  | 1x20 | PDB | 20 | 18 | 64000
109 | Thakurgaon (RZ) |  | 20x1.5+21x1.1 | RPP | 40 | 31 | 338820 | Contract date expired
| Rangpur Area Total |  |  |  | 280 | 222 | 4246566
| Eastern Grid Total |  |  |  | 7423 | 4593 | 97181014
| Western Grid Total |  |  |  | 2600 | 1917 | 35490817
| National Grid Total |  |  |  | 10023 | 6510 | 132671831
*Data collected from respective power station over telephone.

## P3
| POWER GRID COMPANY OF BANGLADESH LTD. | [6 empty] | QF-LDC-09
NATIONAL LOAD DESPATCH CENTER
PEAK HOUR DEMAND (AT S/S END) OF DIFFERENT AREAS
Date: | 2014-08-14
(a) ENTIRE EASTERN GRID : |  |  | 4121 | MW | (b) ENTIRE WESTERN GRID : |  |  | 1873 | MW
i) Dhaka area |  |  | 2318 | MW | i) Khulna area |  |  | 752 | MW
ii) Chittagong area |  |  | 660 | MW | ii) Rajshahi area |  |  | 631 | MW
iii) Comilla area |  |  | 484 | MW | iii) Barisal area |  |  | 136 | MW
iv) Mymensingh area |  |  | 366 | MW | iv) Rangpur area |  |  | 354 | MW
v) Sylhet area |  |  | 293 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 5994 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUBSTATIONS
Sub-Station | Load (MW) | Hour | Sub-Station | Load (MW) | Hour | Sub-Station | Load (MW) | Hour
Siddhirganj | 104 | 1200 | Kishoreganj | 48 | 1930 | Jessore | 110 | 2000
Munsiganj | 69 | 2100 | Netrokona | 39 | 2000 | Jhenida | 47 | 1930
Megnaghat | 19 | 2000 | Jamalpur | 90 | 2000 | Bottail | 64 | 1930
Shyampur | 104 | 1200 | Srimongal | 30 | 2000 | G.K Project | 32 | 1930
Bhulta | 110 | 2000 | Shahjibazar | 33 | 200 | Faridpur | 84 | 2000
Madanganj | 28 | 1100 | Fenchuganj | 46 | 1900 | Madaripur | 75 | 2300
Shitalakhya | 77 | 1500 | Sylhet | 121 | 2000 | Gopalganj | 30 | 1900
Rahim steel | 2 | 800 | Chatak | 36 | 1930 | Bagerhat | 49 | 1830
Matuail | 55 | 1000 | B.Baria | 63 | 100 | Mongla | 22.6 | 1000
Ghorasal | 63 | 100 | Comilla(S) | 129 | 2100 | Satkhira | 50.5 | 2100
Narsingdi | 55 | 2000 | Comilla(N) | 40 | 2100 | Gallamari | 38 | 1200
Haripur (SBU) | 38 | 700 | Chandpur | 66 | 1830 | Magura | 24 | 2000
Ullon | 78 | 2000 | Feni | 83 | 1930 | Chuadanga | 45 | 1930
Hasnabad | 128 | 2000 | Chowmuhani | 119 | 2100 | Barisal | 84 | 1900
Magbazar | 112 | 1600 | Ashuganj | 39 | 1900 | Patuakhali | 53.5 | 2200
Maniknagar | 84 | 2000 | Daudkandi | 38 | 2000 | Bhandaria | 28 | 1900
Bangabhaban | 40 | 1200 | Madanhat | 34.5 | 2000 | Ishurdi | 38 | 2100
Narinda | 74 | 1300 | Hathazari | 80 | 1830 | Natore | 64 | 2100
Dhanmondi | 154 | 1200 | Khulshi | 142 | 1500 | Bogra | 161 | 2100
Agargaon | 14 | 900 | Halishahar | 121 | 2000 | Noagaon | 76 | 2100
Mirpur | 84.5 | 2000 | Baraulia | 73 | 1000 | Rajshahi | 95 | 2100
Kalyanpur | 141 | 1930 | Sikalbaha | 27 | 1930 | C.Nawabganj | 56 | 2000
Gulshan | 111 | 1500 | Dohazari | 64 | 1930 | Pabna | 62 | 2000
Uttara | 81 | 1200 | Cox'sbazar | 52 | 2200 | Shahjadpur | 40 | 200
Kamrangirchar | 87 | 1400 | Chandraghona | 25 | 1900 | Serajganj | 45 | 2100
Savar | 68 | 900 | Kaptai | 3.8 | 1930 | Niyamatpur | 37 | 2000
Bhasantec | 68 | 1200 | A. Khaer Stl. | 5.6 | 1600 | Joypurhat | 25 | 2000
Tongi | 65 | 1000 | Bakulia | 94 | 1900 | Rangpur | 70 | 2000
Kabirpur | 157 | 1000 | Julda | 16 | 300 | Lalmonirhat | 44 | 2000
Basundhara | 107 | 1200 | TK chemical | 12.4 | 1600 | Saidpur | 64 | 2000
Manikganj | 56 | 1930 | Modern Steel | 11 | 600 | Purbasadipur | 54 | 2000
Joydevpur | 181 | 900 | Shahmirpur | 13.7 | 1900 | Thakurgaon | 50 | 2000
New Tongi | 94 | 1200 | Goalpara | 38 | 2000 | Palashbari | 35 | 1930
Tangail | 90 | 2100 | Central s/s | 63 | 200 | Barapukuria | 27 | 1930
Mymensingh | 117 | 1930 | Noapara | 40 | 2100 | Panchagar | 17 | 2000
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## L.curve
Date | 2014-08-14 | [8 empty] | QF-LDC-11
TIME | E-W INT. | EAST GRID | WEST GRID | TOTAL |  | Demand | Hour
0:00 | -510 | 4441 | 1619 | 6060 | -510 | 6060 | 0:00 | DAILY LOAD CURVE | 2014-08-14
0:30 | -357 | 4409.5 | 1549 | 5958.5 | -204 | 5958.5 | 1:00
1:00 | -204 | 4378 | 1479 | 5857 | -210 | 5857 | 2:00
1:30 | -207 | 4319 | 1456.5 | 5775.5 | -236 | 5775.5 | 3:00
2:00 | -210 | 4260 | 1434 | 5694 | -170 | 5694 | 4:00
2:30 | -223 | 4212 | 1376 | 5588 | -260 | 5588 | 5:00
3:00 | -236 | 4164 | 1318 | 5482 | -200 | 5482 | 6:00
3:30 | -203 | 4122 | 1292.5 | 5414.5 | -160 | 5414.5 | 7:00
4:00 | -170 | 4080 | 1267 | 5347 | -230 | 5347 | 8:00
4:30 | -215 | 4033 | 1253.5 | 5286.5 | -60 | 5286.5 | 9:00
5:00 | -260 | 3986 | 1240 | 5226 | 10 | 5226 | 10:00
5:30 | -230 | 3859 | 1213 | 5072 | 20 | 5072 | 11:00
6:00 | -200 | 3732 | 1186 | 4918 | -10 | 4918 | 12:00
6:30 | -180 | 3678.5 | 1189.5 | 4868 | -40 | 4868 | 13:00
7:00 | -160 | 3625 | 1193 | 4818 | -40 | 4818 | 14:00
7:30 | -195 | 3667 | 1164 | 4831 | 140 | 4831 | 15:00
8:00 | -230 | 3709 | 1135 | 4844 | 140 | 4844 | 16:00
8:30 | -145 | 3816 | 1227 | 5043 | 120 | 5043 | 17:00
9:00 | -60 | 3923 | 1319 | 5242 | 0 | 5242 | 18:00
9:30 | -25 | 3998.5 | 1395.5 | 5394 | -40 | 5394 | 18:30
10:00 | 10 | 4074 | 1472 | 5546 | -70 | 5546 | 19:00
10:30 | 15 | 4060.5 | 1438.5 | 5499 | -120 | 5499 | 19:30
11:00 | 20 | 4047 | 1405 | 5452 | -100 | 5452 | 20:00
11:30 | 5 | 4029.5 | 1424.5 | 5454 | -120 | 5454 | 21:00
12:00 | -10 | 4012 | 1444 | 5456 | -80 | 5456 | 22:00
12:30 | -25 | 3975.5 | 1395.5 | 5371 | -80 | 5371 | 23:00
13:00 | -40 | 3939 | 1347 | 5286 | -140 | 5286 | 24:00
13:30 | -40 | 3922.5 | 1349.5 | 5272 |  | 5272
14:00 | -40 | 3906 | 1352 | 5258 | 128.92 | 5258
14:30 | 50 | 3932.5 | 1416.5 | 5349 | 86.5 | 5349
15:00 | 140 | 3959 | 1481 | 5440 |  | 5440
15:30 | 140 | 3978 | 1485.5 | 5463.5 | 7867500 | 5463.5
16:00 | 140 | 3997 | 1490 | 5487 |  | 5487
16:30 | 130 | 4001.5 | 1488 | 5489.5 |  | 5489.5
17:00 | 120 | 4006 | 1486 | 5492 | 700 | 5492
17:30 | 120 | 4006 | 1508 | 5514 | 1800 | 5514
18:00 | 120 | 4006 | 1530 | 5536 | 100 | 5536
18:30 | -40 | 4368 | 1648 | 6016 | 1400 | 6016
19:00 | -70 | 4583 | 1864 | 6447 | 100 | 6447
19:30 | -120 | 4554 | 1939 | 6493 | 1800 | 6493
20:00 | -100 | 4593 | 1917 | 6510 | 1800 | 6510
20:30 | -110 | 4543.5 | 1896.5 | 6440 | 1800 | 6440
21:00 | -120 | 4494 | 1876 | 6370 | 2100 | 6370
21:30 | -100 | 4446.5 | 1874 | 6320.5 | 1900 | 6320.5
22:00 | -80 | 4399 | 1872 | 6271 | 1900 | 6271
22:30 | -80 | 4407.5 | 1823 | 6230.5 |  | 6230.5
23:00 | -80 | 4416 | 1774 | 6190 |  | 6190
23:30 | -110 | 4338 | 1684 | 6022 |  | 6022
24:00 | -140 | 4260 | 1594 | 5854 |  | 5854
*MAX.GEN.(E.P.) |  | 6510 |  | 0.83333
*MAX.GEN.(D.P.) |  | 5546 |  | 0.41667
|  |  |  | min | max
|  | 3063.9 | 3349 | 0.33333 | 0.041667
|  | 2664.1 | 3286.1 | 0.54167 | 0.45833
|  | 2910.2 | 3139.4 | 0.77083 | 24:00
|  | 2664.1 | 3349 | 0.54167 | 0.041667
|  | 282 |  | 0.16667
|  | 276 |  | 0.75
|  | 348 |  | 0.875
|  | 348 |  | 0.875
| Deputy Manager |  |  | Manager |  |  | Deputy General Manager
| Load Despatch Division |  |  | Load Despatch Division |  |  | Load Despatch Circle
NATIONAL LOAD DESPATCH CENTER
3595 MW (09:00 )
4008 MW(05:00 )
.4MW (19:30)
6510MW (20:00)
5546 MW (10:00)

## En.Curve
QF-LDC-12
Date | 2014-08-14 |  | Energy | 132671831
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE |  | DAILY ENERGY CURVE |  | 2014-08-14
0:00 | 1318 | 349 | 2557 | 1440 | 163 | 42 | 213 | 0
0:30 | 1314.5 | 375 | 2558 | 1367.5 | 161.5 | 44 | 160 | 0
1:00 | 1311 | 401 | 2559 | 1295 | 160 | 46 | 107 | 0
1:30 | 1301.5 | 400.5 | 2560.5 | 1227 | 159.5 | 46 | 107 | 0 | [5 empty] | 132.6718
2:00 | 1292 | 400 | 2562 | 1159 | 159 | 46 | 107 | 0 | [5 empty] | 4.1947
2:30 | 1325 | 400.5 | 2556.5 | 1037 | 159.5 | 46 | 89.5 | 0 | [5 empty] | 136.8666
3:00 | 1358 | 401 | 2551 | 915 | 160 | 46 | 72 | 0
3:30 | 1351.5 | 401 | 2548 | 854 | 160.5 | 44 | 72 | 0
4:00 | 1345 | 401 | 2545 | 793 | 161 | 42 | 72 | 0
4:30 | 1347.5 | 401 | 2543 | 745.5 | 162.5 | 41 | 58 | 0
5:00 | 1350 | 401 | 2541 | 698 | 164 | 40 | 44 | 0
5:30 | 1370 | 401.5 | 2534 | 537.5 | 163.5 | 40 | 26 | 0
6:00 | 1390 | 402 | 2527 | 377 | 163 | 40 | 8 | 0
6:30 | 1348.5 | 402 | 2525 | 414.5 | 163.5 | 40 | 8 | 0
7:00 | 1307 | 402 | 2523 | 452 | 164 | 40 | 8 | 0
7:30 | 1286.5 | 402 | 2531 | 476.5 | 163.5 | 41 | 8 | 0
8:00 | 1266 | 402 | 2539 | 501 | 163 | 42 | 8 | 0
8:30 | 1242 | 401.5 | 2527.5 | 739.5 | 162.5 | 42 | 20 | 0
9:00 | 1218 | 401 | 2516 | 978 | 162 | 42 | 32 | 0
9:30 | 1227 | 400.5 | 2501.5 | 1133.5 | 161 | 43 | 50.5 | 0
10:00 | 1236 | 400 | 2487 | 1289 | 160 | 44 | 69 | 0
10:30 | 1247 | 400.5 | 2459.5 | 1259 | 159 | 42 | 70.5 | 0
11:00 | 1258 | 401 | 2432 | 1229 | 158 | 40 | 72 | 0
11:30 | 1266 | 399.5 | 2411 | 1250 | 161 | 40 | 36 | 0
12:00 | 1274 | 398 | 2390 | 1271 | 164 | 40 | 0 | 0
12:30 | 1271.5 | 398 | 2401 | 1180 | 163 | 40 | 22.5 | 0
13:00 | 1269 | 398 | 2412 | 1089 | 162 | 40 | 45 | 0
13:30 | 1287 | 398 | 2436 | 1033.5 | 162.5 | 41 | 48 | 0
14:00 | 1305 | 398 | 2460 | 978 | 163 | 42 | 51 | 0
14:30 | 1284.5 | 398 | 2434 | 1119 | 161.5 | 41 | 51 | 0
15:00 | 1264 | 398 | 2408 | 1260 | 160 | 40 | 51 | 0
15:30 | 1262.5 | 398 | 2407.5 | 1261 | 160 | 41 | 71.5 | 0 | Max Temp. in Dhaka |  | 28.8° C
16:00 | 1261 | 398 | 2407 | 1262 | 160 | 42 | 92 | 0
16:30 | 1263.5 | 398 | 2392.5 | 1251.5 | 160 | 38.5 | 107 | 0
17:00 | 1266 | 398 | 2378 | 1241 | 160 | 35 | 122 | 0
17:30 | 1253.5 | 398 | 2375 | 1248.5 | 159 | 59 | 155 | 0
18:00 | 1241 | 398 | 2372 | 1256 | 158 | 83 | 188 | 0
18:30 | 1258 | 348 | 2396 | 1357 | 158 | 156 | 395 | 0
19:00 | 1265 | 348 | 2404 | 1543 | 158 | 186 | 582 | 0
19:30 | 1259 | 348 | 2391 | 1568 | 154 | 185 | 606 | 0
20:00 | 1264 | 348 | 2387 | 1567 | 158 | 186 | 613 | 0
20:30 | 1262.5 | 347 | 2351 | 1535 | 157 | 186.5 | 599.5 | 0
21:00 | 1261 | 346 | 2315 | 1503 | 156 | 187 | 586 | 0
21:30 | 1243.5 | 346 | 2363.5 | 1477.5 | 157.5 | 135.5 | 572.5 | 0
22:00 | 1226 | 346 | 2412 | 1452 | 159 | 84 | 559 | 0
22:30 | 1211 | 346 | 2434.5 | 1440.5 | 160.5 | 85 | 537.5 | 0
23:00 | 1196 | 346 | 2457 | 1429 | 162 | 86 | 516 | 0
23:30 | 1188 | 346 | 2500.5 | 1381 | 162 | 63 | 389 | 0
24:00 | 1180 | 346 | 2544 | 1333 | 162 | 40 | 262 | 0
|  | 1490 |  |  |  |  | 2380 | 0
|  | Deputy / Asstt. Manager |  |  | Manager
|  | Load Despatch Division |  |  | Load Despatch Division
NATIONAL LOAD DESPATCH CENTER

## volt
NATIONAL LOAD DESPATCH CENTER
The Maximum & Minimum Voltages of different Sub-Stations.
Date : | 2014-08-14
| Maxm |  | Minm |  |  | Maxm |  | Minm
Sub-Station | Voltage | Hour | Voltage | Hour | Sub-Station | Voltage | Hour | Voltage | Hour
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Hathazari | 219 | 1930 | 208 | 1700 | Megnaghat | 219 | 2300 | 210 | 1500
Comilla(N) | 226 | 400 | 215 | 1500 | Haripur | 216 | 2200 | 210 | 1100
Ashuganj | 230 | 100 | 225 | 1500 | Ishurdi | 231 | 900 | 227 | 1500
Ghorasal | 226 | 2300 | 220 | 1300 | Baghabari | 228 | 100 | 222 | 1100
Rampura | 218 | 2400 | 209 | 1500 | Serajganj | 226 | 900 | 222 | 500
Tongi | 214 | 400 | 205 | 1500 | Bogra | 231 | 1830 | 226 | 100
Aminbazar | 215 | 2400 | 205 | 1500 | Barapukuria | 227 | 1300 | 225 | 100
Hasnabad | 235 | 100 | 225 | 1300 | Khulna South | 232 | 1400 | 222 | 800
Fenchuganj | 230 | 800 | 220 | 1500 | Siddhirganj | 225 | 2400 | 209 | 1500
Maniknagar | 223 | 2400 | 207 | 1300
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 136 | 100 | 129 | 1500 | Khulshi | 133 | 2100 | 126 | 1100
Munsiganj | 135 | 1900 | 129 | 1600 | Halishahar | 131 | 2100 | 121 | 1500
Megnaghat | 136 | 100 | 131 | 700 | Baraulia | 130 | 2000 | 120 | 1500
Shyampur | 132 | 100 | 125 | 1500 | Sikalbaha | 135 | 2000 | 121 | 1600
Bhulta | 130 | 300 | 120 | 1400 | Dohazari | 130 | 2100 | 120 | 1300
Madanganj | 131 | 100 | 127 | 1600 | Cox'sbazar | 128 | 1930 | 118 | 1500
Shitalakhya | 137 | 200 | 129 | 1500 | Chandraghona | 133 | 2100 | 123 | 1600
Rahim steal | 133 | 500 | 129 | 100 | Kaptai | 131 | 1900 | 125 | 700
Matuail | 134 | 100 | 127 | 1500 | A. Khaer Stl. | 128 | 2100 | 122 | 1700
Ghorasal | 134 | 800 | 132 | 100 | Bakulia | 128 | 2100 | 121 | 1200
Narsinghdi | 134 | 300 | 130 | 1500 | Julda | 129 | 1930 | 122 | 1100
Haripur (SBU) | 134 | 100 | 128 | 1600 | TK Chemical | 133 | 2100 | 123 | 1400
Ullon | 136 | 700 | 129 | 1300 | Modern Steel | 130 | 2100 | 119 | 1400
Hasnabad | 135 | 100 | 129 | 1200 | Shahmirpur | 128 | 2000 | 120 | 1400
Magbazar | 133 | 600 | 122 | 1500 | Goalpara | 138 | 1600 | 131 | 400
Maniknagar | 132 | 700 | 127 | 1700 | Central s/s | 138 | 1400 | 132 | 600
Bangabhaban | 132 | 700 | 127 | 1700 | Noapara | 136 | 1400 | 126 | 500
Narinda | 132 | 700 | 127 | 1700 | Jessore | 132 | 1400 | 122 | 600
Dhanmondi | 132 | 700 | 127 | 1700 | Jhenida | 132 | 1400 | 117 | 1900
Agargaon | 133 | 100 | 124 | 1500 | Bottail | 136 | 200 | 134 | 600
Mirpur | 131 | 400 | 122 | 1700 | G.K.Project | 138 | 1930 | 135 | 500
Kalyanpur | 134 | 100 | 127 | 1500 | Faridpur | 132 | 1000 | 122 | 1600
Gulshan | 134 | 300 | 123 | 1500 | Madaripur | 133 | 1100 | 122 | 500
Uttara | 131 | 100 | 123 | 1500 | Gopalganj | 137 | 1800 | 118 | 1600
Kamrangirchar | 131 | 500 | 124 | 1800 | Bagerhat | 130 | 1000 | 125 | 500
Savar | 133 | 200 | 125 | 1500 | Mongla | 135 | 1000 | 126 | 400
Bhasantec | 131 | 100 | 125 | 1600 | Satkhira | 135 | 1000 | 129 | 500
Tongi | 135 | 800 | 129 | 1200 | Gallamari | 138 | 1000 | 132 | 400
Kabirpur | 130 | 1800 | 123 | 1400 | Magura | 130 | 1400 | 117 | 1900
Basundhara | 130 | 2100 | 120 | 1930 | Chuadanga | 130 | 1300 | 113 | 1900
Manikganj | 130 | 600 | 124 | 1500 | Barisal | 139 | 600 | 122 | 700
Joydevpur | 134 | 1300 | 128 | 1400 | Patuakhali | 130 | 1100 | 118 | 2000
New Tongi | 133 | 100 | 126 | 1500 | Bhandaria | 130 | 1100 | 122 | 1900
Tangail | 135 | 300 | 125 | 1100 | Ishurdi | 139 | 2000 | 136 | 700
Mymensing | 131 | 1800 | 126 | 2100 | Natore | 136 | 1100 | 132 | 100
Kishorganj | 134 | 600 | 130 | 1930 | Bogra | 135 | 1400 | 131 | 100
Netrokona | 132 | 700 | 125 | 2000 | Noagaon | 132 | 1830 | 127 | 100
Jamalpur | 125 | 500 | 120 | 2100 | Rajshahi | 137 | 1200 | 129 | 200
Srimongal | 143 | 800 | 140 | 100 | C.Nawabganj | 135 | 1830 | 125 | 600
Shahjibazar | 145 | 900 | 142 | 1500 | Pabna | 132 | 100 | 130 | 800
Fenchuganj | 139 | 500 | 134 | 1500 | Shahjadpur | 138 | 100 | 137 | 1800
Sylhet | 137 | 1400 | 131 | 1500 | Serajganj | 134 | 100 | 131 | 1500
Chatak | 136 | 700 | 131 | 1500 | Niyamatpur | 132 | 1830 | 127 | 100
B.Baria | 139 | 500 | 136 | 1500 | Joypurhat | 134 | 1830 | 127 | 100
Comilla(S) | 135 | 700 | 127 | 1500 | Rangpur | 128 | 500 | 124 | 100
Comilla(N) | 137 | 800 | 130 | 1600 | Lalmonirhat | 127 | 600 | 122 | 2000
Chandpur | 135 | 1000 | 132 | 2200 | Saidpur | 126 | 1000 | 122 | 600
Feni | 127 | 700 | 122 | 1500 | Purbasadipur | 126 | 100 | 123 | 1700
Chowmuhani | 128 | 1100 | 124 | 1500 | Thakurgaon | 125 | 1200 | 119 | 1700
Ashuganj | 145 | 100 | 144 | 1500 | Palashbari | 130 | 1400 | 125 | 100
Daudkandi | 134 | 2200 | 127 | 1500 | Barapukuria | 127 | 1300 | 125 | 100
Madanhat | 134 | 1900 | 126 | 1000 | Panchagar | 123 | 1200 | 116 | 600
Hathazari | 131 | 1900 | 125 | 900