## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-03-20 | Monday
|  | Date (day): | 2023-03-20 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11877.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13735 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-03-19 | 2023-03-20 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 90 | 100 | 100 | 80 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 365 |  | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 344 | 352 | 400 | 400 |  |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 307 | 277 | 300 | 300 | 60 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 360 | 320 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 4 | 0 | 0 |  |  | Line shut down
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 310 | 285 | 310 | 310 | 25 |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 34 | 47 | 85 | 85 |  | 17 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 30 | 15 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 102 | 0 | 50 | 60 | 150 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 8 | 14 | 90 | 90 | 10 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 140 | 150 | 220 | 220 |  | 115 | ST under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 8 | 75 | 92 | 10 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 40 | 0 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 64 | 82 | 115 | 34 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 2 | 17 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 12 | 17 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 23 | 43 | 49 | 51 |  | 29 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 16 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 24 | 33 | 50 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 15 | 15 | 280 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 0 | 300 |  | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 23 | 82 | 36 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 52 | 52 | 100
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 16 | 30 | 55 | 90 | 14 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 75 | 90 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 1 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 15 | 35 | 17 | 17 | 38 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 2220 | 2286 | 3178 | 3608 | 1465 | 661
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 135 | 135 | 135 | 135 | 45 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 0 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 9 | 19 | 19 | 19 | 31 |  | Fuel shortage
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 0 | 0 | 25 | 25 | 205 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 212 | 222 | 225 | 225
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 51 | 51 | 34 | 51 | 54 |  | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 8 | 40 | 40 |  | 58 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 65 |  | 37 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 22 | 44 | 54 | 54 |  | 46 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 38 | 100 | 50 | 100
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 5 | 5 | 5 | 5 | 17 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 0 | 0 | 0 | 0
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 1 | 0 | 0 | 108 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 0 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 15 | 120 | 225 | 75 |  | Fuel shortage
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 26 | 35 | 17 | 35 | 19 |  | Fuel shortage
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 43 | 92 | 54 | 92 | 18 |  | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 23 | 12 | 60 | 90 | 10 |  | Fuel shortage
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 57 | 89 | 90 | 90 |  | 26 | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 636 | 887 | 1029 | 1276 | 762 | 317
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 200 | 182 | 210 | 210 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 315 | 330 | 330 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Macine problem
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 330 | 280 | 330 | 330 | 70 |  | FGMO
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 51 | 48 | 50 | 50
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 35 | 55 | 55 | 55
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 102 | 102 | 8 | 8 | 187 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 39 | 43 | 43 | 43 |  | 8 | Engine problem
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 40 | 80 | 40 | 135 |  | 15 | Engine problem
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 35 |  | 17 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 34 | 51 | 100 | 100 | 100 |  | Fuel shortage
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 21 | 21
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 11 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 124 | 102 | 135 | 153
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 0 | 8 | 44 |  | Fuel shortage
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 15 | 15 | 15 | 21 |  | 4 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 17 | 17 | 97 |  | Fuel shortage
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 24 | 9 | 113
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 0 | 17 | 54
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 35 | 95 | 36 | 94 | 21 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 3309 | 3285 | 1024 | 1444 | 1459 | 1820 | 853 | 567
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 44 | 57 | 44 | 65 | 137 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 17 | 19 | 19 | 3 |  | Gas shortage
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 10 | 45 | 165 | 180 | 20 |  | Fuel shortage
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 28 | 104 | 90 | 104 | 11 |  | Fuel shortage
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 13 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 0 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 114 | 229 | 369.6 | 374 | 140 | 0
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 44 | 44 |  | 26 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 43 | 43 |  | 47 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 80 | 80 | 112 |  | 54 | ST U/M.
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 31 | 50 | 51 | 51
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 30 | 47 | 47 | 47
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 8 | 8 | 8 |  | 3 | Engine problem
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 64 | 66 | 65 | 65
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 50 | 86 | 86 | 86
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 79 | 80 | 80 | 80 |  | 151 | Machine Problem
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8 |  | 17 | Engine problem
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 250 | 300 | 300 |  |  | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 353 | 354 | 366 | 368 |  |  | FGMO
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 8 | 8 | 8 | 8
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 360 | 325 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1480 | 1447 | 1586 | 1620 | 0 | 728
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 893 | 869 | 916 | 916
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 16 | 66 | 99 |  | 16 | Engine problem
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 40 |  | 14 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 65 |  | 44 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 230 | 250 | 300 | 300 | 110 |  | Gas shortage
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 8 | 40
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 1 | 35 | 40 | 65 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 100
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 74 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 0 | 0 |  |  | Line O/L
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  |  | 3005 | 3001 | 1197 | 1136 | 1425 | 1600 | 521 | 74
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 48 | 62 |  | Fuel shortage
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 14 | 11 | 15 | 22 |  | 18 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 159 | 170 | 171 | 170
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 630 | 900 | 1000 | 1230
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under maintenance
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Line O/L
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 162 | 161 | 152 | 307
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 965 | 1242 | 1338 | 1777 | 62 | 238
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 32 |  | 20 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 18 | 32 |  | 39 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 40 |  | 10 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 185 | 170 | 150 | 150 | 60 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 268 | 308 | 300 | 360 | 54 |  | Gas shortage
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 36 | 26 | 35 |  | 15 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 20 | 20
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 8 | 44 |  | Fuel shortage
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 34 | 50 | 85 |  | 19 | Enging problem
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 38 | 70 | 70 | 94 |  | 19 | Engine problem
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 70 | 70 | 113
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 2 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 0 | 0 | 0 | 238 | 0 | 260 | 260 |  |  | On test.
| Rajshahi Area Total |  |  |  |  | 2179 | 2129 | 763 | 721 | 1055 | 1282 | 969 | 130
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 169 | 170 | 200 | 200 | 74 |  | Machine problem
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 35 | 78 | 70 | 106 |  | 7 | Engine problem
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 0 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 35 | 0 | 72 | 43 |  | Fuel shortage
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 7 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 74 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 285 | 283 | 438 | 378 | 242 | 92
| Total |  |  |  |  | 23482 | 22700 | 8684 | 9675 | 11877.6 | 13735 | 5014 | 2807
A. |  | 2023-03-19 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 9848 | MW at | 1:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 7822 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9675 | MW
3 | Day peak Generation : |  |  | 8684 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9229.5 | MW
4 | Evening peak Generation : |  |  | 9675 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 216.949 | MKWHr | By Solar | 0.91354 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 139.4344 | MKWHr |  | By Oil: | 21.1203 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 31.7584 | MKWHr |  | By Hydro: | 0.26706 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5014 | MW | Dhaka | 3432.7 | 3432.7 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2807 | MW | Chittagong | 1162.5 | 1162.5 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 7821 | MW | Khulna | 968.8 | 968.8 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 1062.75 | MMCFD |  |  | Rajshahi | 1023.5 | 1023.5 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 151377963.824 | ii) Oil : | Taka | 269930148.81 | Comilla | 653 | 653 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 205693617 | Total | Taka | 627001729.634 | Mymensingh | 769 | 769 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.0495 | MKWHr. | Sylhet | 350 | 350 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 120 | MW (E to W) at | 19:00 | hrs | Barisal | 166 | 166 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | -92 | MW at | 8:00 | hrs | Rangpur | 704 | 704 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 24.7° C |  |  | Total | 9229.5 | 9229.5 |  | 0
B. |  | 2023-03-20 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 28.8° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13735 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8800 | MW
4 | Reserve(Generation end) |  |  |  | 2235 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 253.3422 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6507 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.9018 | MKWHr. | ii) HVDC Flow at Peak Time |  | 869 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.5536 | MKWHr. | iii) Maximum HVDC Flow : |  | 920 | MW at | 14:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 76.98 |  | (b) Today: | 76.87 |  | (c) Rule Curve: |  | 89.96
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-03-19 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 93 | 180 | 0 | 52 | 0 | 398 | 349 |  | 0 | 450 | 289 | 0 | 2 | 0 | 170 | 0 | 37 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 26 | 33 | 33 | 51 | 0 | 25 | 0 | 140 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 0 | 51 | 33 | 0 | 19 | 5 | 0 | 0 | 0 | 0 | 280 | 0 | 211 | 8 | 0 | 50 | 53 | 0 | 43 | 0 | 0 | 8 | 0 | 10 | 33 | 21 | 132 | 82 | 0 | 19 | 0 | 43 | 43 | 50 | 47 | 80 | 0 | 40 | 89 | 0 | 124 | 0 | 0 | 8 | 270 | 8 | 8 | 0 | 0 | 0 | 0 | 68 | 0 | 17 | 0 | 38 | 17 | 74 | 80 | 28 | 52 | 34 | 0 | 65 | 17 | 54 | 17 | 9 | 40 | 400 | 19 | 0 | 0 | 90 | 0 | 0 | 0 | 61 | 17 | 352 | 0 | 0 |  | 886 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 20 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 166 | 0 | 0 |  | 6050 | 3798 | 9848 | 3883 | 886 | 2213 | 0 | 864 | 1757 | 25 | 0 | 88 | 132 | 0 | 40 | 77
2:00 | 0 | 0 | 100 | 180 | 0 | 52 | 0 | 398 | 340 |  | 0 | 450 | 321 | 0 | 0 | 0 | 170 | 0 | 40 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 26 | 33 | 33 | 8 | 0 | 25 | 0 | 140 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 0 | 17 | 33 | 0 | 19 | 5 | 0 | 0 | 0 | 0 | 285 | 0 | 209 | 8 | 0 | 50 | 53 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 33 | 21 | 120 | 86 | 0 | 19 | 0 | 43 | 43 | 50 | 47 | 80 | 0 | 40 | 89 | 0 | 124 | 0 | 0 | 8 | 260 | 8 | 8 | 0 | 0 | 0 | 0 | 69 | 0 | 17 | 0 | 38 | 17 | 0 | 80 | 28 | 17 | 34 | 0 | 30 | 17 | 54 | 17 | 9 | 40 | 350 | 44 | 0 | 0 | 90 | 0 | 0 | 0 | 54 | 0 | 352 | 0 | 0 |  | 886 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 19 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 170 | 0 | 0 |  | 5754 | 3239 | 8993 | 3705 | 886 | 2147 | 0 | 635 | 1422 | 25 | 0 | 53 | 120 | 0 | 0 | 77
3:00 | 0 | 0 | 100 | 180 | 0 | 52 | 0 | 398 | 342 |  | 0 | 400 | 318 | 0 | 0 | 0 | 170 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 26 | 33 | 33 | 8 | 0 | 25 | 0 | 140 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 0 | 33 | 0 | 19 | 5 | 0 | 0 | 0 | 0 | 280 | 0 | 209 | 8 | 0 | 50 | 54 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 33 | 21 | 118 | 86 | 0 | 19 | 0 | 43 | 43 | 50 | 47 | 80 | 0 | 40 | 40 | 0 | 124 | 0 | 0 | 8 | 270 | 8 | 8 | 0 | 0 | 0 | 0 | 45 | 0 | 17 | 0 | 38 | 17 | 0 | 80 | 28 | 17 | 34 | 0 | 15 | 17 | 54 | 17 | 9 | 40 | 350 | 54 | 0 | 0 | 90 | 0 | 0 | 0 | 54 | 0 | 352 | 0 | 0 |  | 887 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 670 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 195 | 0 | 0 |  | 5581 | 2981 | 8562 | 3701 | 887 | 2008 | 0 | 606 | 1217 | 25 | 0 | 0 | 118 | 0 | 0 | 76.99
4:00 | 0 | 0 | 100 | 180 | 0 | 52 | 0 | 396 | 342 |  | 0 | 400 | 311 | 0 | 0 | 0 | 170 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 26 | 33 | 33 | 8 | 0 | 25 | 0 | 140 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 0 | 33 | 0 | 19 | 5 | 0 | 0 | 0 | 0 | 280 | 0 | 203 | 8 | 0 | 50 | 54 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 33 | 15 | 124 | 86 | 0 | 19 | 0 | 43 | 43 | 50 | 47 | 80 | 0 | 40 | 40 | 0 | 124 | 0 | 0 | 8 | 275 | 8 | 8 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 38 | 17 | 0 | 80 | 35 | 17 | 34 | 0 | 0 | 17 | 54 | 17 | 9 | 40 | 350 | 54 | 0 | 0 | 89 | 0 | 0 | 0 | 40 | 0 | 352 | 0 | 0 |  | 888 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 280 | 0 | 0 |  | 5494 | 2870 | 8364 | 3631 | 888 | 1954 | 0 | 530 | 1212 | 25 | 0 | 0 | 124 | 0 | 0 | 76.99
5:00 | 0 | 0 | 100 | 180 | 0 | 52 | 0 | 396 | 304 |  | 0 | 350 | 310 | 0 | 0 | 0 | 170 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 26 | 33 | 33 | 8 | 0 | 25 | 0 | 140 | 0 | 0 | 231 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 0 | 0 | 0 | 0 | 280 | 0 | 207 | 8 | 0 | 50 | 55 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 33 | 21 | 116 | 90 | 0 | 19 | 0 | 43 | 43 | 50 | 47 | 80 | 0 | 40 | 40 | 0 | 124 | 0 | 0 | 8 | 275 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 17 | 0 | 80 | 0 | 17 | 34 | 0 | 0 | 0 | 17 | 0 | 9 | 0 | 350 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 36 | 0 | 353 | 0 | 0 |  | 888 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 297 | 0 | 0 |  | 5134 | 2777 | 7911 | 3651 | 888 | 1866 | 0 | 246 | 1119 | 25 | 0 | 0 | 116 | 0 | 0 | 76.98
6:00 | 0 | 0 | 100 | 180 | 0 | 52 | 0 | 398 | 353 |  | 0 | 400 | 319 | 0 | 0 | 0 | 200 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 26 | 33 | 33 | 8 | 0 | 25 | 0 | 140 | 0 | 0 | 230 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 0 | 0 | 0 | 0 | 315 | 0 | 194 | 8 | 0 | 50 | 55 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 33 | 21 | 112 | 89 | 0 | 19 | 0 | 43 | 43 | 50 | 47 | 80 | 0 | 40 | 40 | 0 | 124 | 0 | 0 | 8 | 270 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 17 | 0 | 80 | 0 | 17 | 34 | 0 | 0 | 0 | 17 | 0 | 9 | 0 | 400 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 36 | 0 | 352 | 0 | 0 |  | 844 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 239 | 0 | 0 |  | 5334 | 2743 | 8077 | 3752 | 844 | 2037 | 0 | 246 | 1061 | 25 | 0 | 0 | 112 | 0 | 0 | 76.98
7:00 | 0 | 0 | 100 | 180 | 0 | 52 | 0 | 399 | 353 |  | 0 | 430 | 302 | 0 | 0 | 0 | 228 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 26 | 33 | 33 | 17 | 0 | 25 | 0 | 140 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 0 | 22 | 0 | 19 | 5 | 0 | 0 | 0 | 0 | 280 | 0 | 193 | 8 | 0 | 51 | 55 | 0 | 31 | 0 | 0 | 0 | 14 | 10 | 33 | 21 | 106 | 51 | 0 | 19 | 0 | 43 | 43 | 50 | 47 | 80 | 0 | 40 | 89 | 0 | 120 | 0 | 0 | 8 | 310 | 8 | 8 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 38 | 17 | 0 | 100 | 16 | 17 | 34 | 0 | 0 | 0 | 19 | 0 | 9 | 2 | 400 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 35 | 3 | 352 | 0 | 0 |  | 797 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 151 | 266 | 2 | 0 |  | 5517 | 2944 | 8461 | 3873 | 797 | 2216 | 0 | 352 | 1087 | 25 | 0 | 0 | 106 | 5 | 0 | 76.97
8:00 | 0 | 0 | 100 | 180 | 0 | 52 | 0 | 395 | 273 |  | 0 | 350 | 283 | 0 | 0 | 0 | 140 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 26 | 0 | 33 | 17 | 0 | 25 | 0 | 140 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 0 | 22 | 0 | 19 | 5 | 0 | 0 | 0 | 0 | 280 | 0 | 190 | 8 | 0 | 50 | 55 | 0 | 43 | 0 | 0 | 0 | 21 | 10 | 0 | 0 | 24 | 52 | 0 | 19 | 0 | 43 | 43 | 50 | 47 | 80 | 0 | 40 | 89 | 0 | 120 | 0 | 0 | 8 | 260 | 8 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 1 | 38 | 17 | 11 | 220 | 16 | 17 | 34 | 0 | 0 | 0 | 40 | 0 | 9 | 29 | 340 | 0 | 1 | 0 | 90 | 0 | 0 | 2 | 36 | 17 | 350 | 0 | 0 |  | 798 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 282 | 0 | 0 | 30 | 0 | 40 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 1 | 152 | 261 | 13 | 0 |  | 5173 | 2861 | 8034 | 3666 | 798 | 1911 | 0 | 498 | 1083 | 25 | 0 | 0 | 24 | 29 | 0 | 76.97
9:00 | 0 | 0 | 100 | 180 | 0 | 52 | 0 | 344 | 277 |  | 0 | 350 | 309 | 0 | 0 | 0 | 140 | 0 | 39 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 5 | 0 | 23 | 7 | 0 | 33 | 8 | 0 | 25 | 0 | 140 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 0 | 33 | 0 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 8 | 0 | 51 | 35 | 0 | 20 | 0 | 0 | 0 | 21 | 7 | 0 | 0 | 74 | 44 | 0 | 19 | 0 | 43 | 43 | 31 | 30 | 80 | 0 | 40 | 60 | 0 | 85 | 0 | 0 | 8 | 270 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 38 | 17 | 20 | 300 | 16 | 17 | 34 | 0 | 0 | 0 | 69 | 0 | 9 | 17 | 340 | 0 | 6 | 0 | 90 | 0 | 0 | 4 | 36 | 17 | 350 | 0 | 0 |  | 845 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 283 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 1 | 31 | 0 | 0 | 0 | 0 | 3 | 151 | 262 | 19 | 0 |  | 4889 | 2933 | 7822 | 3351 | 845 | 1850 | 0 | 530 | 1083 | 25 | 0 | 0 | 74 | 64 | 0 | 76.96
10:00 | 0 | 0 | 100 | 180 | 0 | 52 | 0 | 343 | 279 |  | 0 | 350 | 297 | 0 | 6 | 0 | 140 | 0 | 60 | 1 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 23 | 0 | 0 | 31 | 11 | 0 | 25 | 0 | 140 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 0 | 33 | 0 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 43 | 0 | 51 | 35 | 0 | 20 | 0 | 0 | 0 | 21 | 5 | 0 | 9 | 90 | 44 | 0 | 19 | 1 | 43 | 42 | 31 | 30 | 80 | 0 | 40 | 60 | 0 | 80 | 0 | 0 | 8 | 280 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 48 | 27 | 21 | 337 | 16 | 17 | 35 | 1 | 2 | 5 | 71 | 0 | 10 | 12 | 400 | 0 | 6 | 17 | 90 | 0 | 0 | 0 | 36 | 17 | 360 | 0 | 0 |  | 845 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 1 | 42 | 0 | 0 | 0 | 0 | 7 | 151 | 260 | 26 | 0 |  | 5144 | 3065 | 8209 | 3443 | 845 | 1926 | 0 | 635 | 1161 | 25 | 0 | 0 | 90 | 84 | 0 | 76.96
11:00 | 0 | 0 | 100 | 180 | 0 | 12 | 0 | 298 | 277 |  | 0 | 320 | 302 | 0 | 34 | 28 | 140 | 0 | 42 | 8 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 10 | 0 | 23 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 135 | 0 | 0 | 201 | 0 | 0 | 0 |  | 0 | 0 | 0 | 12 | 0 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 102 | 0 | 51 | 35 | 0 | 20 | 0 | 0 | 0 | 21 | 5 | 0 | 9 | 106 | 44 | 0 | 19 | 1 | 44 | 42 | 14 | 10 | 80 | 0 | 65 | 10 | 0 | 80 | 0 | 0 | 8 | 270 | 8 | 0 | 0 | 12 | 0 | 0 | 8 | 0 | 13 | 0 | 25 | 34 | 40 | 314 | 16 | 17 | 51 | 3 | 15 | 17 | 34 | 0 | 11 | 12 | 360 | 14 | 4 | 17 | 51 | 0 | 0 | 4 | 36 | 17 | 330 | 0 | 0 |  | 893 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 35 | 0 | 36 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 1 | 52 | 0 | 0 | 0 | 0 | 8 | 150 | 255 | 42 | 0 |  | 4924 | 3078 | 8002 | 3266 | 893 | 1766 | 0 | 701 | 1155 | 0 | 0 | 0 | 106 | 115 | 0 | 76.95
12:00 | 0 | 0 | 100 | 180 | 0 | 12 | 0 | 344 | 307 |  | 0 | 360 | 310 | 0 | 34 | 30 | 140 | 0 | 102 | 8 | 24 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 23 | 0 | 33 | 0 | 24 | 0 | 0 | 0 | 135 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 0 | 0 | 22 | 0 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 102 | 0 | 51 | 35 | 0 | 39 | 0 | 0 | 0 | 0 | 10 | 0 | 15 | 124 | 44 | 0 | 19 | 0 | 43 | 42 | 31 | 30 | 112 | 0 | 64 | 50 | 0 | 79 | 0 | 0 | 8 | 300 | 8 | 0 | 0 | 15 | 0 | 0 | 10 | 0 | 23 | 0 | 38 | 34 | 40 | 353 | 28 | 17 | 51 | 0 | 15 | 26 | 43 | 0 | 9 | 23 | 360 | 16 | 13 | 17 | 57 | 0 | 0 | 1 | 35 | 15 | 330 | 0 | 0 |  | 893 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 169 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268 | 0 | 0 | 38 | 0 | 35 | 0 | 0 | 0 | 630 | 0 | 0 | 0 | 2 | 74 | 0 | 0 | 0 | 0 | 7 | 162 | 238 | 74 | 0 |  | 5474 | 3210 | 8684 | 3477 | 893 | 1999 | 0 | 805 | 1199 | 0 | 0 | 16 | 124 | 171 | 0 | 76.95
13:00 | 0 | 0 | 100 | 180 | 0 | 12 | 0 | 395 | 307 |  | 0 | 360 | 289 | 0 | 34 | 10 | 140 | 0 | 102 | 8 | 24 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 23 | 14 | 33 | 16 | 16 | 0 | 0 | 0 | 135 | 0 | 3 | 228 | 0 | 0 | 0 |  | 0 | 9 | 0 | 22 | 0 | 13 | 5 | 0 | 0 | 0 | 0 | 90 | 0 | 179 | 102 | 0 | 51 | 54 | 0 | 43 | 0 | 0 | 0 | 0 | 10 | 0 | 15 | 122 | 35 | 0 | 19 | 0 | 43 | 42 | 48 | 41 | 112 | 0 | 66 | 50 | 0 | 79 | 0 | 0 | 8 | 270 | 8 | 3 | 0 | 15 | 0 | 0 | 57 | 0 | 35 | 0 | 50 | 34 | 40 | 343 | 94 | 15 | 34 | 2 | 15 | 35 | 55 | 0 | 9 | 50 | 319 | 17 | 5 | 17 | 72 | 0 | 0 | 0 | 36 | 16 | 310 | 0 | 0 |  | 892 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 740 | 0 | 0 | 0 | 2 | 65 | 0 | 0 | 0 | 0 | 5 | 161 | 332 | 74 | 0 |  | 5746 | 3516 | 9262 | 3570 | 892 | 2115 | 0 | 982 | 1403 | 0 | 0 | 25 | 122 | 153 | 0 | 76.94
14:00 | 0 | 0 | 100 | 180 | 0 | 12 | 0 | 397 | 307 |  | 0 | 320 | 297 | 0 | 21 | 30 | 140 | 0 | 39 | 8 | 24 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 23 | 20 | 0 | 16 | 16 | 0 | 0 | 0 | 135 | 0 | 8 | 228 | 0 | 0 | 0 |  | 0 | 8 | 0 | 33 | 0 | 16 | 5 | 0 | 0 | 0 | 0 | 20 | 0 | 181 | 102 | 0 | 50 | 55 | 0 | 43 | 0 | 0 | 0 | 0 | 10 | 25 | 15 | 114 | 36 | 0 | 19 | 1 | 43 | 42 | 51 | 44 | 80 | 0 | 40 | 50 | 0 | 80 | 0 | 0 | 8 | 270 | 8 | 5 | 0 | 15 | 0 | 0 | 45 | 0 | 35 | 0 | 50 | 34 | 40 | 340 | 52 | 15 | 34 | 1 | 15 | 35 | 72 | 0 | 9 | 17 | 360 | 17 | 10 | 17 | 72 | 0 | 0 | 8 | 36 | 17 | 315 | 0 | 0 |  | 920 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 750 | 0 | 0 | 0 | 1 | 30 | 0 | 0 | 0 | 0 | 12 | 162 | 0 | 138 | 0 |  | 5539 | 3209 | 8748 | 3433 | 920 | 2035 | 0 | 939 | 1082 | 0 | 0 | 24 | 114 | 201 | 0 | 76.95
15:00 | 0 | 0 | 100 | 180 | 0 | 12 | 0 | 392 | 352 |  | 0 | 320 | 305 | 0 | 17 | 30 | 180 | 0 | 97 | 8 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 23 | 20 | 0 | 16 | 0 | 0 | 0 | 0 | 135 | 0 | 8 | 228 | 0 | 0 | 0 |  | 0 | 8 | 0 | 33 | 0 | 19 | 5 | 0 | 0 | 0 | 0 | 35 | 0 | 182 | 102 | 0 | 51 | 55 | 0 | 43 | 0 | 0 | 0 | 0 | 10 | 25 | 15 | 120 | 35 | 0 | 19 | 1 | 44 | 42 | 50 | 44 | 112 | 0 | 40 | 50 | 0 | 80 | 0 | 0 | 8 | 280 | 8 | 8 | 0 | 15 | 0 | 0 | 45 | 0 | 35 | 0 | 38 | 34 | 40 | 345 | 52 | 0 | 35 | 2 | 15 | 35 | 72 | 0 | 9 | 12 | 400 | 17 | 7 | 17 | 86 | 0 | 0 | 4 | 36 | 17 | 330 | 0 | 0 |  | 900 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 820 | 0 | 0 | 0 | 1 | 10 | 0 | 0 | 0 | 0 | 11 | 160 | 0 | 14 | 0 |  | 5738 | 3236 | 8974 | 3691 | 900 | 2168 | 0 | 887 | 1150 | 0 | 0 | 8 | 120 | 50 | 0 | 76.93
16:00 | 0 | 0 | 100 | 180 | 0 | 12 | 0 | 376 | 352 |  | 0 | 320 | 296 | 0 | 17 | 30 | 180 | 0 | 97 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 23 | 26 | 0 | 31 | 0 | 0 | 0 | 0 | 135 | 0 | 8 | 228 | 0 | 0 | 0 |  | 0 | 8 | 0 | 33 | 0 | 19 | 5 | 0 | 0 | 0 | 0 | 50 | 0 | 181 | 102 | 0 | 44 | 55 | 0 | 43 | 0 | 0 | 0 | 0 | 11 | 30 | 15 | 110 | 35 | 0 | 17 | 0 | 43 | 42 | 50 | 44 | 112 | 0 | 40 | 50 | 0 | 80 | 0 | 0 | 8 | 270 | 8 | 8 | 0 | 15 | 0 | 0 | 45 | 0 | 35 | 3 | 50 | 34 | 10 | 356 | 52 | 0 | 51 | 1 | 15 | 35 | 80 | 0 | 10 | 12 | 400 | 17 | 6 | 17 | 89 | 0 | 0 | 2 | 51 | 17 | 330 | 0 | 0 |  | 905 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 34 | 0 | 3 | 0 | 870 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 11 | 161 | 0 | 38 | 0 |  | 5742 | 3246 | 8988 | 3710 | 905 | 2128 | 0 | 861 | 1201 | 0 | 0 | 8 | 110 | 65 | 0 | 76.93
17:00 | 0 | 0 | 100 | 180 | 0 | 12 | 0 | 381 | 310 |  | 0 | 320 | 306 | 0 | 17 | 30 | 180 | 0 | 59 | 8 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 22 | 23 | 27 | 33 | 28 | 16 | 0 | 0 | 0 | 135 | 0 | 8 | 231 | 0 | 0 | 0 |  | 0 | 8 | 0 | 44 | 0 | 19 | 5 | 0 | 0 | 0 | 0 | 105 | 0 | 183 | 102 | 0 | 47 | 55 | 0 | 43 | 0 | 0 | 0 | 0 | 11 | 33 | 15 | 108 | 47 | 0 | 17 | 0 | 43 | 42 | 50 | 44 | 112 | 0 | 40 | 50 | 0 | 80 | 0 | 0 | 8 | 270 | 8 | 8 | 0 | 15 | 0 | 0 | 45 | 0 | 36 | 1 | 50 | 34 | 15 | 375 | 52 | 2 | 51 | 0 | 15 | 35 | 91 | 0 | 26 | 12 | 400 | 17 | 1 | 17 | 89 | 0 | 0 | 0 | 59 | 17 | 330 | 0 | 0 |  | 904 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 34 | 0 | 1 | 0 | 880 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 162 | 0 | 3 | 0 |  | 5917 | 3105 | 9022 | 3789 | 904 | 2029 | 0 | 931 | 1212 | 0 | 0 | 40 | 108 | 9 | 0 | 76.92
18:00 | 0 | 0 | 100 | 180 | 0 | 12 | 0 | 383 | 310 |  | 0 | 320 | 309 | 0 | 19 | 30 | 180 | 0 | 59 | 8 | 8 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 25 | 22 | 23 | 27 | 33 | 29 | 33 | 0 | 0 | 0 | 135 | 0 | 8 | 228 | 0 | 0 | 0 |  | 5 | 11 | 12 | 44 | 0 | 19 | 5 | 0 | 0 | 0 | 0 | 195 | 0 | 182 | 102 | 0 | 51 | 55 | 0 | 43 | 0 | 0 | 3 | 0 | 11 | 33 | 15 | 120 | 51 | 0 | 17 | 0 | 43 | 42 | 50 | 47 | 80 | 0 | 40 | 86 | 0 | 80 | 0 | 0 | 8 | 275 | 8 | 8 | 0 | 25 | 0 | 0 | 53 | 0 | 42 | 0 | 50 | 50 | 31 | 355 | 75 | 24 | 51 | 0 | 15 | 35 | 92 | 9 | 38 | 12 | 340 | 23 | 0 | 17 | 89 | 0 | 0 | 0 | 86 | 19 | 330 | 0 | 0 |  | 905 | 0 | 250 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 10 | 0 | 36 | 0 | 0 | 35 | 880 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 6199 | 3182 | 9381 | 3795 | 905 | 2050 | 0 | 1211 | 1213 | 0 | 0 | 87 | 120 | 0 | 0 | 76.92
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.05
19:00 | 0 | 0 | 90 | 180 | 0 | 12 | 0 | 352 | 277 |  | 0 | 320 | 285 | 4 | 47 | 15 | 150 | 0 | 0 | 14 | 8 | 64 | 0 | 0 | 0 | 0 | 40 | 2 | 12 | 0 | 23 | 20 | 33 | 16 | 33 | 0 | 0 | 0 | 135 | 0 | 8 | 222 | 0 | 0 | 0 |  | 6 | 8 | 51 | 44 | 1 | 19 | 5 | 0 | 0 | 0 | 0 | 315 | 0 | 182 | 102 | 0 | 48 | 55 | 0 | 43 | 0 | 0 | 8 | 0 | 11 | 33 | 15 | 102 | 57 | 0 | 17 | 0 | 43 | 42 | 50 | 47 | 80 | 0 | 66 | 86 | 0 | 80 | 0 | 0 | 8 | 250 | 8 | 8 | 0 | 15 | 0 | 0 | 45 | 0 | 82 | 0 | 100 | 51 | 80 | 354 | 104 | 52 | 51 | 0 | 15 | 35 | 92 | 0 | 24 | 12 | 325 | 30 | 0 | 75 | 89 | 0 | 0 | 0 | 95 | 35 | 280 | 0 | 0 |  | 869 | 0 | 250 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 36 | 22 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 1 | 0 | 70 | 0 | 78 | 0 | 0 | 70 | 900 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 |  | 6293 | 3382 | 9675 | 3711 | 869 | 1956 | 0 | 1613 | 1231 | 0 | 0 | 193 | 102 | 0 | 0 | 76.9
19:30 | 0 | 0 | 100 | 180 | 0 | 12 | 0 | 305 | 277 |  | 0 | 320 | 286 | 9 | 30 | 0 | 150 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 0 | 23 | 20 | 33 | 29 | 0 | 0 | 0 | 0 | 140 | 0 | 8 | 222 | 0 | 0 | 0 |  | 6 | 7 | 51 | 35 | 0 | 19 | 5 | 0 | 0 | 0 | 0 | 335 | 0 | 181 | 102 | 0 | 45 | 55 | 0 | 43 | 0 | 0 | 8 | 0 | 11 | 33 | 0 | 102 | 74 | 0 | 17 | 0 | 43 | 42 | 50 | 47 | 80 | 0 | 66 | 86 | 0 | 80 | 0 | 0 | 8 | 250 | 8 | 8 | 0 | 0 | 0 | 0 | 45 | 0 | 45 | 0 | 100 | 17 | 50 | 355 | 113 | 17 | 51 | 0 | 15 | 35 | 92 | 0 | 26 | 12 | 294 | 0 | 0 | 17 | 89 | 0 | 0 | 0 | 72 | 35 | 280 | 0 | 0 |  | 834 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 36 | 22 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 4 | 0 | 70 | 0 | 98 | 0 | 0 | 35 | 1000 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 |  | 5904 | 3398 | 9302 | 3658 | 834 | 1963 | 0 | 1259 | 1330 | 0 | 0 | 156 | 102 | 0 | 0 | 0
20:00 | 0 | 0 | 100 | 180 | 0 | 12 | 0 | 314 | 309 |  | 0 | 320 | 297 | 0 | 5 | 0 | 150 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 0 | 0 | 0 | 33 | 30 | 0 | 0 | 0 | 0 | 140 | 0 | 8 | 227 | 0 | 0 | 0 |  | 6 | 6 | 51 | 10 | 0 | 19 | 5 | 0 | 0 | 0 | 0 | 365 | 0 | 165 | 55 | 0 | 50 | 55 | 0 | 43 | 0 | 0 | 8 | 0 | 8 | 33 | 0 | 96 | 76 | 0 | 17 | 0 | 43 | 42 | 50 | 47 | 80 | 0 | 66 | 86 | 0 | 79 | 0 | 0 | 8 | 270 | 8 | 8 | 0 | 0 | 0 | 0 | 16 | 0 | 42 | 0 | 60 | 17 | 50 | 356 | 115 | 17 | 51 | 0 | 15 | 35 | 92 | 0 | 8 | 12 | 400 | 0 | 0 | 0 | 89 | 0 | 0 | 0 | 54 | 35 | 280 | 0 | 0 |  | 833 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 70 | 0 | 88 | 0 | 0 | 0 | 1020 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 |  | 5792 | 3327 | 9119 | 3774 | 833 | 1983 | 0 | 1009 | 1351 | 0 | 0 | 73 | 96 | 0 | 0 | 0
21:00 | 0 | 0 | 90 | 180 | 0 | 12 | 0 | 372 | 352 |  | 0 | 430 | 305 | 0 | 0 | 0 | 150 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 228 | 0 | 0 | 0 |  | 6 | 0 | 0 | 10 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 153 | 8 | 0 | 51 | 54 | 0 | 43 | 0 | 0 | 0 | 0 | 11 | 33 | 21 | 106 | 86 | 0 | 17 | 0 | 44 | 42 | 52 | 47 | 80 | 0 | 65 | 86 | 0 | 80 | 0 | 0 | 8 | 280 | 8 | 8 | 0 | 0 | 0 | 0 | 16 | 0 | 19 | 0 | 60 | 17 | 10 | 374 | 85 | 17 | 17 | 0 | 0 | 17 | 68 | 0 | 8 | 12 | 400 | 0 | 0 | 0 | 89 | 0 | 0 | 0 | 17 | 17 | 280 | 0 | 0 |  | 833 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 |  | 5690 | 3278 | 8968 | 3889 | 833 | 2163 | 0 | 608 | 1369 | 0 | 0 | 0 | 106 | 0 | 0 | 76.9
22:00 | 0 | 0 | 100 | 180 | 0 | 12 | 0 | 401 | 352 |  | 0 | 430 | 290 | 0 | 0 | 0 | 150 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 15 | 18 | 0 | 32 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 228 | 0 | 0 | 0 |  | 6 | 0 | 0 | 10 | 0 | 19 | 5 | 0 | 0 | 0 | 0 | 285 | 0 | 186 | 8 | 0 | 51 | 53 | 0 | 43 | 0 | 0 | 0 | 0 | 11 | 33 | 21 | 94 | 86 | 0 | 17 | 0 | 43 | 42 | 52 | 50 | 80 | 0 | 66 | 86 | 0 | 80 | 0 | 0 | 8 | 285 | 8 | 8 | 0 | 0 | 0 | 0 | 16 | 0 | 17 | 0 | 60 | 17 | 10 | 364 | 85 | 17 | 17 | 0 | 0 | 17 | 68 | 0 | 8 | 0 | 400 | 0 | 0 | 0 | 89 | 0 | 0 | 0 | 17 | 17 | 280 | 0 | 0 |  | 833 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 5677 | 3278 | 8955 | 3910 | 833 | 2151 | 0 | 594 | 1373 | 0 | 0 | 0 | 94 | 0 | 0 | 76.9
23:00 | 0 | 0 | 100 | 180 | 0 | 12 | 0 | 395 | 352 |  | 0 | 430 | 295 | 0 | 0 | 0 | 150 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 20 | 16 | 10 | 32 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 228 | 0 | 0 | 0 |  | 6 | 0 | 0 | 10 | 0 | 19 | 5 | 0 | 0 | 0 | 0 | 285 | 0 | 195 | 8 | 0 | 51 | 54 | 0 | 51 | 0 | 0 | 0 | 0 | 11 | 33 | 21 | 92 | 83 | 0 | 17 | 0 | 43 | 42 | 52 | 50 | 80 | 0 | 66 | 86 | 0 | 80 | 0 | 0 | 8 | 270 | 8 | 8 | 0 | 0 | 0 | 0 | 16 | 0 | 17 | 0 | 60 | 17 | 0 | 352 | 85 | 0 | 17 | 0 | 0 | 17 | 68 | 0 | 8 | 0 | 400 | 0 | 0 | 0 | 89 | 0 | 0 | 0 | 17 | 0 | 280 | 0 | 0 |  | 834 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 |  | 5613 | 3000 | 8613 | 3878 | 834 | 2096 | 0 | 463 | 1250 | 0 | 0 | 0 | 92 | 0 | 0 | 76.89
24:00 | 0 | 0 | 100 | 180 | 0 | 13 | 0 | 395 | 352 |  | 0 | 370 | 285 | 0 | 0 | 0 | 150 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 20 | 27 | 25 | 32 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 229 | 0 | 0 | 0 |  | 6 | 0 | 0 | 10 | 0 | 19 | 5 | 0 | 0 | 0 | 0 | 285 | 0 | 181 | 8 | 0 | 51 | 30 | 0 | 5 | 0 | 0 | 0 | 0 | 11 | 33 | 21 | 92 | 83 | 0 | 16 | 0 | 43 | 43 | 52 | 50 | 80 | 0 | 40 | 40 | 0 | 80 | 0 | 0 | 8 | 260 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 17 | 0 | 352 | 85 | 0 | 17 | 0 | 0 | 0 | 65 | 0 | 8 | 0 | 400 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 17 | 0 | 250 | 0 | 0 |  | 903 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 |  | 5321 | 2959 | 8280 | 3838 | 903 | 1899 | 0 | 406 | 1142 | 0 | 0 | 0 | 92 | 0 | 0 | 76.89
KWH | 0 | 0 | 2368344 | 4410000 | 0 | 724500 | 0 | 9201670 | 7668000 |  | 0 | 8932250 | 7311156 | 9600 | 223914 | 269438 | 4077693 | 0 | 1305000 | 74698 | 198144 | 289920 | 0 | 0 | 0 | 0 | 303840 | 363182 | 269788 | 260028 | 552000 | 405720 | 510700 | 640300 | 322560 | 0 | 267060 | 0 | 3200000 | 0 | 67741 | 5358912 | 0 | 0 | 0 |  | 42480 | 55920 | 203865 | 588000 | 1920 | 417120 | 110112 | 22560 | 0 | 0 | 0 | 4925000 | 0 | 4626000 | 1170909 | 0 | 1189872 | 1221120 | 0 | 893506 | 0 | 0 | 29122 | 87192 | 227700 | 598200 | 359630 | 2553600 | 1433280 | 0 | 419040 | 4800 | 1033000 | 968400 | 1177800 | 1050264 | 2132100 | 0 | 1141440 | 1551360 | 0 | 2287200 | 0 | 0 | 193500 | 6779500 | 190608 | 147500 | 0 | 2007272 | 0 | 0 | 732000 | 0 | 505296 | 6615 | 1179840 | 672000 | 620582 | 6219000 | 1215600 | 474240 | 909959 | 10336 | 323673 | 516897 | 1545593 | 90060 | 330120 | 432960 | 8935200 | 432960 | 81580 | 253440 | 2003509 | 0 | 3240 | 33121 | 1054080 | 337680 | 7858300 | 0 | 0 |  | 20901818 | 0 | 6499296 | 0 | 25920 | 0 | 0 | 0 | 0 | 0 | 0 | 4022719 | 369600 | 0 | 0 | 0 | 0 | 0 | 11030 | 31008 | 0 | 0 | 0 | 0 | 44663 | 394320 | 0 | 203472 | 0 | 0 | 4310800 | 0 | 0 | 4134800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7934581 | 10080 | 0 | 650976 | 0 | 721267 | 0 | 5088 | 102720 | 20298500 | 0 | 0 | 0 | 12780 | 315360 | 150336 | 0 | 0 | 0 | 70180 | 3840000 | 3309091 | 373680 | 0 |  | 138204931 | 78744085 | 216949016 | 89907328 | 20901818 | 49527026 | 0 | 20483847 | 31758391 | 267060 | 0 | 636406 | 2553600 | 913540 | 0
Fuel Cost | 0 | 0 | 3457782.24 | 6570900 | 0 | 963585 | 0 | 9661753.5 | 8281440 |  | 0 | 9736152.5 | 8115383.16 | 107328 | 2966860.5 | 3570053.5 | 4567016.16 | 0 | 2283750 | 1092084.76 | 2787886.08 | 4699603.2 | 0 | 0 | 0 | 0 | 3864844.8 | 4902957 | 3617857.08 | 195021 | 414000 | 0 | 0 | 0 | 5486745.6 | 0 | 72106.2 | 0 | 6048000 | 0 | 1107565.35 | 5573268.48 | 0 | 0 | 0 |  | 554364 | 932745.6 | 3469782.3 | 7943880 | 24345.6 | 4826078.4 | 139842.24 | 75124.8 | 0 | 0 | 0 | 5466750 | 0 | 5366160 | 1510472.61 | 0 | 1344555.36 | 1819468.8 | 0 | 1492155.02 | 0 | 0 | 391690.9 | 119453.04 | 170775 | 1046850 | 269722.5 | 18334848 | 1562275.2 | 0 | 569894.4 | 76512 | 1415210 | 1278288 | 2049372 | 1816956.72 | 2451915 | 0 | 2214393.6 | 3537100.8 | 0 | 2310072 | 0 | 0 | 383130 | 6779500 | 142956 | 112100 | 0 | 27399262.8 | 0 | 0 | 9867360 | 0 | 6998349.6 | 77329.35 | 12175948.8 | 9179520 | 8235123.14 | 5721480 | 14781696 | 6857510.4 | 11510981.35 | 0 | 3799921.02 | 5629008.33 | 16429653.59 | 1222114.2 | 4255246.8 | 5100268.8 | 8220384 | 5606832 | 1178831 | 3216153.6 | 22799932.42 | 0 | 42314.4 | 395795.95 | 15779577.6 | 4447245.6 | 0 | 0 | 0 |  | 62705454 | 0 | 7279211.52 | 0 | 269827.2 | 0 | 0 | 0 | 0 | 0 | 0 | 4505445.28 | 717024 | 0 | 0 | 0 | 0 | 0 | 192914.7 | 484965.12 | 0 | 0 | 0 | 0 | 753464.81 | 816242.4 | 0 | 154028.304 | 0 | 0 | 22804132 | 0 | 0 | 4796368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7855235.19 | 135475.2 | 0 | 7701046.08 | 0 | 9160090.9 | 0 | 56222.4 | 1247020.8 | 182889485 | 0 | 0 | 0 | 144541.8 | 3699172.8 | 2304650.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 393070524.75 | 320672018.384 | 713742543.134 | 92977705.824 | 62705454 | 58400258 | 0 | 259396673.08 | 205693617 | 72106.2 | 0 | 10533475.73 | 18334848 | 5628405.3 | 0
Yesterday Day Peak | 0 | 0 | 100 | 180 | 0 | 12 | 0 | 344 | 307 |  | 0 | 360 | 310 | 0 | 34 | 30 | 140 | 0 | 102 | 8 | 24 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 23 | 0 | 33 | 0 | 24 | 0 | 0 | 0 | 135 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 0 | 0 | 22 | 0 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 102 | 0 | 51 | 35 | 0 | 39 | 0 | 0 | 0 | 0 | 10 | 0 | 15 | 124 | 44 | 0 | 19 | 0 | 43 | 42 | 31 | 30 | 112 | 0 | 64 | 50 | 0 | 79 | 0 | 0 | 8 | 300 | 8 | 0 | 0 | 15 | 0 | 0 | 10 | 0 | 23 | 0 | 38 | 34 | 40 | 353 | 28 | 17 | 51 | 0 | 15 | 26 | 43 | 0 | 9 | 23 | 360 | 16 | 13 | 17 | 57 | 0 | 0 | 1 | 35 | 15 | 330 | 0 | 0 |  | 893 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 169 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268 | 0 | 0 | 38 | 0 | 35 | 0 | 0 | 0 | 630 | 0 | 0 | 0 | 2 | 74 | 0 | 0 | 0 | 0 | 7 | 162 | 238 | 74 | 0 |  | 8684 | DayPeak
Yesterday Evening Peak | 0 | 0 | 90 | 180 | 0 | 12 | 0 | 352 | 277 | 0 | 0 | 320 | 285 | 4 | 47 | 15 | 150 | 0 | 0 | 14 | 8 | 64 | 0 | 0 | 0 | 0 | 40 | 2 | 12 | 0 | 23 | 20 | 33 | 16 | 33 | 0 | 0 | 0 | 135 | 0 | 8 | 222 | 0 | 0 | 0 | 0 | 6 | 8 | 51 | 44 | 1 | 19 | 5 | 0 | 0 | 0 | 0 | 315 | 0 | 182 | 102 | 0 | 48 | 55 | 0 | 43 | 0 | 0 | 8 | 0 | 11 | 33 | 15 | 102 | 57 | 0 | 17 | 0 | 43 | 42 | 50 | 47 | 80 | 0 | 66 | 86 | 0 | 80 | 0 | 0 | 8 | 250 | 8 | 8 | 0 | 15 | 0 | 0 | 45 | 0 | 82 | 0 | 100 | 51 | 80 | 354 | 104 | 52 | 51 | 0 | 15 | 35 | 92 | 0 | 24 | 12 | 325 | 30 | 0 | 75 | 89 | 0 | 0 | 0 | 95 | 35 | 280 | 0 | 0 |  | 869 | 0 | 250 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 36 | 22 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 1 | 0 | 70 | 0 | 78 | 0 | 0 | 70 | 900 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 |  | 9675 | EvPeak
Forecast for Evening | 0 | 0 | 100 | 180 | 0 | 0 | 0 | 400 | 300 | 0 | 0 | 450 | 310 | 0 | 85 | 55 | 220 | 0 | 60 | 90 | 92 | 115 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 23 | 28 | 33 | 33 | 50 | 0 | 25 | 0 | 135 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 6 | 40 | 65 | 54 | 0 | 19 | 5 | 0 | 0 | 0 | 0 | 330 | 0 | 210 | 8 | 0 | 50 | 55 | 0 | 43 | 0 | 35 | 8 | 21 | 10 | 33 | 21 | 153 | 65 | 0 | 19 | 0 | 44 | 43 | 51 | 47 | 112 | 0 | 65 | 86 | 0 | 80 | 0 |  | 8 | 300 | 8 | 8 |  | 300 | 0 | 0 | 180 | 0 | 149 | 0 | 100 | 100 | 135 | 368 | 104 | 100 | 51 | 0 | 225 | 35 | 92 | 17 | 113 | 90 | 400 | 90 | 0 | 162 | 90 | 0 | 54 |  | 94 | 17 | 330 |  |  |  | 916 | 0 | 300 |  | 99 | 0 | 0 | 0 | 40 | 65 | 40 | 170 | 22 | 48 | 0 | 0 | 0 | 32 | 32 | 85 | 0 | 42 | 40 | 8 | 35 | 20 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 150 |  | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 40 | 0 | 94 | 100 | 106 | 0 | 0 | 113 | 1230 | 0 |  | 0 |  |  | 72 | 0 |  | 0 |  | 307 | 260 |  | 0
Forecast for Day | 0 | 0 | 100 | 180 | 0 | 0 | 0 | 400 | 300 | 0 | 0 | 450 | 310 | 0 | 85 | 55 | 220 | 0 | 50 | 90 | 75 | 82 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 22 | 23 | 26 | 33 | 33 | 50 | 0 | 25 | 0 | 135 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 0 | 40 | 51 | 54 | 0 | 19 | 5 | 0 | 0 | 0 | 0 | 330 | 0 | 210 | 8 | 0 | 50 | 55 | 0 | 43 | 0 | 0 | 0 | 21 | 10 | 33 | 15 | 135 | 44 | 0 | 19 | 1.6 | 44 | 43 | 51 | 47 | 80 | 0 | 65 | 86 | 0 | 80 | 0 | 0 | 8 | 300 | 8 | 8 | 0 | 280 | 0 | 0 | 165 | 0 | 36 | 20 | 50 | 100 | 40 | 366 | 90 | 52 | 34 | 5 | 120 | 17 | 54 | 17 | 9 | 60 | 400 | 55 | 50 | 90 | 90 | 0 | 17 | 30 | 36 | 17 | 330 |  |  |  | 916 | 0 | 300 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 8 | 171 | 15 | 0 | 0 | 0 | 0 | 0 | 18 | 50 | 0 | 42 | 32 | 0 | 26 | 20 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 35 | 0 | 70 | 0 | 70 | 0 | 8 | 70 | 1000 | 0 |  | 0 | 6 | 100 | 0 | 0 |  | 0 | 30 | 152 | 260 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 100 | 180 | 0 | 0 | 0 | 398 | 352 | 0 | 0 | 370 | 315 | 0 | 0 | 0 | 180 | 0 | 41 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 26 | 0 | 32 | 17 | 0 | 0 | 0 | 135 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 19 | 5 | 0 | 0 | 0 | 0 | 345 | 0 | 212 | 8 | 0 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 16 | 82 | 44 | 0 | 0 | 1 | 44 | 42 | 7 | 5 | 80 | 0 | 52 | 5 | 0 | 80 | 0 | 0 | 8 | 295 | 8 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 16 | 4 | 10 | 17 | 0 | 371 | 47 | 0 | 17 | 2 | 0 | 0 | 17 | 0 | 0 | 0 | 400 | 0 | 20 | 0 | 89 | 0 | 0 | 2 | 26 | 0 | 330 | 0 | 0 | 0 | 804 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 2 | 41 | 0 | 0 | 0 | 0 | 1 | 154 | 181 | 37 | 0 | 0 |  |  |  | 139.4344 | 20.9018 | 21.1203 | 31.7584 | 0.26706 | 2.5536 | 0.91354
216.949
| Minimum Generation |  | 7822 | 9:00
| Highest Generation |  | 9848 | 1:00
| Day Peak Generation |  | 8684 | 12:00
| Evening Peak Generation |  | 9675 | 19:00
| HVDC Max Flow |  | 920 | 14:00
| HVDC EvPeak Flow |  | 869 | 19:00
| Load factor L.F |  | 91.79% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-03-20
Till now the maximum generation is : - |  |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  |  | 2023-03-19 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 8684 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6507
Evening Peak Generation : |  |  | 9675 | MW Hour : | 19:00 | Available Max Generation : |  | 13735
E.P. Demand (at gen end) : |  |  | 9675 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 11500
Maximum Generation : |  |  | 9848 | MW Hour : | 1:00 | Reserve(Generation end) |  | 2235
Total Gen. (MKWH) : |  |  | 216.949 | System Load Factor : | 91.79% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | -92 | MW at | 8:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-03-20
Actual : |  | 76.87 | Ft.(MSL) , | Rule curve : | 89.96 | Ft.( MSL )
Gas Consumed : |  | Total = | 1062.75 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 151377963.824
: |  |  | Coal : | 205693617 | Oil : | 269930148.81 | Total : | 627001729.634
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3948.8334 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1090.4778 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1432.9418 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1263.6312 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1079.1812 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 886.6511 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 401.0597 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 323.2277 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 700.1211 |  |  | 0 | 0%
Total |  | 0 |  | 11126.125 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
[5 empty] | 1) Barapukuria ST: Unit- 1,2 | 10) Bhula Nuton Biddut
2) Ghorasal-3,7
3) Ashuganj-5
4) Baghabari-100 MW & 71 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj-1 & 2
9) Kushiara 163 MW ST
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
- | 8:10 | Niamatpur 132/33kV S/S 417T LT is restored.
8:10 | - | Ashuganj (NCR) all shunt reactors are in service.
- | 8:10 | Niamatpur 132/33kV S/S 407T LT is restored.
8:45 | - | Ashuganj North 360MW tripped due to Auxiliary supply fail. | [5 empty] | 280MW generation interrup.
8:47 | 8:58 | Brahmanbaria-Narsinghdi 132 kV Ckt-1 Tripped from Narshingdi 132/33kV end showing ABB, REL670 relays Due to Stormy weather.
9:22 | 10:17 | Madanganj 132/33kV S/S Madanganj-Fatullah 132KV Ckt Forced S/D Due to 132 kv Haripur-1 & Haripur-2 Ckt Overload.
10:44 | 14:58 | Bhulta 132/33kV S/S GT1 HT Tripped showing VAJ Relay relays Due to Undefined.
11:02 | 13:22 | Shahjadpur 132/33kV S/S T-1(405T) HT Forced S/D Due to 33 kV incoming Ds flashing.
12:21 | 13:54 | Narshingdi 132/33kV S/S T-2 LT Scheduled S/D Due to Relay Maintenance by ABB India.
12:22 | 13:47 | Narshingdi 132/33kV S/S T-2 HT Scheduled S/D Due to Relay Maintenance by ABB India.
- | 12:37 | Ashuganj North 360MW GT was sync.
13:19 | 16:24 | Cumilla(S) 132/33kV S/S TR-1 LT Project Work S/D.
13:20 | 16:23 | Cumilla(S) 132/33kV S/S TR-1 HT Project Work S/D.
13:39 | - | Adani Power Jharkhand Ltd. Unit-1 tripped. | [5 empty] | 330MW generation interrup.
13:51 | 14:05 | Faridpur 132/33kV S/S Transformer-1 HT Tripped showing Lockout relays. | [5 empty] | 72.0MW load interrup.
13:51 | 14:03 | Faridpur 132/33kV S/S Transformer-2 HT Tripped showing Lockout relays. | [5 empty] | 72.0MW load interrup.
13:51 | 14:04 | Faridpur 132/33kV S/S Transformer-2 LT Tripped showing MCGG(67) relays Due to Rajbari 33kv wz feeder fault. | [5 empty] | 72.0MW load interrup.
13:51 | 14:06 | Faridpur 132/33kV S/S Transformer-1 LT Tripped showing MCGG(67) relays. | [5 empty] | 72.0MW load interrup.
16:25 | 18:28 | Cumilla(S) 132/33kV S/S TR-2 LT Project Work S/D Due to AVR Test.
16:26 | 18:28 | Cumilla(S) 132/33kV S/S TR-2 HT Project Work S/D Due to AVR Test.
- | 16:44 | Ashuganj North 360MW ST was sync.
- | 17:04 | Sonargaon 132/33kV S/S OPML(IEL-1) is restored.
17:06 | 19:05 | Barishal 230/132kV S/S T-4 LT Scheduled S/D Due to S/D taken by Barishal PBS-2 due to 33 kv Babugang feeder hot spot
repair & maintenance works.
17:08 | 19:03 | Barishal 230/132kV S/S T-4 HT Scheduled S/D Due to S/D taken by Barishal pbs-2.
17:41 | - | Sylhet 132/33kV S/S T4 LT Forced S/D Due to Unexpected sound appear T4A incoming B phase XLPE cable top end.
17:50 | - | Sylhet 132/33kV S/S T4 HT Forced S/D Due to Unexpected sound appear T4A incoming B phase XLPE cable top end.
18:41 | 22:32 | Chandpur 132/33kV S/S 422T LT Tripped showing O/C & E/F relay relays. | [5 empty] | 18.0MW load interrup.
18:41 | 18:53 | Chandpur 132/33kV S/S 402T LT Tripped showing O/C & E/F Relay relays. | [5 empty] | 17.0MW load interrup.
18:59 | 22:07 | Maniknagar-Siddhirganj 230kV Ckt-2 Tripped from Siddhirganj 230/132kV end showing REL-670 relays Due to Zone-1,Distance. | [5 empty] | 170.0MW load interrup.
18:59 | 19:52 | Siddhirganj 132/33kV S/S 120MW EGCB GT1 Tripped showing RED 670 LBB Initiation relays Due to Master trip. | [5 empty] | 36.0MW load interrup.
19:39 | 19:43 | Chattak 132/33kV S/S T-1 LT Tripped showing 86x master trip relay. relays Due to 33kv Sunamganj PDB feeder fault.
20:20 | - | Bogura West 400/230 KV T-3 Shutdown Withdrawal.
20:26 | 22:32 | Chandpur 132/33kV S/S 422T LT Scheduled S/D Due to 33 Kv Bus Maintenance. | [5 empty] | 5.0MW load interrup.
20:26 | 22:30 | Chandpur 132/33kV S/S 422T HT Scheduled S/D Due to 33 Kv Bus Coupler Maintenance. | [5 empty] | 5.0MW load interrup.
0:36 | 0:44 | Barishal-Patuakhali(Barguna T at Bakergonj) 132 kV Ckt Scheduled S/D from Patuakhali 132/33kV end Due to Safety purpose | [5 empty] | 5.0MW load interrup.
due to transport of Transformer when truck crossing the Line.
1:35 | - | Siddhirganj 132/33kV S/S 120MW EGCB GT1 Tripped showing LBB Initiation relays Due to Master trip.
1:37 | - | Maniknagar-Siddhirganj 230kV Ckt-2 Tripped from Siddhirganj 230/132kV end showing REL670 relays Due to zone 1,Distance.
1:37 | - | Maniknagar - Siddhirganj 230kV ckt-2 tripped from Siddhirganj end.
3:00 | 6:42 | Cox'sbazar 132/33kV S/S 405T-T1 HT Project Work S/D Due to G2G project work. | [5 empty] | 40.0MW load interrup.
3:26 | - | Bogura New - Bogura West 230kV ckt-3 tripped from Bogura New end showing AR block.
3:26 | - | Bogura New - Bogura West 230kV ckt-4 tripped from Bogura New end showing AR block.
- | 4:33 | Adani Power Jharkhand Ltd. Unit-1 was sync.
6:01 | - | Thakurgaon 132/33kV T-1 tripped from 33kV side showing EF. | [5 empty] | 11MW load interrup.
6:01 | 7:02 | Thakurgaon 132/33kV T-2 tripped from 33kV side showing EF. | [5 empty] | 11MW load interrup.
6:21 | - | Siddhirganj - Maniknagar 230kv ckt-2 was S/D properly.
6:27 | - | BIPTC S/S 10CF26 Tripped showing 87 relays Due to capacitor unbalance.
6:42 | - | Bogura(New)-Naogaon 132 kV Ckt-1 Project Work S/D from Bogura 230/132kV end Due to Tower Extend work.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-03-19 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 90 | 2368344 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4410000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 724500 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 352 | 9201670 | Frequency control
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 277 | 7668000 | Frequency control
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 320 | 8932250 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 4 | 9600
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 285 | 7311156 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 47 | 223914 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 269438 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 260028 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 1305000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 14 | 74698 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 150 | 4077693 | ST U/M.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 198144 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 40 | 303840 | Low demand
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 64 | 289920 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 2 | 363182 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 12 | 269788 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 43 | 957720 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 510700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 16 | 640300 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 33 | 322560 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 15 | 2007272 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 82 | 505296 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 474240 | Low demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 30 | 432960 | Low demand
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 75 | 253440 | Low demand
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 33121
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 337680 | Fuel shortage
| Dhaka area Total |  |  |  | 5847 | 2286 | 54736454
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 135 | 3200000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 8 | 67741 | Low demand
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 6615
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 417120 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 0 | 267060 | Under shut down
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 222 | 5358912
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 909959 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 8 | 55920 | Low demand
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 203865 | Low demand
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 44 | 588000 | Low demand
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1179840
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 5 | 110112 | Gas shortage
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 0 | 22560
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 1 | 1920 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 10336
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 323673 | Low demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 35 | 516897 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 92 | 1545593 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 432960 | Low demand
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 89 | 2003509 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2382 | 887 | 17222592
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 182 | 4626000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 315 | 4925000 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 280 | 7858300 | FGMO
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 48 | 1189872
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 55 | 1221120
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 102 | 1170909 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 893506 | Engine problem
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 80 | 620582 | Low demand
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Low demand
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 51 | 672000 | Low demand
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 87192
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 227700
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 102 | 2553600
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 598200
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 29122 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 15 | 359630 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Fuel shortage
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 90060 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 24 | 330120 | Low demand
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 0 | 3240 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 95 | 1054080 | Engine problem
| Cumilla Area Total |  |  |  | 3285 | 1444 | 28510233
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 57 | 1433280 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 419040 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 4800
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 45 | 732000 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 104 | 1215600 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 81580
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 42480 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 229 | 3928780
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1033000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 968400 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 80 | 2132100 | ST U/M.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1177800
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 47 | 1050264
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 147500 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 66 | 1141440
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1551360
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 80 | 2287200 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 190608 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 250 | 6779500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 354 | 6219000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 8 | 193500 | Engine problem
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 325 | 8935200
| Sylhet Area Total |  |  |  | 2427 | 1447 | 33806872
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 869 | 20901818
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 25920 | Low demand
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 250 | 6499296 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Low demand
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 1 | 10080 | Low demand
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Transformer O/L
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 315360
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0 | Machine problem
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3001 | 1136 | 27752474
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 11 | 369600 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 170 | 4022719
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 900 | 20298500 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 0 | 0 | Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal 307 MW |  | BCPCL | 307*1 | 307 | 161 | 3840000
| Barisal Area Total |  |  |  | 2265 | 1242 | 28530819
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Low demand
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 11030 | Low demand
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Low demand
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Low demand
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 170 | 4134800 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 308 | 7934581 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 36 | 44663 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 394320
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 203472
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 34 | 31008 | Low demand
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 650976 | Low demand
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 70 | 102720 | Low demand
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 12780
| Adani Power Jharkhanda Ltd |  | Import | 0 | 0 | 0 | 3309091 | On test.
| Rajshahi Area Total |  |  |  | 2129 | 721 | 16829441
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4310800
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 78 | 721267 | Low demand
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 5088
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 35 | 150336 | Low demand
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 70180
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 373680
| Rangpur Area Total |  |  |  | 750 | 283 | 5631351
| Total |  |  |  | 22700 | 9675 | 216949016
| Eastern Grid Total |  |  |  | 14555 | 6293 | 138204931
| Western Grid Total |  |  |  | 8145 | 3382 | 78744085
| National Grid Total |  |  |  | 22700 | 9675 | 216949016
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-03-19
| (a) ENTIRE EASTERN GRID : |  | 6367.2 | MW | (b) ENTIRE WESTERN GRID : |  | 2862.3 | MW
| i) Dhaka area |  | 3432.7 | MW | i) Khulna area |  | 968.8 | MW
| ii) Chittagong area |  | 1162.5 | MW | ii) Rajshahi area |  | 1023.5 | MW
| iii) Comilla area |  | 653 | MW | iii) Barisal area |  | 166 | MW
| iv) Mymensingh area |  | 769 | MW | iv) Rangpur area |  | 704 | MW
| v) Sylhet area |  | 350 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 9229.5 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 17 | 00:00 | Kamrangirchar | 55 | 13:00 | Natore | 94 | 21:00 | Shitalakhya | 117 | 11:00
2 | AKSML | 96 | 02:00 | Chowmuhani | 138 | 18:30 | Kaptai | 3 | 18:00 | Nawabganj | 29 | 00:00 | Sholosohor | 26 | 18:30
3 | Aftabnagar | 27 | 14:00 | Chuadanga | 69 | 19:00 | Kazla | 67 | 23:00 | Netrakona | 92 | 00:00 | Shyampur | 166 | 09:00
4 | Agargaon | 65 | 10:00 | Coxsbazar | 107 | 00:00 | Keranigonj | 54 | 13:00 | New | 63 | 11:00 | Siddhirganj | 90 | 10:00
5 | Agrabad | 52 | 18:00 | Cumilla(N) | 117 | 00:00 | Khagrachori | 24 | 19:00 | Niamatpur | 66 | 13:00 | Sirajganj | 82 | 19:30
6 | Amnura | 64 | 07:00 | Cumilla(S) | 135 | 00:00 | Khulna | 81 | 17:00 | Noapara | 33.5 | 22:00 | Sonargaon | 93 | 00:00
7 | Ashuganj | 55 | 00:00 | Daudkandi | 104 | 00:00 | Khulshi | 162 | 19:30 | PHP | 9 | 19:00 | Sreemongol | 37 | 00:00
8 | BIPTC | N/A | N/A | Dhaka | 36 | 13:00 | Kishoreganj | 108 | 00:00 | Pabna | 83 | 19:00 | Srinagar | 29.71 | 21:00
9 | BSRM | 111 | 11:00 | Dhamrai | 96 | 15:00 | Kodda | 265 | 17:00 | Palashbari | 90 | 00:00 | Sunamganj | 34 | 19:30
10 | Bagerhat | 57 | 00:00 | Dhanmondi | 115.7 | 13:00 | Kulaura | 24 | 00:00 | Panchagarh | 40 | 19:00 | Sylhet | 96 | 18:30
11 | Bakulia | 80 | 05:00 | Dohazari | 74 | 18:30 | Kurigram | 60 | 11:00 | Patuakhali | 69 | 00:00 | TK | 21 | 18:30
12 | Banani | 35 | 13:00 | Faridpur | 97 | 00:00 | Kushtia | 96 | 19:00 | Payra | 12 | 00:00 | Tangail | 173 | 07:00
13 | Bangabhaban | 18 | 10:00 | Fatullah | 59 | 10:00 | Lalbag | 72 | 13:00 | Postogola | 31 | 00:00 | Thakurgaon | 71 | 19:00
14 | Barapukuria | 43 | 20:00 | Fenchuganj | 33 | 18:30 | Lalmonirhat | 40 | 18:30 | Purbachal | 14 | 00:00 | Tongi | 102 | 11:00
15 | Barguna | 12 | 00:00 | Feni | 97 | 18:30 | Madanganj | 29 | 00:00 | Purbasadipur | 94 | 19:00 | Ullon | 44 | 20:00
16 | Barishal | 80 | 22:00 | GPH | 84 | 04:00 | Madaripur | 67 | 00:00 | Rahanpur_I | 32.4 | 22:00 | Uttara | 65 | 13:00
17 | Barishal-230 | 48 | 00:00 | Ghorashal | 56 | 19:30 | Madartek | 64 | 00:00 | Rahim | 36 | 16:00 | UttaraNew | 18 | 13:00
18 | Baroaulia | 54 | 00:00 | Goalpara | 22 | 13:00 | Madunaghat | 44 | 19:00 | Rajbari | 42 | 19:00 | Zigatola | 64 | 13:00
19 | Baroirhat | 36 | 18:30 | Gollamari | 28 | 13:00 | Magura | 46 | 19:00 | Rajendrapur | 100 | 20:00
20 | Bashundhara | 123 | 13:00 | Gopalganj | 66 | 08:00 | Mahasthangarh | 50 | 00:00 | Rajshahi | 97 | 21:00
21 | BashundharaCement | 0 | 00:00 | Gulshan | 88 | 13:00 | Manikganj | 75 | 08:00 | Rajshahi-230 | 28 | 00:00
22 | Beanibazar | 38 | 18:30 | Halishahar | 84 | 15:00 | Maniknagar | 55 | 13:00 | Ramganj | 72 | 00:00
23 | Benapole | 46 | 07:00 | HaripurSBU | 137 | 02:00 | Matarbari | 35 | 18:30 | Rampur | 28 | 00:00
24 | Bhaluka | 98 | 18:30 | Hasnabad | 79 | 00:00 | Matuail | 62 | 15:00 | Rangamati | 12 | 18:30
25 | Bhandaria | 30 | 00:00 | Hathazari | 46 | 19:00 | Millgate | 68 | 09:00 | Rangpur | 113 | 19:00
26 | Bhangura | 24 | 19:30 | Ishurdi | 53 | 19:30 | Mirpur | 101 | 18:30 | Ruppur | 4.2 | 09:00
27 | Bheramara(GK) | 39 | 18:30 | Jaldhaka | 63 | 18:30 | Mirsorai | 3 | 18:30 | SSM | 0 | 00:00
28 | Bhulta | 236 | 00:00 | Jamalpur | 112 | 00:00 | Mithapukur | 32 | 19:30 | Saidpur | 95 | 18:30
29 | Bog-Sherpur | 60 | 00:00 | Jashore | 104 | 13:00 | Modern | 0 | 00:00 | Satkhira | 81 | 07:00
30 | Bogura | 114 | 00:00 | Jhenaidah | 88 | 08:00 | Mogbazar | 102 | 15:00 | Satmasjid | 77 | 13:00
31 | Borhanuddin | 35 | 00:00 | Joydebpur | 121 | 00:00 | Mongla | 32 | 13:00 | Savar | 150 | 16:00
32 | Brahmanbaria | 128 | 00:00 | Joypurhat | 47 | 00:00 | Motijheel | 30 | 12:00 | Shahjadpur | 85 | 07:00
33 | Cantonment | 102 | 11:00 | Juldah | 25 | 12:00 | Munshiganj | 84 | 19:00 | Shahjibazar | 87 | 00:00
34 | Chandpur | 50 | 00:00 | KSRM | 26.5 | 19:00 | Mymensingh | 170 | 00:00 | Shahmirpur | 40.3 | 00:00
35 | Chandraghona | 22 | 18:30 | Kabirpur | 253 | 12:00 | Naogaon | 99 | 00:00 | Shariatpur | 44 | 00:00
36 | Chapai | 54 | 12:00 | Kachua | 55 | 00:00 | Narail | 36 | 08:00 | Sherpur | 104 | 01:00
37 | Charsaidpur | 48 | 04:00 | Kallyanpur | 69 | 00:00 | Narinda | 58 | 13:00 | Shikalbaha | 29 | 00:00
38 | Chauddagram | 34 | 00:00 | Kalurghat | 28 | 10:00 | Narshingdi | 152 | 00:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-03-19 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 409 | 08:00 | 395 | 00:00 | Kaliakoir | 397 | 08:00 | 390 | 02:00
| Bhulta | 403 | 18:30 | 387 | 15:00 | Madunaghat_I | 408 | 20:00 | 392 | 14:00
| Bibiana | 411 | 20:00 | 398 | 16:00 | Payra | 417 | 05:00 | 408 | 00:00
| BIPTC | 406 | 04:00 | 399 | 13:00 | Rahanpur_I | 424 | 02:00 | 400 | 14:00
| Gopalganj | 422 | 05:00 | 395 | 00:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 238 | 18:30 | 229 | 00:00 | Hasnabad | 239 | 18:30 | 231 | 00:00
| AKSML | 238 | 19:30 | 212 | 11:00 | Hathazari | 238 | 20:00 | 226 | 11:00
| Aminbazar | 239 | 17:00 | 232 | 00:00 | Ishurdi | 239 | 04:00 | 233 | 12:00
| Ashuganj | 246 | 19:30 | 238 | 00:00 | Jhenaidah | 237 | 04:00 | 229 | 12:00
| Baghabari | 235 | 02:00 | 232 | 00:00 | Kaliakoir | 236 | 08:00 | 229 | 00:00
| Barapukuria | 228 | 02:00 | 220 | 14:00 | Keranigonj | 238 | 19:30 | 229 | 00:00
| Barishal | 241 | 18:00 | 233 | 00:00 | Khulna(S) | 244 | 18:00 | 232 | 00:00
| Bheramara | 236 | 04:00 | 229 | 12:00 | Madunaghat_I | 238 | 20:00 | 227 | 01:00
| Bhulta | 239 | 18:30 | 232 | 16:00 | Maniknagar | 237 | 18:30 | 231 | 00:00
| Bibiana | 244 | 18:30 | 236 | 03:00 | Meghnaghat | 240 | 03:00 | 236 | 15:00
| BIPTC | 239 | 06:00 | 231 | 12:00 | Mirsorai | 235 | 10:00 | 219 | 17:00
| Bogura | 234 | 05:00 | 226 | 14:00 | Rajshahi | 238 | 23:00 | 228 | 12:00
| Borhanuddin | 243 | 18:30 | 235 | 00:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 238 | 20:00 | 226 | 05:00 | Rampura | 238 | 19:00 | 230 | 16:00
| Cumilla(N) | 239 | 18:30 | 229 | 01:00 | Shikalbaha | 234 | 10:00 | 223 | 06:00
| Fenchuganj | 247 | 08:00 | 242 | 00:00 | Shyampur | 239 | 19:00 | 232 | 14:00
| Ghorashal | N/A | N/A | N/A | N/A | Siddhirganj | 240 | 18:30 | 233 | 00:00
| GPH | 234 | 10:00 | 222 | 06:00 | Sirajgonj | 234 | 19:30 | 230 | 00:00
| Haripur | 238 | 19:00 | 231 | 12:00 | Tongi | 232 | 20:00 | 223 | 11:00
| 132 kV | KV |  | KV
| Aftabnagar | 138 | 04:00 | 133 | 12:00 | Lalbag | 137 | 18:30 | 132 | 00:00
| Agargaon | 138 | 19:30 | 132 | 00:00 | Lalmonirhat | 138 | 04:00 | 126 | 12:00
| Agrabad | 135 | 10:00 | 128 | 04:00 | Madanganj | 137 | 19:00 | 131 | 00:00
| AKS | 134 | 10:00 | 126 | 05:00 | Madaripur | 136 | 18:30 | 131 | 00:00
| Aminbazar | 138 | 17:00 | 132 | 00:00 | Madartek | 137 | 08:00 | 131 | 14:00
| Amnura | 136 | 23:00 | 129 | 00:00 | Madunaghat | 138 | 19:30 | 129 | 06:00
| Ashuganj | 140 | 08:00 | 136 | 00:00 | Magura | 139 | 17:00 | 133 | 12:00
| Bagerhat | 138 | 17:00 | 128 | 14:00 | Mahasthangarh | 138 | 03:00 | 131 | 14:00
| Bakulia | 136 | 10:00 | 126 | 06:00 | Manikganj | 138 | 18:30 | 130 | 12:00
| Banani | 139 | 08:00 | 132 | 13:00 | Maniknagar | 136 | 08:00 | 133 | 00:00
| Bangabhaban | 137 | 18:30 | 133 | 00:00 | Matarbari | 135 | 10:00 | 116 | 04:00
| Barapukuria | 139 | 02:00 | 132 | 15:00 | Matuail | 138 | 18:30 | 133 | 00:00
| Barguna | 131 | 18:00 | 125 | 04:00 | Millgate | 138 | 08:00 | 132 | 10:00
| Barishal | 136 | 18:30 | 130 | 00:00 | Mirpur | 138 | 18:30 | 130 | 00:00
| Barishal-230 | 138 | 18:30 | 131 | 00:00 | Mithapukur | 139 | 04:00 | 129 | 13:00
| Baroaulia | 140 | 20:00 | 129 | 06:00 | Modern | 138 | 20:00 | 130 | 12:00
| Baroirhat | 138 | 08:00 | 126 | 05:00 | Mogbazar | 139 | 08:00 | 133 | 15:00
| Bashundhara | 140 | 08:00 | 133 | 00:00 | Mongla | 138 | 18:00 | 128 | 00:00
| BashundharaCement | 137 | 19:00 | 131 | 00:00 | Motijheel | 137 | 18:30 | 133 | 00:00
| Beanibazar | 138 | 08:00 | 133 | 00:00 | Munshiganj | 138 | 18:30 | 132 | 00:00
| Benapole | 137 | 18:00 | 128 | 12:00 | Mymensingh | 138 | 05:00 | 121 | 11:00
| Bhaluka | 136 | 08:00 | 116 | 11:00 | Naogaon | 135 | 02:00 | 127 | 14:00
| Bhandaria | 140 | 18:00 | 127 | 00:00 | Narail | 139 | 18:00 | 124 | 07:00
| Bhangura | 142 | 04:00 | 136 | 00:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 137 | 03:00 | 137 | 04:00 | Narshingdi | 138 | 10:00 | 127 | 00:00
| Bheramara(GK) | 139 | 04:00 | 135 | 14:00 | Natore | 137 | 03:00 | 131 | 14:00
| Bhulta | 134 | 11:00 | 126 | 00:00 | Nawabganj | 138 | 19:00 | 131 | 00:00
| Bog-Sherpur | 139 | 03:00 | 132 | 17:00 | Netrakona | 136 | 08:00 | 118 | 18:00
| Bogura | 139 | 03:00 | 132 | 14:00 | New | 140 | 08:00 | 133 | 12:00
| Bogura-230 | 137 | 05:00 | 132 | 01:00 | Niamatpur | 132 | 19:30 | 123 | 13:00
| Brahmanbaria | 136 | 08:00 | 131 | 17:00 | Noapara | 138 | 18:00 | 131 | 12:00
| Cantonment | 138 | 19:00 | 132 | 00:00 | Pabna | 138 | 23:00 | 132 | 12:00
| Chandpur | 141 | 18:00 | 127 | 01:00 | Palashbari | 138 | 03:00 | 128 | 17:00
| Chandraghona | 139 | 20:00 | 128 | 06:00 | Panchagarh | 136 | 04:00 | 121 | 09:00
| Chapai | 136 | 19:00 | 128 | 14:00 | Patuakhali | 130 | 04:00 | 125 | 00:00
| Charsaidpur | 139 | 18:30 | 132 | 01:00 | Payra | 131 | 04:00 | 128 | 00:00
| Chauddagram | 138 | 08:00 | 127 | 05:00 | PHP | 139 | 20:00 | 125 | 05:00
| Chhatak | 138 | 08:00 | 132 | 00:00 | Postogola | 138 | 18:30 | 132 | 00:00
| Chowmuhani | 136 | 20:00 | 124 | 00:00 | Purbachal | 140 | 08:00 | 132 | 14:00
| Chuadanga | 136 | 18:00 | 131 | 07:00 | Purbasadipur | 137 | 03:00 | 125 | 09:00
| Coxsbazar | 134 | 10:00 | 113 | 05:00 | Rahim | 139 | 11:00 | 134 | 00:00
| Cumilla(N) | 142 | 08:00 | 133 | 01:00 | Rajbari | 136 | 18:30 | 130 | 00:00
| Cumilla(S) | 141 | 08:00 | 127 | 12:00 | Rajendrapur | 139 | 14:00 | 129 | 17:00
| Daudkandi | 140 | 08:00 | 130 | 00:00 | Rajshahi | 135 | 02:00 | 131 | 11:00
| Dhaka | 137 | 03:00 | 132 | 16:00 | Rajshahi-230 | 137 | 18:00 | 131 | 12:00
| Dhamrai | 136 | 19:00 | 131 | 00:00 | Ramganj | 138 | 20:00 | 125 | 01:00
| Dhanmondi | 138 | 20:00 | 134 | 16:00 | Rampur | 135 | 10:00 | 126 | 02:00
| Dohazari | 136 | 09:00 | 124 | 05:00 | Rampura | 138 | 08:00 | 132 | 13:00
| Faridpur | 136 | 18:00 | 130 | 00:00 | Rangamati | 138 | 20:00 | 129 | 06:00
| Fatullah | 138 | 18:30 | 132 | 00:00 | Rangpur | 140 | 04:00 | 127 | 12:00
| Fenchuganj | 141 | 08:00 | 137 | 00:00 | Ruppur | 138 | 19:00 | 130 | 18:00
| Feni | 140 | 08:00 | 128 | 12:00 | Saidpur | 138 | 04:00 | 126 | 09:00
| Ghorashal | 142 | 07:00 | 139 | 11:00 | Satkhira | 139 | 18:00 | 130 | 12:00
| Goalpara | 139 | 17:00 | 132 | 12:00 | Satmasjid | 138 | 19:30 | 132 | 00:00
| Gollamari | 137 | 18:30 | 128 | 00:00 | Savar | 139 | 19:00 | 129 | 00:00
| Gopalganj | 136 | 18:00 | 128 | 00:00 | Shahjadpur | 144 | 03:00 | 139 | 10:00
| Gopalganj-400 | 138 | 18:30 | 131 | 00:00 | Shahjibazar | 137 | 09:00 | 133 | 23:00
| Gulshan | 137 | 19:00 | 131 | 15:00 | Shahmirpur | 138 | 20:00 | 127 | 05:00
| Halishahar | 138 | 20:00 | 126 | 06:00 | Shariatpur | 136 | 18:00 | 130 | 00:00
| Haripur | 139 | 11:00 | 134 | 00:00 | Sherpur | 136 | 04:00 | 124 | 00:00
| HaripurSBU | 139 | 11:00 | 134 | 00:00 | Shikalbaha | 139 | 20:00 | 127 | 05:00
| Hasnabad | 137 | 20:00 | 132 | 00:00 | Shikalbaha-230 | 135 | 09:00 | 128 | 06:00
| Hathazari | 140 | 20:00 | 133 | 11:00 | Shitalakhya | 138 | 18:30 | 132 | 00:00
| Ishurdi | 139 | 23:00 | 135 | 00:00 | Sholosohor | 136 | 10:00 | 128 | 05:00
| Jaldhaka | 136 | 05:00 | 124 | 12:00 | Shyampur | 137 | 18:30 | 132 | 00:00
| Jamalpur | 138 | 03:00 | 126 | 12:00 | Shyampur-230 | 138 | 18:30 | 132 | 01:00
| Jashore | 138 | 18:00 | 128 | 12:00 | Siddhirganj | 139 | 18:30 | 133 | 00:00
| Jhenaidah | 140 | 18:00 | 134 | 12:00 | Sirajganj | 140 | 02:00 | 133 | 15:00
| Jhenaidah-230 | 140 | 18:00 | 134 | 12:00 | Sonargaon | 138 | 19:30 | 129 | 01:00
| Joydebpur | 145 | 18:30 | 134 | 10:00 | Sreemongol | 136 | 09:00 | 133 | 00:00
| Joypurhat | 134 | 19:30 | 126 | 14:00 | Srinagar | 136 | 19:00 | 131 | 00:00
| Juldah | 138 | 20:00 | 126 | 05:00 | SSM | 135 | 14:00 | 131 | 06:00
| Kabirpur | 140 | 18:30 | 131 | 12:00 | Sunamganj | 137 | 08:00 | 131 | 00:00
| Kachua | 142 | 19:30 | 128 | 01:00 | Sylhet | 137 | 08:00 | 134 | 00:00
| Kaliakoir | 141 | 08:00 | 133 | 00:00 | Tangail | 137 | 08:00 | 130 | 00:00
| Kallyanpur | 140 | 18:30 | 132 | 00:00 | Thakurgaon | 137 | 04:00 | 122 | 11:00
| Kalurghat | 138 | 20:00 | 129 | 05:00 | TK | 136 | 08:00 | 131 | 11:00
| Kamrangirchar | 137 | 18:30 | 132 | 00:00 | Tongi | 139 | 13:00 | 134 | 00:00
| Kaptai | 135 | 08:00 | 132 | 00:00 | Ullon | 138 | 08:00 | 132 | 11:00
| Kazla | 137 | 08:00 | 132 | 16:00 | Uttara | 138 | 18:30 | 130 | 01:00
| Keranigonj | 137 | 18:30 | 130 | 12:00 | UttaraNew | 139 | 08:00 | 133 | 10:00
| Khagrachori | 137 | 10:00 | 128 | 06:00 | Zigatola | 136 | 19:00 | 131 | 13:00
| Khulna | 139 | 18:00 | 132 | 00:00
| Khulna(S) | 140 | 18:00 | 132 | 00:00
| Khulshi | 137 | 20:00 | 126 | 05:00
| Kishoreganj | 136 | 08:00 | 127 | 11:00
| Kodda | 141 | 18:30 | 130 | 12:00
| KSRM | 138 | 09:00 | 130 | 05:00
| Kulaura | 139 | 09:00 | 137 | 00:00
| Kurigram | 136 | 03:00 | 126 | 11:00
| Kushtia | 138 | 03:00 | 134 | 00:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2023-03-19
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 960 | 5321 | 2959 | 8280 |  |  |  | QF-LDC-11
0:30 | 550 | 5685.5 | 3378.5 | 9064 | Date: | 2023-03-19
1:00 | 140 | 6050 | 3798 | 9848
1:30 | 140.5 | 5902 | 3518.5 | 9420.5
2:00 | 141 | 5754 | 3239 | 8993
2:30 | 150.5 | 5667.5 | 3110 | 8777.5 | [5 empty] | Gen. at Eve. Peak | 9675 | 9675 MW (19:00 )
3:00 | 160 | 5581 | 2981 | 8562 | [6 empty] | 19:00
3:30 | 193 | 5537.5 | 2925.5 | 8463 | [5 empty] | Gen. at Day Peak | 8684 | 8684 MW (12:00 )
4:00 | 226 | 5494 | 2870 | 8364 | [6 empty] | 12:00
4:30 | 241.5 | 5314 | 2823.5 | 8137.5 | [5 empty] | Highest Generation | 9848
5:00 | 257 | 5134 | 2777 | 7911 | [6 empty] | 1:00
5:30 | 231 | 5234 | 2760 | 7994
6:00 | 205 | 5334 | 2743 | 8077
6:30 | 121 | 5425.5 | 2843.5 | 8269
7:00 | 37 | 5517 | 2944 | 8461
7:30 | 64.5 | 5345 | 2902.5 | 8247.5
8:00 | 92 | 5173 | 2861 | 8034
8:30 | 260 | 5031 | 2897 | 7928
9:00 | 428 | 4889 | 2933 | 7822
9:30 | 569 | 5016.5 | 2999 | 8015.5
10:00 | 710 | 5144 | 3065 | 8209
10:30 | 758.5 | 5034 | 3071.5 | 8105.5
11:00 | 807 | 4924 | 3078 | 8002
11:30 | 716 | 5199 | 3144 | 8343
12:00 | 625 | 5474 | 3210 | 8684
12:30 | 567.5 | 5610 | 3363 | 8973
13:00 | 510 | 5746 | 3516 | 9262
13:30 | 495 | 5642.5 | 3362.5 | 9005
14:00 | 480 | 5539 | 3209 | 8748
14:30 | 492.5 | 5638.5 | 3222.5 | 8861
15:00 | 505 | 5738 | 3236 | 8974
15:30 | 538.5 | 5740 | 3241 | 8981
16:00 | 572 | 5742 | 3246 | 8988
16:30 | 553.5 | 5829.5 | 3175.5 | 9005
17:00 | 535 | 5917 | 3105 | 9022
17:30 | 409 | 6058 | 3143.5 | 9201.5
18:00 | 283 | 6199 | 3182 | 9381
18:30 | 201.5 | 6246 | 3282 | 9528
19:00 | 120 | 6293 | 3382 | 9675
19:30 | 210 | 5904 | 3398 | 9302
20:00 | 180 | 5792 | 3327 | 9119 |  |  |  | Executive Engineer
20:30 | 282 | 5741 | 3302.5 | 9043.5 |  |  |  | Network Operation Division
21:00 | 384 | 5690 | 3278 | 8968
21:30 | 518 | 5683.5 | 3278 | 8961.5
22:00 | 652 | 5677 | 3278 | 8955 |  |  |  |  | Page 6 of 7
22:30 | 681 | 5645 | 3139 | 8784
23:00 | 710 | 5613 | 3000 | 8613
23:30 | 835 | 5467 | 2979.5 | 8446.5
24:00 | 960 | 5321 | 2959 | 8280
9675 MW (19:00 )
8684 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-03-19 |  | Energy |  | 216949016
[13 empty] | 2023-03-19 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3838 | 903 | 1899 | 0 | 406 | 1142 | 0 | 0 | 0 | 92 | 0 | 0
0:30 | 3860.5 | 894.5 | 2056 | 0 | 635 | 1449.5 | 12.5 | 0 | 44 | 112 | 0 | 20 | Date: | 2023-03-19
1:00 | 3883 | 886 | 2213 | 0 | 864 | 1757 | 25 | 0 | 88 | 132 | 0 | 40
1:30 | 3794 | 886 | 2180 | 0 | 749.5 | 1589.5 | 25 | 0 | 70.5 | 126 | 0 | 20 | [7 empty] | Total Energy | 216.949 | Total Energy Gen 216.949 MKWHr Energy Not Served 0.038 MKWHr Energy Requirement 216.987 MKWHr
2:00 | 3705 | 886 | 2147 | 0 | 635 | 1422 | 25 | 0 | 53 | 120 | 0 | 0 | [7 empty] | Energy not Served | 0.0384
2:30 | 3703 | 886.5 | 2077.5 | 0 | 620.5 | 1319.5 | 25 | 0 | 26.5 | 119 | 0 | 0 | [7 empty] | Energy Requirement | 216.9874
3:00 | 3701 | 887 | 2008 | 0 | 606 | 1217 | 25 | 0 | 0 | 118 | 0 | 0
3:30 | 3666 | 887.5 | 1981 | 0 | 568 | 1214.5 | 25 | 0 | 0 | 121 | 0 | 0 | [5 empty] | Shortage
4:00 | 3631 | 888 | 1954 | 0 | 530 | 1212 | 25 | 0 | 0 | 124 | 0 | 0
4:30 | 3641 | 888 | 1910 | 0 | 388 | 1165.5 | 25 | 0 | 0 | 120 | 0 | 0
5:00 | 3651 | 888 | 1866 | 0 | 246 | 1119 | 25 | 0 | 0 | 116 | 0 | 0
5:30 | 3701.5 | 866 | 1951.5 | 0 | 246 | 1090 | 25 | 0 | 0 | 114 | 0 | 0
6:00 | 3752 | 844 | 2037 | 0 | 246 | 1061 | 25 | 0 | 0 | 112 | 0 | 0
6:30 | 3812.5 | 820.5 | 2126.5 | 0 | 299 | 1074 | 25 | 0 | 0 | 109 | 2.5 | 0 |  |  |  | Coal
7:00 | 3873 | 797 | 2216 | 0 | 352 | 1087 | 25 | 0 | 0 | 106 | 5 | 0
7:30 | 3769.5 | 797.5 | 2063.5 | 0 | 425 | 1085 | 25 | 0 | 0 | 65 | 17 | 0 |  |  | Oil |  |  |  | ,
8:00 | 3666 | 798 | 1911 | 0 | 498 | 1083 | 25 | 0 | 0 | 24 | 29 | 0
8:30 | 3508.5 | 821.5 | 1880.5 | 0 | 514 | 1083 | 25 | 0 | 0 | 49 | 46.5 | 0
9:00 | 3351 | 845 | 1850 | 0 | 530 | 1083 | 25 | 0 | 0 | 74 | 64 | 0
9:30 | 3397 | 845 | 1888 | 0 | 582.5 | 1122 | 25 | 0 | 0 | 82 | 74 | 0
10:00 | 3443 | 845 | 1926 | 0 | 635 | 1161 | 25 | 0 | 0 | 90 | 84 | 0
10:30 | 3354.5 | 869 | 1846 | 0 | 668 | 1158 | 12.5 | 0 | 0 | 98 | 99.5 | 0
11:00 | 3266 | 893 | 1766 | 0 | 701 | 1155 | 0 | 0 | 0 | 106 | 115 | 0
11:30 | 3371.5 | 893 | 1882.5 | 0 | 753 | 1177 | 0 | 0 | 8 | 115 | 143 | 0
12:00 | 3477 | 893 | 1999 | 0 | 805 | 1199 | 0 | 0 | 16 | 124 | 171 | 0
12:30 | 3523.5 | 892.5 | 2057 | 0 | 893.5 | 1301 | 0 | 0 | 20.5 | 123 | 162 | 0
13:00 | 3570 | 892 | 2115 | 0 | 982 | 1403 | 0 | 0 | 25 | 122 | 153 | 0
13:30 | 3570 | 892 | 2115 | 0 | 982 | 1403 | 0 | 0 | 25 | 122 | 153 | 0
14:00 | 3570 | 892 | 2115 | 0 | 982 | 1403 | 0 | 0 | 25 | 122 | 153 | 0
14:30 | 3630.5 | 896 | 2141.5 | 0 | 934.5 | 1276.5 | 0 | 0 | 16.5 | 121 | 101.5 | 0
15:00 | 3691 | 900 | 2168 | 0 | 887 | 1150 | 0 | 0 | 8 | 120 | 50 | 0
15:30 | 3700.5 | 902.5 | 2148 | 0 | 874 | 1175.5 | 0 | 0 | 8 | 115 | 57.5 | 0
16:00 | 3710 | 905 | 2128 | 0 | 861 | 1201 | 0 | 0 | 8 | 110 | 65 | 0
16:30 | 3749.5 | 904.5 | 2078.5 | 0 | 896 | 1206.5 | 0 | 0 | 24 | 109 | 37 | 0
17:00 | 3789 | 904 | 2029 | 0 | 931 | 1212 | 0 | 0 | 40 | 108 | 9 | 0
17:30 | 3792 | 904.5 | 2039.5 | 0 | 1071 | 1212.5 | 0 | 0 | 63.5 | 114 | 4.5 | 0
18:00 | 3795 | 905 | 2050 | 0 | 1211 | 1213 | 0 | 0 | 87 | 120 | 0 | 0
18:30 | 3753 | 887 | 2003 | 0 | 1412 | 1222 | 0 | 0 | 140 | 111 | 0 | 0
19:00 | 3711 | 869 | 1956 | 0 | 1613 | 1231 | 0 | 0 | 193 | 102 | 0 | 0
19:30 | 3658 | 834 | 1963 | 0 | 1259 | 1330 | 0 | 0 | 156 | 102 | 0 | 0
20:00 | 3774 | 833 | 1983 | 0 | 1009 | 1351 | 0 | 0 | 73 | 96 | 0 | 0
20:30 | 3831.5 | 833 | 2073 | 0 | 808.5 | 1360 | 0 | 0 | 36.5 | 101 | 0 | 0
21:00 | 3889 | 833 | 2163 | 0 | 608 | 1369 | 0 | 0 | 0 | 106 | 0 | 0
21:30 | 3899.5 | 833 | 2157 | 0 | 601 | 1371 | 0 | 0 | 0 | 100 | 0 | 0
22:00 | 3910 | 833 | 2151 | 0 | 594 | 1373 | 0 | 0 | 0 | 94 | 0 | 0
22:30 | 3894 | 833.5 | 2123.5 | 0 | 528.5 | 1311.5 | 0 | 0 | 0 | 93 | 0 | 0
23:00 | 3878 | 834 | 2096 | 0 | 463 | 1250 | 0 | 0 | 0 | 92 | 0 | 0
23:30 | 3858 | 868.5 | 1997.5 | 0 | 434.5 | 1196 | 0 | 0 | 0 | 92 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C
24:00 | 3838 | 903 | 1899 | 0 | 406 | 1142 | 0 | 0 | 0 | 92 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 216.949 MKWHr Energy Not Served 0.038 MKWHr Energy Requirement 216.987 MKWHr
Note on W13: Author:

## Generation
g | 2023-03-19
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | [15 empty] | 267060
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 |  | 135 | 140 | 140 | 140 | 140 | 140 | 140 | 3200000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [12 empty] | 3 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 |  |  |  | 0 | 67741
| Teknaf 20MW PP (Solartech) | [6 empty] | 0 | 1 | [7 empty] | 3 | 1 | [9 empty] | 6615
6 | Sikalbaha 225MW CCPP (Gas) | 228 | 226 | 229 | 229 | 231 | 230 | 229 | 229 | 229 | 229 | 201 | 212 | 228 | 228 | 228 | 228 | 231 | 228 |  | 222 | 222 | 227 | 228 | 228 | 228 | 229 | 5358912
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 17 | 0 | [14 empty] | 12 |  | 51 | 51 | 51 |  |  |  | 0 | 203865
12 | Hathazari 100 MW peaking PP | [12 empty] | 9 | 8 | 8 | 8 | 8 | 11 |  | 8 | 7 | 6 |  |  |  |  | 55920
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 35 | 51 | 51 | 34 | 34 | 35 | 51 | 51 | 51 |  | 51 | 51 | 51 | 17 | 17 | 17 | 17 | 909959
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 37 | 40 | 38 | 37 | 40 | 40 | 40 | 37 | 39 | 60 | 42 | 102 | 102 | 39 | 97 | 97 | 59 | 59 |  |  |  |  | 37 | 37 | 37 | 40 | 1305000
17 | Siddhirganj 335 MW CCPP | 170 | 170 | 170 | 170 | 170 | 200 | 228 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 180 | 180 | 180 | 180 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 4077693
18 | Kodda 300 MW PP Unit-2 (Summit) | [10 empty] | 12 | 15 | 15 | 15 | 15 | 15 | 15 | 25 |  | 15 | [6 empty] | 2007272
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 43 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 |  | 102 | 102 | 55 | 8 | 8 | 8 | 8 | 1170909
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 93 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 90 | 100 | 100 | 90 | 100 | 100 | 100 | 2368344
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4410000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 50 | 50 | 50 | 50 | 50 | 50 | 51 | 50 | 51 | 51 | 51 | 51 | 51 | 50 | 51 | 44 | 47 | 51 |  | 48 | 45 | 50 | 51 | 51 | 51 | 51 | 1189872
33 | Ashuganj 225 MW CCPP | 211 | 209 | 209 | 203 | 207 | 194 | 193 | 190 | 199 | 181 | 200 | 200 | 179 | 181 | 182 | 181 | 183 | 182 |  | 182 | 181 | 165 | 153 | 186 | 195 | 181 | 4626000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 280 | 285 | 280 | 280 | 280 | 315 | 280 | 280 |  |  |  |  | 90 | 20 | 35 | 50 | 105 | 195 |  | 315 | 335 | 365 | 365 | 285 | 285 | 285 | 4925000
| Ashuganj 420 MW CCPP(East) | 352 | 352 | 352 | 352 | 353 | 352 | 352 | 350 | 350 | 360 | 330 | 330 | 310 | 315 | 330 | 330 | 330 | 330 |  | 280 | 280 | 280 | 280 | 280 | 280 | 250 | 7858300
35 | Ashuganj 55 MW PP (Precision) | 53 | 53 | 54 | 54 | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 54 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 54 | 53 | 54 | 30 | 1221120
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 398 | 398 | 398 | 396 | 396 | 398 | 399 | 395 | 344 | 343 | 298 | 344 | 395 | 397 | 392 | 376 | 381 | 383 |  | 352 | 305 | 314 | 372 | 401 | 395 | 395 | 9201670
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 400 | 400 | 350 | 400 | 430 | 350 | 350 | 350 | 320 | 360 | 360 | 320 | 320 | 320 | 320 | 320 |  | 320 | 320 | 320 | 430 | 430 | 430 | 370 | 8932250
41 | Haripur 360MW CCPP(HPL) | 349 | 340 | 342 | 342 | 304 | 353 | 353 | 273 | 277 | 279 | 277 | 307 | 307 | 307 | 352 | 352 | 310 | 310 |  | 277 | 277 | 309 | 352 | 352 | 352 | 352 | 7668000
42 | RPCL 210MW CCPP | 82 | 86 | 86 | 86 | 90 | 89 | 51 | 52 | 44 | 44 | 44 | 44 | 35 | 36 | 35 | 35 | 47 | 51 |  | 57 | 74 | 76 | 86 | 86 | 83 | 83 | 1433280
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 0 | 1 | 6 | 6 | 4 | 13 | 5 | 10 | 7 | 6 | 1 | 0 | [8 empty] | 81580
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 43 | 43 | 43 | 44 | 43 | 43 | 43 |  | 43 | 43 | 43 | 44 | 43 | 43 | 43 | 1033000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 43 | 968400
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 65 | 64 | 66 | 40 | 40 | 40 | 40 | 40 |  | 66 | 66 | 66 | 65 | 66 | 66 | 40 | 1141440
48 | Shahjibazar 86MW PP (Shahjibazar) | 89 | 89 | 40 | 40 | 40 | 40 | 89 | 89 | 60 | 60 | 10 | 50 | 50 | 50 | 50 | 50 | 50 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 40 | 1551360
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 124 | 124 | 124 | 124 | 124 | 124 | 120 | 120 | 85 | 80 | 80 | 79 | 79 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 79 | 80 | 80 | 80 | 80 | 2287200
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 193500
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [5 empty] | 3 | 5 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 147500
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 31 | 31 | 14 | 31 | 48 | 51 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 52 | 52 | 52 | 52 | 1177800
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 190608
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 260 | 270 | 275 | 275 | 270 | 310 | 260 | 270 | 280 | 270 | 300 | 270 | 270 | 280 | 270 | 270 | 275 |  | 250 | 250 | 270 | 280 | 285 | 270 | 260 | 6779500
| Bibiyana South 400 MW | 400 | 350 | 350 | 350 | 350 | 400 | 400 | 340 | 340 | 400 | 360 | 360 | 319 | 360 | 400 | 400 | 400 | 340 |  | 325 | 294 | 400 | 400 | 400 | 400 | 400 | 8935200
58 | Nababganj 55 MW PP (Southern power ) | [8 empty] | 5 | 17 | 10 | 17 | 35 | 35 | 17 | 17 | 17 | 25 |  | 12 | 17 | 17 |  |  |  | 0 | 269788
59 | Tangail Palli Power Gen 22 MW | [17 empty] | 5 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 42480
60 | Barabkunda 22 MW PP (Regent) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 |  | 5 | 5 | 5 | 110112
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | [9 empty] | 22 | 22 |  |  |  |  | 22 | 22 | 22 | 22 | 260028
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 419040
63 | Impoprt (Tripura) | 132 | 120 | 118 | 124 | 116 | 112 | 106 | 24 | 74 | 90 | 106 | 124 | 122 | 114 | 120 | 110 | 108 | 120 |  | 102 | 102 | 96 | 106 | 94 | 92 | 92 | 2553600
64 | Malancha, Ctg. EPZ (United) | [10 empty] | 0 | [14 empty] | 0 | 22560
65 | Feni 22MW PP (Doreen) | [6 empty] | 14 | 21 | 21 | 21 | 21 | [14 empty] | 0 | 87192
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 7 | 5 | 5 | 10 | 10 | 10 | 10 | 11 | 11 | 11 |  | 11 | 11 | 8 | 11 | 11 | 11 | 11 | 227700
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | [6 empty] | 25 | 25 | 30 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 598200
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 15 | 21 | 21 | 21 |  |  | 9 | 9 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 |  |  | 21 | 21 | 21 | 21 | 359630
69 | Summit Ashulia | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 0 | 0 | 15 | 20 | 20 | 552000
70 | Summit Madhabdi | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 7 | 0 | 0 | 0 | 14 | 20 | 20 | 26 | 27 | 27 |  | 20 | 20 | 0 | 0 | 18 | 16 | 27 | 405720
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 0 | 0 | 0 | 33 | 33 | 0 | 0 | 0 | 33 | 33 |  | 33 | 33 | 33 | 0 | 0 | 10 | 25 | 510700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 31 | 0 | 0 | 16 | 16 | 16 | 31 | 28 | 29 |  | 16 | 29 | 30 | 31 | 32 | 32 | 32 | 640300
73 | Ghorashal 108MW PP (Regent) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 724500
| Feni Lanka Power | 17 | 17 | 17 | 17 | 0 | [12 empty] | 9 | [7 empty] | 0 | 90060
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 11 | 9 | 9 | 9 | 9 | 10 | 26 | 38 |  | 24 | 26 | 8 | 8 | 8 | 8 | 8 | 330120
| Manikgonj 162MW PP(MPGL) | [9 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 75 | 17 |  |  |  |  | 0 | 253440
77 | Siddhirganj 100 PP(Dutch Bangla) | [9 empty] | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 14 | [5 empty] | 0 | 74698
78 | Gazipur 52 MW PP | 51 | 8 | 8 | 8 | 8 | 8 | 17 | 17 | 8 | 11 | 16 | 24 | 16 | 16 |  |  | 16 | 33 |  | 33 | [5 empty] | 0 | 322560
79 | Kodda 150 MW PP | 32 | 32 | 0 | [8 empty] | 16 | 16 | 16 |  |  | 32 | 64 |  | 64 | 32 | 16 |  |  |  | 0 | 289920
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 0 | [15 empty] | 3 |  | 8 | 8 | 8 |  |  |  |  | 29122
| Gazipur 100 MW PP | 52 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 15 | 15 |  |  | 2 | 24 |  | 52 | 17 | 17 | 17 | 17 |  | 0 | 474240
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 0 | 0 | 1 | 3 | 0 | 2 | 1 | 2 | 1 | 0 | [9 empty] | 10336
| Jodiac Power | 17 | 17 | 17 | 17 | 0 |  |  |  |  | 5 | 17 | 26 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 17 | 17 | 17 | 0 | 516897
| Karnaphuli Power Ltd. | 54 | 54 | 54 | 54 | 17 | 17 | 19 | 40 | 69 | 71 | 34 | 43 | 55 | 72 | 72 | 80 | 91 | 92 |  | 92 | 92 | 92 | 68 | 68 | 68 | 65 | 1545593
82 | Madanganj 102 PP(Summit) | 2 | 0 | [7 empty] | 6 | 34 | 34 | 34 | 21 | 17 | 17 | 17 | 19 |  | 47 | 30 | 5 |  |  |  | 0 | 223914
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 289 | 321 | 318 | 311 | 310 | 319 | 302 | 283 | 309 | 297 | 302 | 310 | 289 | 297 | 305 | 296 | 306 | 309 |  | 285 | 286 | 297 | 305 | 290 | 295 | 285 | 7311156
87 | Meghnaghat 100 MW(IEL) | [19 empty] | 4 | 9 |  |  |  |  | 0 | 9600
| Meghnaghat 104 MW PP (OPCL) | 19 | 44 | 54 | 54 | 0 | [5 empty] | 14 | 16 | 17 | 17 | 17 | 17 | 17 | 23 |  | 30 | [5 empty] | 0 | 432960
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 33 | 33 | 33 | 33 | 0 |  | 22 | 22 | 33 | 33 | 12 | 22 | 22 | 33 | 33 | 33 | 44 | 44 |  | 44 | 35 | 10 | 10 | 10 | 10 | 10 | 588000
92 | Fenchuganj 44MW (Energyprima) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 30 | 30 | 10 | 30 | 41 | 44 | 44 | 44 | 44 | 47 |  | 47 | 47 | 47 | 47 | 50 | 50 | 50 | 1050264
93 | Ashuganj 51 MW PP (Midland) | 43 | 10 | 10 | 10 | 10 | 10 | 31 | 43 | 20 | 20 | 20 | 39 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 51 | 5 | 893506
94 | Gagnagar 102 MW PP (Digital Power) | [8 empty] | 3 | 24 | 24 | 24 | 24 | 24 | 24 | 8 | 8 | 8 |  | 8 | [5 empty] | 0 | 198144
95 | Patenga 50MW PP (Baraka) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 6 | 6 | 6 | 9 | 13 | 16 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 417120
96 | Chattogram 108 MW PP (ECPV) | [19 empty] | 1 |  | 0 |  |  |  | 0 | 1920
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [10 empty] | 28 | 30 | 10 | 30 | 30 | 30 | 30 | 30 |  | 15 | [5 empty] | 0 | 269438
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 2 | [5 empty] | 0 | 363182
101 | Kushiara 163 MW CCPP (KP) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 112 | 112 | 80 | 112 | 112 | 112 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2132100
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | [9 empty] | 4800
103 | Kamalaghat 54 MW PP(Banco Energy) | [10 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 40 | 54 | 35 | 35 | 35 | 17 | 0 | 303840
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 68 | 69 | 45 | 9 | 0 |  | 5 | 16 | 8 | 8 | 8 | 10 | 57 | 45 | 45 | 45 | 45 | 53 |  | 45 | 45 | 16 | 16 | 16 | 16 | 0 | 732000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 17 | 17 | 0 | [6 empty] | 13 | 23 | 35 | 35 | 35 | 35 | 36 | 42 |  | 82 | 45 | 42 | 19 | 17 | 17 | 0 | 505296
115 | Juldah 100 MW PP Unit-3 (Acorn) | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 48 | 25 | 38 | 50 | 50 | 38 | 50 | 50 | 50 |  | 100 | 100 | 60 | 60 | 60 | 60 | 60 | 1179840
116 | Chandpur 200MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 27 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 50 |  | 51 | 17 | 17 | 17 | 17 | 17 | 17 | 672000
117 | Ashuganj 150MW PP (Midland) | 74 | 0 | [5 empty] | 11 | 20 | 21 | 40 | 40 | 40 | 40 | 40 | 10 | 15 | 31 |  | 80 | 50 | 50 | 10 | 10 |  | 0 | 620582
118 | Bibiyana-III 400 MW CCPP | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 220 | 300 | 337 | 314 | 353 | 343 | 340 | 345 | 356 | 375 | 355 |  | 354 | 355 | 356 | 374 | 364 | 352 | 352 | 6219000
| Jamalpur 115 MW PP (United) | 28 | 28 | 28 | 35 | 0 |  | 16 | 16 | 16 | 16 | 16 | 28 | 94 | 52 | 52 | 52 | 52 | 75 |  | 104 | 113 | 115 | 85 | 85 | 85 | 85 | 1215600
| Anwara 300 MW PP (United) | 65 | 30 | 15 | 0 | [5 empty] | 2 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 |  |  |  | 0 | 323673
| Juldah unit-2 (Acorn) | 40 | 40 | 40 | 40 | 0 |  | 2 | 29 | 17 | 12 | 12 | 23 | 50 | 17 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 |  |  | 0 | 432960
| Anlima Energy Ltd. | 90 | 90 | 90 | 89 | 51 | 51 | 74 | 90 | 90 | 90 | 51 | 57 | 72 | 72 | 86 | 89 | 89 | 89 |  | 89 | 89 | 89 | 89 | 89 | 89 | 102 | 2003509
| Bhairob 54.5 MW | [25 empty] | 0 | 3240
| Spectra Solar Plant Ltd. | [6 empty] | 0 | 2 | 4 | 0 | 4 | 1 | 0 | 8 | 4 | 2 | 0 | [9 empty] | 33121
| Chandpur 115(Doreen) | 61 | 54 | 54 | 40 | 36 | 36 | 35 | 36 | 36 | 36 | 36 | 35 | 36 | 36 | 36 | 51 | 59 | 86 |  | 95 | 72 | 54 | 17 | 17 | 17 | 17 | 1054080
| Kanchan Purbachal Power Generation Ltd. | 17 | 0 |  |  |  |  | 3 | 17 | 17 | 17 | 17 | 15 | 16 | 17 | 17 | 17 | 17 | 19 |  | 35 | 35 | 35 | 17 | 17 |  | 0 | 337680
| Mirsharai 150 MW (Oil) | [25 empty] | 0 | 0
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 6050 | 5754 | 5581 | 5494 | 5134 | 5334 | 5517 | 5173 | 4889 | 5144 | 4924 | 5474 | 5746 | 5539 | 5738 | 5742 | 5917 | 6199 | 5738 | 6293 | 5904 | 5792 | 5690 | 5677 | 5613 | 5321 | 138204931
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [17 empty] | 16 |  | 16 | [5 empty] | 0 | 25920
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [19 empty] | 1 | 4 |  |  |  |  | 0 | 10080
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 2 | 11 | 31 | 42 | 52 | 74 | 65 | 30 | 10 | 1 | [10 empty] | 315360
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [25 empty] | 0 | 0
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 201 | 152 | 152 | 152 | 152 | 152 | 151 | 152 | 151 | 151 | 150 | 162 | 161 | 162 | 160 | 161 | 162 | 163 |  | 161 | 160 | 161 | 159 | 163 | 150 | 152 | 3840000
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 170 | 158 | 158 | 158 | 158 | 158 | 170 | 151 | 170 | 161 | 159 | 159 | 146 | 170 | 170 | 158 | 170 | 159 |  | 170 | 148 | 168 | 170 | 170 | 170 | 170 | 4022719
140 | Bhola 33 MW PP (Venture) | 20 | 19 | 18 | 17 | 16 | 8 | 5 | 10 | 16 | 15 | 15 | 14 | 15 | 16 | 15 | 14 | 15 | 19 |  | 11 | 15 | 17 | 22 | 20 | 19 | 17 | 369600
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 886 | 886 | 887 | 888 | 888 | 844 | 797 | 798 | 845 | 845 | 893 | 893 | 892 | 920 | 900 | 905 | 904 | 905 |  | 869 | 834 | 833 | 833 | 833 | 834 | 903 | 20901818
147 | Bheramara 410 MW CCPP | 350 | 250 | 250 | 200 | 200 | 200 | 300 | 260 | 230 | 230 | 230 | 230 | 230 | 230 | 280 | 280 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6499296
148 | Payra 1320 MW | 1190 | 900 | 670 | 580 | 500 | 500 | 500 | 500 | 500 | 580 | 580 | 630 | 740 | 750 | 820 | 870 | 880 | 880 |  | 900 | 1000 | 1020 | 1040 | 1040 | 930 | 820 | 20298500
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 169 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4310800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [26 empty] | 0
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 0 | 0 | [9 empty] | 12780
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 160 | 140 | 140 | 130 | 130 | 130 | 154 | 150 | 150 | 150 | 150 | 185 | 200 | 150 | 185 | 190 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 140 | 140 | 4134800
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 383 | 357 | 308 | 257 | 258 | 334 | 378 | 282 | 283 | 325 | 270 | 268 | 382 | 358 | 398 | 380 | 310 | 314 |  | 308 | 310 | 312 | 362 | 360 | 307 | 308 | 7934581
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 5 | 4 | [24 empty] | 11030
162 | Bogra 22 MW PP (GBB) | 22 | 3 | 3 | 3 | 3 | 3 | 18 | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 20 | 22 | 20 |  | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 394320
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 0 | 0 | 5 | 5 | 5 | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 203472
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [19 empty] | 36 | 36 | [5 empty] | 44663
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 34 | 30 |  |  |  |  | 0 | 31008
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [7 empty] | 30 | 35 | 35 | 35 | 38 | 35 | 35 | 35 |  |  | 10 |  | 70 | 70 | 70 | 35 | 35 |  | 0 | 650976
172 | Confidence Power Bogura Unit-1 113 MW | [17 empty] | 35 |  | 70 | 35 |  |  |  |  | 0 | 102720
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 34 | 0 |  |  |  |  | 25 | 40 | 35 | 35 | 36 | 35 | 34 | 34 | 34 | 34 | 34 | 36 |  | 78 | 98 | 88 | 34 | 34 |  | 0 | 721267
177 | Sympa Solar Power 8MW | [6 empty] | 0 | [8 empty] | 3 | 1 | [9 empty] | 5088
178 | Energypac Power Venture Thakurgaon Ltd. | [17 empty] | 24 |  | 35 | 35 | 35 |  |  |  | 0 | 150336
| Intraco Solar 30 MW | [6 empty] | 1 | 1 | 3 | 7 | 8 | 7 | 5 | 12 | 11 | 11 | 3 | 0 | [8 empty] | 70180
| Adani Power Jharkhanda Ltd | 166 | 170 | 195 | 280 | 297 | 239 | 266 | 261 | 262 | 260 | 255 | 238 | 332 | [13 empty] | 3309091
178 | Teesta Solar Limited | [6 empty] | 2 | 13 | 19 | 26 | 42 | 74 | 74 | 138 | 14 | 38 | 3 | 0 | [8 empty] | 373680