## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-03-27 | Monday
|  | Date (day): | 2023-03-27 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12010.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13796 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-03-26 | 2023-03-27 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Line O/L
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 365 |  | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 78 | 77 | 78 | 78 | 30 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 378 | 381 | 400 | 400 | 12
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 312 | 272 | 300 | 300 | 60 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 360 | 380 | 400 | 50 |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 50 | 92 |  | 8 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 272 | 238 | 270 | 270 | 65 |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 50 | 80 | 80 |  | 22 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 42 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 19 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 40 | 90 | 90 |  | 10
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 130 | 160 | 110 | 160 |  | 118 | ST under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 8 | 92 | 102 |  | 10
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 16 | 82 | 115 | 34 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 35 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 43 | 43 | 45 | 45 |  | 35 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 51 | 51 | 51
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 30 | 280 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 0 | 300 |  | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 35 | 135 | 36 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 3 | 105 | 70 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 71 | 55 | 72 | 32 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 110 | 162 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 32 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 1994 | 2601 | 3125 | 3438 | 1664 | 703
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 130 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 20 | 20 | 20 | 20 | 30 |  | Fuel shortage
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 25 | 25 | 25 | 25 | 205 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 225 | 228 | 225 | 225
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 34 | 34 | 34 | 71 |  | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 40 |  | 58 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 0 | 85 |  | 17 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 44 | 22 | 55 | 55 |  | 45 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 76 | 100 | 75 | 100
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 5 | 0 | 5 | 5 | 17 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 31 | 42 | 5 | 15
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 5 | 5 | 5 | 5 | 103 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 45 | 30 | 120 | 230 | 70 |  | Fuel shortage
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17 | 37 |  | Fuel shortage
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 54 | 54 | 51 | 54 | 56 |  | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 30 | 100 | 100
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 11 | 89 | 107 | 107 |  | 9 | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 739 | 730 | 894 | 1142 | 949 | 279
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 215 | 217 | 190 | 210 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 0 | 0 | 0 | 360 |  | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 135 | 110 | 210 | 240 | 120 |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 240 | 260 | 320 | 320 |  |  | FGMO
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 47 | 47 | 47 | 35 |  | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 5 | 48 | 53 | 53 | 50 |  | Gas shortage
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 30 | 51 | 41 |  | Gas shortage
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 143 | 30 | 150
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 35 |  | 17 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 64 | 120 | 180 | 180 |  | 20 | Engine problem
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 18 | 19 | 19
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 0 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 128 | 132 | 135 | 153
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 16 | 0 | 52
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 18 | 18 | 18 | 18 |  | 7 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 34 | 114
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 76 | 9 | 113
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 54
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 115 | 52 | 115 | 115
| Cumilla Area Total |  |  |  |  | 3309 | 3285 | 1340 | 1358 | 1451 | 1968 | 1135 | 207
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 102 | 151 | 100 | 100 | 102 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 0 | 19 | 19 | 3 |  | Gas shortage
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 8 | 164 | 150 | 160 | 40 |  | Fuel shortage
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 99 | 89 | 90 | 115
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 32 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 277 | 422 | 428.6 | 412 | 105 | 4
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 41 | 38 | 44 | 44 |  | 26 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 112 | 112 | 112 |  | 51 | ST U/M.
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 50 | 49 | 50 | 50
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 61 | 65 | 65
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 89 | 86 | 86 | 86
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 |  | 231 | Under maint
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 16 | 16 | 9 |  | Gas shortage
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 270 | 270 | 300 | 300 |  |  | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 365 | 368 | 366 | 368 |  |  | FGMO
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 8 | 10 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 380 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1506 | 1505 | 1530 | 1552 | 29 | 789
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 900 | 893 | 909 | 909
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 66 | 99 |  | 16 | Engine problem
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 40 |  | 14 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 65 |  | 44 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 180 | 195 | 200 | 200 | 210 |  | Gas shortage
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 8 | 40
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 50 | 50 | 55 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 0 | 100
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 93 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 366 | 356 | 370 | 370
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3005 | 3001 | 1539 | 1459 | 1703 | 1873 | 611 | 74
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 48 | 62 |  | Fuel shortage
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 17 | 10 | 22 | 22 |  | 18 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 170 | 170 | 170 | 170 | 24 |  | Gas shortage
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 670 | 680 | 700 | 900 |  |  | Line O/L
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under maintenance
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Line O/L
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 148 | 154 | 150 | 150 |  |  | Line O/L
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1005 | 1014 | 1042 | 1290 | 86 | 238
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 32 |  | 20 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 18 | 32 |  | 39 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 50
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 40 |  | 10 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 130 | 174 | 150 | 180 | 30 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 355 | 370 | 350 | 400 | 14
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 26 | 35 |  | 15 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 19 | 22 | 22 | 22
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 34 | 18 |  | Fuel shortage
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 50 | 85 |  | 19 | Enging problem
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 94 | 50 | 95 | 18 |  | Fuel shortage
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 35 | 113
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 0 | 0 | 0 | 604 | 599 | 600 | 600 |  |  | On test.
| Rajshahi Area Total |  |  |  |  | 2179 | 2129 | 1159 | 1340 | 1392 | 1729 | 891 | 103
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 | 104 |  | Coal Shortage.
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 107 | 107 | 107 |  | 6 | Engine problem
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 34 | 70 | 0 | 115
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 33 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 140 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 415 | 347 | 445 | 392 | 229 | 91
| Total |  |  |  |  | 23482 | 22700 | 9974 | 10776 | 12010.6 | 13796 | 5699 | 2488
A. |  | 2023-03-26 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 10782 | MW at | 14:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 7896 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10776 | MW
3 | Day peak Generation : |  |  | 9974 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10247 | MW
4 | Evening peak Generation : |  |  | 10776 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 237.2032 | MKWHr | By Solar | 2.6857 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 131.8316 | MKWHr |  | By Oil: | 28.251 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 49.3804 | MKWHr |  | By Hydro: | 0.6036 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5699 | MW | Dhaka | 3675.2 | 3675.2 |  | 0 |  | 18:00 |  | 6
|  |  | For Plants S/D or M/C prob = |  |  | 2488 | MW | Chittagong | 1083.4 | 1083.4 |  | 0 |  | 19:00 |  | 47
|  |  | Total = |  |  | 8187 | MW | Khulna | 994.2 | 994.2 |  | 0 |  | 19:30 |  | 30
7 | Total Gas Supplied : |  |  | 986.76 | MMCFD |  |  | Rajshahi | 1329.2 | 1329.2 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 144002392.422 | ii) Oil : | Taka | 363712873.48 | Comilla | 782 | 782 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 184471982 | Total | Taka | 692187247.902 | Mymensingh | 997 | 997 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 392 | 392 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 600 | MW (E to W) at | 21:00 | hrs | Barisal | 260 | 260 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 280 | MW at | 20:00 | hrs | Rangpur | 734 | 734 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.6° C |  |  | Total | 10247 | 10247 |  | 0
B. |  | 2023-03-27 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 33.9° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13796 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10700 | MW
4 | Reserve(Generation end) |  |  |  | 1896 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 261.7991 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7755 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.4989 | MKWHr. | ii) HVDC Flow at Peak Time |  | 893 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.952 | MKWHr. | iii) Maximum HVDC Flow : |  | 914 | MW at | 19:30 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 76.9 |  | (b) Today: | 76.76 |  | (c) Rule Curve: |  | 89
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-03-26 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 45 | 0 | 372 | 283 |  | 0 | 400 | 276 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 19 | 17 | 27 | 33 | 28 | 0 | 0 | 25 | 0 | 135 | 0 | 0 | 224 | 0 | 0 | 0 |  | 16 | 0 | 0 | 33 | 6 | 20 | 5 | 37 | 0 | 0 | 0 | 270 | 14 | 182 | 8 | 0 | 28 | 25 | 0 | 10 | 0 | 0 | 16 | 19 | 11 | 33 | 21 | 126 | 82 | 0 | 19 | 0 | 41 | 42 | 22 | 20 | 80 | 0 | 65 | 40 | 0 | 0 | 0 | 0 | 8 | 280 | 16 | 8 | 0 | 0 | 0 | 0 | 47 | 0 | 55 | 0 | 76 | 51 | 5 | 365 | 49 | 17 | 34 | 0 | 100 | 17 | 54 | 0 | 6 | 12 | 370 | 0 | 0 | 17 | 89 | 0 | 17 | 0 | 52 | 0 | 250 | 0 | 0 |  | 910 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 201 | 608 | 0 | 0 |  | 5591 | 4122 | 9713 | 3595 | 910 | 1927 | 0 | 927 | 2171 | 25 | 0 | 32 | 126 | 0 | 0 | 76.9
2:00 | 0 | 0 | 0 | 180 | 0 | 43 | 0 | 343 | 282 |  | 0 | 340 | 271 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 17 | 27 | 33 | 29 | 0 | 0 | 25 | 0 | 135 | 0 | 0 | 227 | 0 | 0 | 0 |  | 17 | 0 | 0 | 10 | 5 | 20 | 5 | 39 | 0 | 0 | 0 | 270 | 66 | 159 | 8 | 0 | 30 | 15 | 0 | 10 | 0 | 0 | 16 | 19 | 11 | 33 | 21 | 122 | 83 | 0 | 19 | 0 | 41 | 42 | 22 | 20 | 80 | 0 | 65 | 89 | 0 | 0 | 0 | 0 | 8 | 260 | 16 | 8 | 0 | 0 | 0 | 0 | 47 | 0 | 17 | 0 | 76 | 51 | 5 | 367 | 49 | 52 | 34 | 0 | 100 | 17 | 54 | 0 | 5 | 12 | 370 | 0 | 0 | 0 | 89 | 0 | 17 | 0 | 52 | 0 | 250 | 0 | 0 |  | 910 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 770 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 201 | 606 | 0 | 0 |  | 5471 | 3999 | 9470 | 3583 | 910 | 1828 | 0 | 849 | 2121 | 25 | 0 | 32 | 122 | 0 | 0 | 76.9
3:00 | 0 | 0 | 0 | 180 | 0 | 43 | 0 | 335 | 283 |  | 0 | 420 | 300 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 17 | 27 | 33 | 30 | 0 | 0 | 25 | 0 | 135 | 0 | 0 | 225 | 0 | 0 | 0 |  | 18 | 0 | 0 | 10 | 5 | 20 | 5 | 39 | 0 | 0 | 0 | 270 | 95 | 151 | 8 | 0 | 30 | 5 | 0 | 10 | 0 | 0 | 16 | 19 | 11 | 33 | 21 | 120 | 82 | 0 | 19 | 0 | 41 | 42 | 53 | 46 | 80 | 0 | 65 | 89 | 0 | 0 | 0 | 0 | 8 | 270 | 16 | 8 | 0 | 0 | 0 | 0 | 43 | 0 | 17 | 0 | 76 | 51 | 5 | 365 | 77 | 70 | 34 | 0 | 100 | 17 | 46 | 0 | 9 | 12 | 400 | 0 | 0 | 0 | 89 | 0 | 17 | 0 | 52 | 0 | 240 | 0 | 0 |  | 909 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 790 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 202 | 598 | 0 | 0 |  | 5736 | 4062 | 9798 | 3612 | 909 | 2045 | 0 | 888 | 2135 | 25 | 0 | 64 | 120 | 0 | 0 | 76.9
4:00 | 0 | 0 | 0 | 180 | 0 | 43 | 0 | 371 | 348 |  | 0 | 420 | 291 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 17 | 27 | 28 | 30 | 0 | 0 | 25 | 0 | 135 | 0 | 0 | 224 | 0 | 0 | 0 |  | 18 | 0 | 0 | 10 | 5 | 20 | 5 | 40 | 0 | 0 | 0 | 270 | 95 | 144 | 8 | 0 | 30 | 5 | 0 | 10 | 0 | 0 | 16 | 19 | 11 | 33 | 21 | 120 | 83 | 0 | 19 | 0 | 41 | 42 | 53 | 50 | 80 | 0 | 64 | 89 | 0 | 0 | 0 | 0 | 8 | 270 | 14 | 8 | 0 | 0 | 0 | 0 | 75 | 0 | 17 | 0 | 76 | 51 | 5 | 365 | 78 | 70 | 34 | 0 | 50 | 17 | 54 | 0 | 9 | 12 | 400 | 0 | 0 | 0 | 82 | 0 | 17 | 0 | 52 | 0 | 240 | 0 | 0 |  | 909 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 810 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 200 | 598 | 0 | 0 |  | 5802 | 4091 | 9893 | 3638 | 909 | 2113 | 0 | 872 | 2152 | 25 | 0 | 64 | 120 | 0 | 0 | 76.9
5:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 368 | 307 |  | 0 | 400 | 288 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 17 | 20 | 28 | 30 | 0 | 0 | 25 | 0 | 135 | 0 | 0 | 229 | 0 | 0 | 0 |  | 18 | 0 | 0 | 10 | 5 | 20 | 5 | 38 | 0 | 0 | 0 | 270 | 114 | 137 | 8 | 0 | 30 | 5 | 0 | 10 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 118 | 83 | 0 | 19 | 0 | 41 | 42 | 53 | 50 | 80 | 0 | 64 | 89 | 0 | 0 | 0 | 0 | 8 | 270 | 8 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 17 | 0 | 20 | 17 | 0 | 367 | 55 | 34 | 17 | 0 | 0 | 17 | 17 | 0 | 9 | 0 | 380 | 0 | 0 | 0 | 51 | 0 | 14 | 0 | 52 | 0 | 230 | 0 | 0 |  | 910 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 150 | 588 | 0 | 0 |  | 5156 | 3700 | 8856 | 3556 | 910 | 2007 | 0 | 397 | 1843 | 25 | 0 | 0 | 118 | 0 | 0 | 76.9
6:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 318 | 275 |  | 0 | 350 | 266 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 17 | 27 | 28 | 30 | 0 | 0 | 25 | 0 | 135 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 6 | 20 | 5 | 36 | 0 | 0 | 0 | 270 | 66 | 167 | 8 | 0 | 10 | 5 | 0 | 10 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 100 | 83 | 0 | 19 | 0 | 41 | 42 | 11 | 10 | 80 | 0 | 40 | 20 | 0 | 0 | 0 | 0 | 8 | 260 | 8 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 17 | 0 | 20 | 17 | 0 | 323 | 45 | 0 | 17 | 0 | 0 | 17 | 17 | 0 | 9 | 0 | 330 | 0 | 0 | 0 | 51 | 0 | 17 | 0 | 17 | 0 | 230 | 0 | 0 |  | 839 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 151 | 605 | 0 | 0 |  | 4577 | 3436 | 8013 | 3305 | 839 | 1645 | 0 | 304 | 1795 | 25 | 0 | 0 | 100 | 0 | 0 | 76.9
7:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 302 | 259 |  | 0 | 330 | 300 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 17 | 27 | 28 | 33 | 0 | 0 | 25 | 0 | 135 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 6 | 20 | 5 | 42 | 0 | 0 | 0 | 270 | 80 | 178 | 8 | 0 | 10 | 5 | 0 | 10 | 0 | 0 | 0 | 19 | 11 | 8 | 21 | 104 | 85 | 0 | 19 | 0 | 41 | 42 | 11 | 10 | 80 | 0 | 40 | 10 | 0 | 0 | 0 | 0 | 8 | 265 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 3 | 20 | 0 | 0 | 318 | 24 | 0 | 17 | 1 | 0 | 17 | 17 | 0 | 0 | 0 | 330 | 0 | 3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 240 | 0 | 0 |  | 840 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 368 | 3 | 150 | 600 | 21 | 0 |  | 4428 | 3468 | 7896 | 3293 | 840 | 1646 | 0 | 156 | 1788 | 25 | 0 | 0 | 104 | 44 | 0 | 0
8:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 302 | 283 |  | 0 | 330 | 287 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 17 | 27 | 16 | 33 | 0 | 0 | 25 | 0 | 135 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 5 | 20 | 5 | 40 | 0 | 0 | 0 | 270 | 55 | 187 | 8 | 0 | 10 | 5 | 0 | 10 | 0 | 0 | 0 | 19 | 11 | 8 | 18 | 96 | 105 | 0 | 16 | 0 | 41 | 42 | 11 | 10 | 80 | 0 | 40 | 10 | 0 | 0 | 0 | 0 | 8 | 270 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 9 | 20 | 0 | 0 | 364 | 24 | 0 | 17 | 2 | 0 | 17 | 17 | 0 | 0 | 0 | 380 | 0 | 7 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 240 | 0 | 0 |  | 815 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 540 | 0 | 0 | 0 | 1 | 34 | 0 | 0 | 0 | 367 | 9 | 151 | 605 | 62 | 0 |  | 4529 | 3559 | 8088 | 3373 | 815 | 1660 | 0 | 156 | 1833 | 25 | 0 | 0 | 96 | 130 | 0 | 76.89
9:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 350 | 352 |  | 0 | 370 | 278 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 17 | 27 | 25 | 33 | 0 | 0 | 25 | 0 | 130 | 0 | 0 | 227 | 0 | 0 | 0 |  | 1 | 0 | 0 | 10 | 6 | 20 | 5 | 38 | 0 | 0 | 0 | 270 | 70 | 199 | 0 | 0 | 10 | 5 | 0 | 10 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 110 | 106 | 0 | 16 | 1 | 41 | 42 | 28 | 26 | 80 | 0 | 40 | 30 | 0 | 0 | 0 | 0 | 8 | 270 | 8 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 14 | 20 | 13 | 0 | 365 | 73 | 0 | 0 | 3 | 15 | 17 | 24 | 0 | 2 | 0 | 400 | 0 | 7 | 0 | 0 | 0 | 0 | 18 | 33 | 0 | 240 | 0 | 0 |  | 840 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 169 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 560 | 0 | 0 | 0 | 3 | 59 | 0 | 0 | 0 | 374 | 19 | 150 | 607 | 103 | 0 |  | 4943 | 3675 | 8618 | 3490 | 840 | 1806 | 0 | 259 | 1860 | 25 | 0 | 0 | 110 | 228 | 0 | 76.89
10:00 | 0 | 0 | 0 | 180 | 0 | 55 | 0 | 360 | 342 |  | 0 | 400 | 285 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 17 | 25 | 25 | 33 | 0 | 0 | 25 | 0 | 130 | 0 | 0 | 224 | 0 | 0 | 0 |  | 18 | 0 | 0 | 10 | 5 | 20 | 5 | 20 | 0 | 0 | 0 | 270 | 95 | 212 | 0 | 0 | 10 | 5 | 0 | 24 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 116 | 105 | 0 | 16 | 2 | 41 | 42 | 53 | 50 | 112 | 0 | 63 | 86 | 0 | 0 | 0 | 0 | 8 | 280 | 8 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 19 | 18 | 40 | 19 | 0 | 316 | 88 | 0 | 0 | 4 | 45 | 17 | 51 | 0 | 9 | 0 | 370 | 0 | 20 | 0 | 0 | 0 | 0 | 27 | 54 | 0 | 240 | 0 | 0 |  | 862 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 570 | 0 | 0 | 0 | 4 | 80 | 0 | 0 | 0 | 367 | 26 | 150 | 610 | 148 | 0 |  | 5414 | 3751 | 9165 | 3517 | 862 | 1990 | 0 | 457 | 1867 | 25 | 0 | 0 | 116 | 331 | 0 | 76.88
11:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 353 | 332 |  | 0 | 400 | 278 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 17 | 27 | 25 | 33 | 0 | 0 | 25 | 0 | 130 | 0 | 0 | 222 | 0 | 0 | 0 |  | 18 | 0 | 0 | 41 | 5 | 20 | 5 | 28 | 0 | 0 | 0 | 270 | 110 | 216 | 0 | 0 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 116 | 105 | 0 | 16 | 2 | 41 | 42 | 53 | 50 | 112 | 0 | 63 | 86 | 0 | 0 | 0 | 0 | 8 | 280 | 8 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 34 | 20 | 76 | 35 | 0 | 316 | 98 | 0 | 1 | 4 | 45 | 17 | 52 | 0 | 9 | 1 | 370 | 0 | 43 | 0 | 0 | 0 | 4 | 31 | 65 | 0 | 240 | 0 | 0 |  | 899 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 1 | 0 | 30 | 0 | 3 | 0 | 580 | 0 | 0 | 0 | 5 | 90 | 2 | 0 | 0 | 370 | 28 | 150 | 611 | 141 | 0 |  | 5617 | 3877 | 9494 | 3528 | 899 | 2062 | 0 | 616 | 1881 | 25 | 0 | 0 | 116 | 367 | 0 | 76.88
12:00 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 378 | 312 |  | 0 | 400 | 272 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 17 | 26 | 25 | 33 | 0 | 0 | 25 | 0 | 130 | 0 | 0 | 225 | 0 | 0 | 0 |  | 18 | 0 | 0 | 44 | 5 | 20 | 5 | 31 | 0 | 0 | 0 | 270 | 135 | 215 | 0 | 0 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 128 | 102 | 0 | 16 | 2 | 41 | 42 | 50 | 50 | 112 | 0 | 63 | 89 | 0 | 0 | 0 | 0 | 8 | 270 | 8 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 35 | 20 | 76 | 64 | 0 | 365 | 99 | 3 | 17 | 2 | 45 | 17 | 54 | 0 | 9 | 12 | 400 | 0 | 32 | 0 | 11 | 0 | 17 | 32 | 115 | 0 | 240 | 0 | 0 |  | 900 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 35 | 0 | 34 | 0 | 4 | 0 | 670 | 0 | 0 | 0 | 5 | 93 | 34 | 0 | 0 | 366 | 33 | 148 | 604 | 140 | 0 |  | 5856 | 4118 | 9974 | 3655 | 900 | 2119 | 0 | 826 | 1958 | 25 | 0 | 0 | 128 | 363 | 0 | 76.88
13:00 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 405 | 303 |  | 0 | 380 | 265 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 17 | 26 | 25 | 33 | 0 | 0 | 25 | 0 | 125 | 0 | 0 | 220 | 0 | 0 | 0 |  | 18 | 0 | 0 | 44 | 6 | 20 | 5 | 31 | 0 | 0 | 0 | 270 | 180 | 207 | 0 | 0 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 138 | 102 | 0 | 16 | 2 | 41 | 42 | 53 | 49 | 112 | 0 | 60 | 89 | 0 | 0 | 0 | 0 | 8 | 280 | 16 | 8 | 0 | 0 | 0 | 0 | 12 | 0 | 35 | 19 | 88 | 71 | 0 | 375 | 100 | 17 | 21 | 4 | 45 | 17 | 54 | 0 | 9 | 15 | 394 | 0 | 49 | 1 | 89 | 0 | 17 | 31 | 115 | 0 | 240 | 0 | 0 |  | 900 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415 | 0 | 0 | 35 | 0 | 47 | 0 | 4 | 0 | 780 | 0 | 0 | 0 | 5 | 91 | 36 | 0 | 0 | 367 | 31 | 149 | 595 | 160 | 0 |  | 6067 | 4417 | 10484 | 3843 | 900 | 2155 | 0 | 966 | 2061 | 25 | 0 | 0 | 138 | 396 | 0 | 76.87
14:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 406 | 282 |  | 0 | 360 | 255 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 19 | 17 | 26 | 25 | 31 | 18 | 0 | 25 | 0 | 125 | 0 | 0 | 223 | 0 | 0 | 0 |  | 18 | 0 | 30 | 44 | 4 | 20 | 5 | 36 | 0 | 0 | 0 | 225 | 235 | 178 | 0 | 0 | 10 | 5 | 0 | 51 | 0 | 0 | 19 | 18 | 11 | 33 | 15 | 142 | 102 | 0 | 16 | 2 | 41 | 42 | 53 | 46 | 112 | 0 | 60 | 89 | 0 | 0 | 0 | 0 | 8 | 270 | 16 | 8 | 0 | 30 | 0 | 0 | 65 | 0 | 35 | 0 | 100 | 122 | 32 | 368 | 98 | 70 | 34 | 4 | 45 | 17 | 54 | 0 | 9 | 62 | 400 | 1 | 43 | 17 | 89 | 0 | 17 | 27 | 98 | 0 | 240 | 0 | 0 |  | 900 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 421 | 0 | 0 | 35 | 0 | 95 | 0 | 5 | 0 | 840 | 0 | 0 | 0 | 5 | 80 | 17 | 0 | 0 | 366 | 27 | 200 | 592 | 97 | 0 |  | 6324 | 4458 | 10782 | 3791 | 900 | 2100 | 0 | 1336 | 2168 | 25 | 0 | 30 | 142 | 290 | 10 | 76.88
15:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 402 | 282 |  | 0 | 360 | 247 | 6 | 12 | 5 | 145 | 0 | 0 | 5 | 8 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 19 | 17 | 26 | 25 | 31 | 42 | 0 | 25 | 0 | 125 | 0 | 0 | 222 | 0 | 0 | 0 |  | 18 | 0 | 34 | 44 | 5 | 19 | 5 | 37 | 0 | 0 | 0 | 70 | 260 | 192 | 0 | 0 | 10 | 5 | 0 | 51 | 0 | 0 | 50 | 18 | 8 | 33 | 15 | 140 | 102 | 0 | 16 | 2 | 41 | 42 | 53 | 49 | 80 | 0 | 61 | 89 | 0 | 0 | 0 | 0 | 8 | 260 | 16 | 8 | 0 | 30 | 0 | 0 | 140 | 0 | 34 | 14 | 100 | 161 | 103 | 368 | 88 | 70 | 34 | 3 | 45 | 17 | 54 | 0 | 9 | 100 | 350 | 15 | 33 | 17 | 89 | 0 | 17 | 21 | 92 | 0 | 240 | 0 | 0 |  | 900 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 50 | 0 | 106 | 0 | 4 | 0 | 750 | 0 | 0 | 0 | 3 | 65 | 35 | 0 | 0 | 369 | 21 | 199 | 583 | 89 | 0 |  | 6415 | 4332 | 10747 | 3618 | 900 | 2013 | 0 | 1691 | 2071 | 25 | 0 | 34 | 140 | 255 | 17 | 76.87
16:00 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 374 | 292 |  | 0 | 360 | 252 | 8 | 17 | 15 | 146 | 0 | 0 | 9 | 8 | 7 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 19 | 17 | 26 | 25 | 31 | 42 | 0 | 25 | 0 | 125 | 0 | 0 | 225 | 0 | 0 | 0 |  | 18 | 0 | 34 | 55 | 5 | 20 | 5 | 37 | 0 | 0 | 0 | 0 | 320 | 194 | 0 | 0 | 30 | 20 | 0 | 51 | 0 | 0 | 8 | 18 | 8 | 33 | 15 | 130 | 99 | 0 | 19 | 1 | 41 | 42 | 50 | 49 | 80 | 0 | 61 | 89 | 0 | 0 | 0 | 0 | 8 | 280 | 16 | 8 | 0 | 30 | 0 | 0 | 111 | 0 | 27 | 9 | 100 | 180 | 132 | 368 | 49 | 90 | 34 | 2 | 30 | 17 | 54 | 0 | 9 | 60 | 350 | 17 | 19 | 17 | 89 | 0 | 17 | 13 | 93 | 0 | 240 | 0 | 0 |  | 900 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 35 | 0 | 107 | 0 | 2 | 0 | 750 | 0 | 0 | 0 | 2 | 40 | 35 | 60 | 0 | 319 | 14 | 200 | 613 | 71 | 0 |  | 6353 | 4296 | 10649 | 3586 | 900 | 2073 | 0 | 1609 | 2052 | 25 | 60 | 41 | 130 | 173 | 0 | 76.86
17:00 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 373 | 282 |  | 0 | 350 | 245 | 9 | 17 | 15 | 145 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 22 | 17 | 26 | 33 | 32 | 50 | 0 | 25 | 0 | 130 | 0 | 0 | 224 | 0 | 0 | 0 |  | 18 | 0 | 34 | 10 | 6 | 20 | 5 | 42 | 0 | 0 | 0 | 0 | 350 | 200 | 0 | 0 | 30 | 30 | 0 | 51 | 0 | 0 | 8 | 18 | 11 | 33 | 15 | 134 | 100 | 0 | 19 | 0 | 41 | 42 | 53 | 49 | 80 | 0 | 60 | 89 | 0 | 0 | 0 | 0 | 8 | 280 | 16 | 8 | 0 | 30 | 0 | 0 | 115 | 0 | 17 | 3 | 50 | 136 | 137 | 368 | 49 | 90 | 34 | 1 | 30 | 17 | 54 | 0 | 23 | 60 | 350 | 17 | 7 | 17 | 89 | 0 | 17 | 3 | 56 | 0 | 240 | 0 | 0 |  | 900 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 17 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 35 | 0 | 70 | 0 | 2 | 0 | 740 | 0 | 0 | 0 | 0 | 8 | 35 | 50 | 0 | 303 | 6 | 171 | 613 | 31 | 0 |  | 6208 | 4123 | 10331 | 3644 | 900 | 2064 | 0 | 1400 | 1997 | 25 | 50 | 56 | 134 | 61 | 0 | 76.86
18:00 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 371 | 281 |  | 0 | 350 | 235 | 12 | 18 | 16 | 145 | 0 | 0 | 14 | 24 | 32 | 0 | 0 | 0 | 0 | 35 | 17 | 25 | 22 | 17 | 26 | 33 | 16 | 51 | 0 | 25 | 0 | 0 | 0 | 1 | 228 | 0 | 0 | 0 |  | 18 | 0 | 34 | 10 | 6 | 19 | 5 | 42 | 0 | 0 | 0 | 0 | 355 | 202 | 0 | 0 | 30 | 30 | 0 | 51 | 0 | 0 | 12 | 18 | 11 | 33 | 15 | 152 | 102 | 0 | 19 | 0 | 41 | 42 | 53 | 49 | 112 | 0 | 61 | 86 | 0 | 0 | 0 | 0 | 8 | 275 | 16 | 8 | 0 | 35 | 0 | 0 | 145 | 0 | 41 | 0 | 50 | 136 | 134 | 368 | 80 | 90 | 34 | 0 | 65 | 17 | 54 | 34 | 40 | 60 | 335 | 18 | 0 | 30 | 89 | 0 | 17 | 0 | 52 | 0 | 240 | 0 | 0 |  | 893 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 20 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 40 | 0 | 106 | 0 | 0 | 30 | 680 | 0 | 0 | 0 | 0 | 1 | 52 | 50 | 0 | 302 | 0 | 173 | 609 | 3 | 0 |  | 6331 | 4021 | 10352 | 3457 | 893 | 2008 | 0 | 1727 | 1934 | 25 | 50 | 102 | 152 | 4 | 6 | 76.85
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 42 | 0 | 331 | 257 |  | 0 | 310 | 227 | 39 | 58 | 36 | 130 | 0 | 0 | 40 | 24 | 32 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 17 | 26 | 33 | 10 | 51 | 0 | 25 | 0 | 0 | 0 | 23 | 184 | 0 | 0 | 0 |  | 18 | 0 | 34 | 10 | 5 | 19 | 5 | 42 | 0 | 0 | 0 | 0 | 280 | 210 | 0 | 0 | 37 | 30 | 0 | 35 | 0 | 0 | 30 | 18 | 11 | 0 | 18 | 114 | 102 | 0 | 19 | 0 | 40 | 42 | 53 | 49 | 80 | 0 | 61 | 86 | 0 | 0 | 0 | 0 | 8 | 260 | 16 | 8 | 0 | 80 | 0 | 0 | 155 | 0 | 138 | 0 | 65 | 120 | 130 | 354 | 89 | 105 | 34 | 0 | 65 | 17 | 54 | 14 | 75 | 60 | 360 | 37 | 0 | 90 | 89 | 0 | 17 | 0 | 52 | 0 | 240 | 0 | 0 |  | 905 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 35 | 21 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 81 | 0 | 107 | 0 | 0 | 35 | 600 | 0 | 0 | 0 | 0 | 0 | 72 | 50 | 0 | 309 | 0 | 147 | 599 | 0 | 0 |  | 6403 | 3963 | 10366 | 3260 | 905 | 1818 | 0 | 2268 | 1825 | 25 | 50 | 101 | 114 | 0 | 47 | 76.84
19:30 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 351 | 257 |  | 0 | 310 | 271 | 42 | 55 | 40 | 133 | 0 | 0 | 40 | 24 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 17 | 26 | 33 | 33 | 51 | 0 | 25 | 0 | 0 | 0 | 8 | 182 | 0 | 0 | 0 |  | 8 | 0 | 34 | 10 | 5 | 19 | 5 | 42 | 0 | 0 | 0 | 0 | 280 | 204 | 0 | 0 | 45 | 30 | 0 | 51 | 0 | 0 | 16 | 18 | 0 | 10 | 18 | 106 | 115 | 0 | 0 | 0 | 38 | 42 | 53 | 49 | 80 | 0 | 60 | 86 | 0 | 0 | 0 | 0 | 8 | 280 | 16 | 8 | 0 | 45 | 0 | 0 | 155 | 0 | 149 | 0 | 100 | 120 | 133 | 368 | 89 | 105 | 34 | 0 | 50 | 17 | 54 | 0 | 75 | 30 | 360 | 69 | 0 | 90 | 89 | 0 | 17 | 0 | 52 | 0 | 240 | 0 | 0 |  | 914 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 22 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 94 | 0 | 107 | 0 | 0 | 35 | 690 | 0 | 0 | 0 | 0 | 0 | 72 | 50 | 0 | 309 | 0 | 152 | 582 | 0 | 0 |  | 6515 | 4079 | 10594 | 3330 | 914 | 1937 | 0 | 2243 | 1903 | 25 | 50 | 86 | 106 | 0 | 30 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 351 | 257 |  | 0 | 310 | 266 | 40 | 53 | 36 | 130 | 0 | 0 | 40 | 24 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 17 | 26 | 33 | 33 | 51 | 0 | 25 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 |  | 10 | 0 | 34 | 10 | 4 | 20 | 5 | 42 | 0 | 0 | 0 | 0 | 280 | 208 | 0 | 0 | 45 | 40 | 0 | 51 | 0 | 0 | 16 | 18 | 0 | 33 | 18 | 120 | 132 | 0 | 0 | 0 | 38 | 42 | 53 | 49 | 80 | 0 | 60 | 86 | 0 | 0 | 0 | 0 | 8 | 280 | 8 | 8 | 0 | 30 | 0 | 0 | 164 | 0 | 149 | 0 | 100 | 120 | 134 | 368 | 89 | 105 | 34 | 0 | 50 | 17 | 54 | 0 | 76 | 30 | 360 | 68 | 0 | 90 | 89 | 0 | 17 | 0 | 52 | 0 | 240 | 0 | 0 |  | 914 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 21 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 94 | 0 | 107 | 0 | 0 | 35 | 680 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 309 | 0 | 152 | 609 | 0 | 0 |  | 6548 | 4048 | 10596 | 3365 | 914 | 1942 | 0 | 2224 | 1920 | 25 | 0 | 86 | 120 | 0 | 0 | 76.84
21:00 | 0 | 0 | 0 | 180 | 0 | 77 | 0 | 381 | 272 |  | 0 | 360 | 238 | 0 | 50 | 42 | 160 | 0 | 0 | 40 | 8 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 17 | 26 | 33 | 33 | 51 | 0 | 25 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 18 | 0 | 34 | 22 | 5 | 20 | 0 | 42 | 0 | 0 | 0 | 0 | 110 | 217 | 0 | 0 | 47 | 48 | 0 | 51 | 0 | 0 | 16 | 18 | 0 | 33 | 18 | 132 | 151 | 0 | 0 | 0 | 38 | 42 | 53 | 49 | 112 | 0 | 61 | 86 | 0 | 0 | 0 | 0 | 10 | 270 | 8 | 8 | 0 | 30 | 0 | 0 | 164 | 0 | 135 | 0 | 100 | 120 | 143 | 368 | 89 | 105 | 34 | 0 | 30 | 17 | 54 | 0 | 76 | 30 | 400 | 71 | 0 | 110 | 89 | 0 | 17 | 0 | 52 | 0 | 260 | 0 | 0 |  | 893 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 22 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 94 | 15 | 107 | 0 | 0 | 35 | 680 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 356 | 0 | 154 | 599 | 0 | 0 |  | 6616 | 4160 | 10776 | 3409 | 893 | 2070 | 0 | 2203 | 1959 | 25 | 0 | 85 | 132 | 0 | 0 | 76.84
22:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 406 | 287 |  | 0 | 370 | 239 | 0 | 15 | 42 | 155 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 17 | 28 | 33 | 33 | 33 | 0 | 25 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 18 | 0 | 34 | 22 | 5 | 20 | 5 | 42 | 0 | 0 | 0 | 0 | 120 | 220 | 0 | 0 | 48 | 52 | 0 | 51 | 0 | 0 | 16 | 18 | 11 | 33 | 18 | 132 | 152 | 0 | 0 | 0 | 38 | 42 | 53 | 49 | 112 | 0 | 62 | 84 | 0 | 0 | 0 | 0 | 10 | 260 | 8 | 8 | 0 | 0 | 0 | 0 | 164 | 0 | 71 | 0 | 100 | 120 | 140 | 367 | 89 | 105 | 34 | 0 | 0 | 17 | 54 | 0 | 55 | 12 | 360 | 0 | 0 | 72 | 89 | 0 | 17 | 0 | 52 | 0 | 240 | 0 | 0 |  | 892 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 18 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 94 | 15 | 49 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 376 | 0 | 151 | 610 | 0 | 0 |  | 6249 | 3985 | 10234 | 3382 | 892 | 2052 | 0 | 1699 | 1967 | 25 | 0 | 85 | 132 | 0 | 0 | 76.83
23:00 | 0 | 0 | 0 | 180 | 0 | 42 | 0 | 377 | 322 |  | 0 | 330 | 234 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 0 | 28 | 33 | 33 | 8 | 0 | 25 | 0 | 0 | 0 | 0 | 207 | 0 | 0 | 0 |  | 18 | 0 | 34 | 33 | 5 | 19 | 5 | 42 | 0 | 0 | 0 | 0 | 120 | 219 | 0 | 0 | 48 | 53 | 0 | 10 | 0 | 0 | 0 | 18 | 11 | 33 | 18 | 130 | 154 | 0 | 19 | 0 | 38 | 42 | 53 | 10 | 80 | 0 | 62 | 84 | 0 | 0 | 0 | 0 | 10 | 260 | 8 | 8 | 0 | 0 | 0 | 0 | 35 | 0 | 42 | 0 | 100 | 51 | 10 | 318 | 65 | 17 | 34 | 0 | 0 | 17 | 54 | 0 | 15 | 12 | 360 | 0 | 0 | 0 | 91 | 0 | 17 | 0 | 52 | 0 | 240 | 0 | 0 |  | 891 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 3 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 15 | 34 | 0 | 0 | 0 | 650 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 373 | 0 | 153 | 615 | 0 | 0 |  | 5172 | 3841 | 9013 | 3256 | 891 | 1884 | 0 | 796 | 1961 | 25 | 0 | 70 | 130 | 0 | 0 | 76.83
24:00 | 0 | 0 | 0 | 180 | 0 | 42 | 0 | 364 | 303 |  | 0 | 330 | 270 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 28 | 16 | 33 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 207 | 0 | 0 | 0 |  | 18 | 0 | 34 | 44 | 5 | 19 | 5 | 42 | 0 | 0 | 0 | 0 | 18 | 186 | 0 | 0 | 48 | 52 | 0 | 10 | 0 | 0 | 0 | 18 | 11 | 33 | 18 | 124 | 153 | 0 | 19 | 0 | 41 | 42 | 11 | 10 | 80 | 0 | 62 | 84 | 0 | 0 | 0 | 0 | 10 | 280 | 8 | 8 | 0 | 0 | 0 | 0 | 35 | 0 | 16 | 0 | 100 | 51 | 0 | 327 | 35 | 0 | 28 | 0 | 15 | 17 | 54 | 0 | 9 | 45 | 340 | 0 | 0 | 0 | 89 | 0 | 17 | 0 | 34 | 0 | 240 | 0 | 0 |  | 892 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 15 | 34 | 0 | 0 | 0 | 630 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 373 | 0 | 153 | 610 | 0 | 0 |  | 4922 | 3759 | 8681 | 3079 | 892 | 1876 | 0 | 715 | 1936 | 25 | 0 | 34 | 124 | 0 | 0 | 76.82
KWH | 0 | 0 | 0 | 4362750 | 0 | 1304727 | 0 | 8816640 | 7054000 |  | 0 | 8345250 | 6429295 | 113280 | 220659 | 212238 | 3194910 | 0 | 0 | 146563 | 115776 | 312480 | 0 | 0 | 0 | 0 | 872280 | 176879 | 358065 | 443988 | 408000 | 619020 | 712200 | 752200 | 404640 | 0 | 603600 | 0 | 2300000 | 0 | 31703 | 5121909 | 0 | 0 | 0 |  | 369840 | 0 | 377792 | 531360 | 143040 | 479520 | 116064 | 959520 | 0 | 0 | 0 | 4124800 | 3625000 | 4636000 | 0 | 0 | 606024 | 491520 | 0 | 888973 | 0 | 0 | 263558 | 425124 | 210240 | 739800 | 436660 | 2952000 | 2454720 | 0 | 360864 | 12550 | 952000 | 970440 | 988800 | 923616 | 2201727 | 0 | 1394496 | 1743360 | 0 | 0 | 0 | 0 | 194220 | 6614500 | 270432 | 176352 | 0 | 918327 | 0 | 0 | 1672800 | 0 | 1049040 | 129735 | 1673280 | 1846560 | 1185963 | 8593000 | 1654800 | 1159680 | 649018 | 30238 | 978545 | 450996 | 1153345 | 36480 | 502320 | 704448 | 8839400 | 286080 | 242390 | 527040 | 1570691 | 0 | 362520 | 209872 | 1457280 | 0 | 5834800 | 0 | 0 |  | 21498909 | 0 | 5284800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4041518 | 371000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5578 | 227892 | 409200 | 0 | 210906 | 0 | 0 | 4137000 | 0 | 0 | 3922991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7953818 | 0 | 0 | 889728 | 52128 | 1148592 | 0 | 32231 | 158208 | 18045200 | 0 | 0 | 0 | 36720 | 658800 | 616320 | 183665 | 0 | 8581818 | 226700 | 4058200 | 14558182 | 1106450 | 0 |  | 138786612 | 98416554 | 237203166 | 84958048 | 21498909 | 46873526 | 0 | 27149168 | 49380400 | 603600 | 183665 | 918164 | 2952000 | 2685686 | 0
Fuel Cost | 0 | 0 | 0 | 6500497.5 | 0 | 1735286.91 | 0 | 9257472 | 7618320 |  | 0 | 9096322.5 | 7136517.45 | 1266470.4 | 2923731.75 | 2812153.5 | 3578299.2 | 0 | 0 | 2142751.06 | 1628968.32 | 5065300.8 | 0 | 0 | 0 | 0 | 11095401.6 | 2387866.5 | 4801651.65 | 332991 | 306000 | 0 | 0 | 0 | 6882926.4 | 0 | 162972 | 0 | 4347000 | 0 | 518344.05 | 5326785.36 | 0 | 0 | 0 |  | 4826412 | 0 | 6430019.84 | 7178673.6 | 1813747.2 | 5548046.4 | 147401.28 | 3195201.6 | 0 | 0 | 0 | 4578528 | 3951250 | 5377760 | 0 | 0 | 684807.12 | 732364.8 | 0 | 1484584.91 | 0 | 0 | 3544855.1 | 582419.88 | 157680 | 1294650 | 327495 | 21195360 | 2675644.8 | 0 | 490775.04 | 200047 | 1304240 | 1280980.8 | 1720512 | 1597855.68 | 2531986.05 | 0 | 2705322.24 | 3974860.8 | 0 | 0 | 0 | 0 | 384555.6 | 6614500 | 202824 | 134027.52 | 0 | 12535163.55 | 0 | 0 | 22549344 | 0 | 14529204 | 1516602.15 | 17268249.6 | 25224009.6 | 15737729.01 | 7905560 | 20122368 | 16768972.8 | 8210077.7 | 0 | 11488118.3 | 4911346.44 | 12260057.35 | 495033.6 | 6474904.8 | 8298397.44 | 8132248 | 3704736 | 3502535.5 | 6688137.6 | 17874463.58 | 0 | 4734511.2 | 2507970.4 | 21815481.6 | 0 | 0 | 0 | 0 |  | 64496727 | 0 | 5918976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4526500.16 | 719740 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76028.14 | 3844538.04 | 847044 | 0 | 159655.842 | 0 | 0 | 21884730 | 0 | 0 | 4550669.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7874279.82 | 0 | 0 | 10525482.24 | 753249.6 | 14587118.4 | 0 | 356152.55 | 1920645.12 | 162587252 | 0 | 0 | 0 | 415303.2 | 7727724 | 9448185.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 471048640.43 | 323220001.272 | 794268641.702 | 86738460.302 | 64496727 | 57263932.12 | 0 | 348373014.8 | 184471982 | 162972 | 0 | 15339858.68 | 21195360 | 16226334.8 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 378 | 312 |  | 0 | 400 | 272 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 17 | 26 | 25 | 33 | 0 | 0 | 25 | 0 | 130 | 0 | 0 | 225 | 0 | 0 | 0 |  | 18 | 0 | 0 | 44 | 5 | 20 | 5 | 31 | 0 | 0 | 0 | 270 | 135 | 215 | 0 | 0 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 128 | 102 | 0 | 16 | 2 | 41 | 42 | 50 | 50 | 112 | 0 | 63 | 89 | 0 | 0 | 0 | 0 | 8 | 270 | 8 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 35 | 20 | 76 | 64 | 0 | 365 | 99 | 3 | 17 | 2 | 45 | 17 | 54 | 0 | 9 | 12 | 400 | 0 | 32 | 0 | 11 | 0 | 17 | 32 | 115 | 0 | 240 | 0 | 0 |  | 900 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 35 | 0 | 34 | 0 | 4 | 0 | 670 | 0 | 0 | 0 | 5 | 93 | 34 | 0 | 0 | 366 | 33 | 148 | 604 | 140 | 0 |  | 9974 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 77 | 0 | 381 | 272 | 0 | 0 | 360 | 238 | 0 | 50 | 42 | 160 | 0 | 0 | 40 | 8 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 17 | 26 | 33 | 33 | 51 | 0 | 25 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 18 | 0 | 34 | 22 | 5 | 20 | 0 | 42 | 0 | 0 | 0 | 0 | 110 | 217 | 0 | 0 | 47 | 48 | 0 | 51 | 0 | 0 | 16 | 18 | 0 | 33 | 18 | 132 | 151 | 0 | 0 | 0 | 38 | 42 | 53 | 49 | 112 | 0 | 61 | 86 | 0 | 0 | 0 | 0 | 10 | 270 | 8 | 8 | 0 | 30 | 0 | 0 | 164 | 0 | 135 | 0 | 100 | 120 | 143 | 368 | 89 | 105 | 34 | 0 | 30 | 17 | 54 | 0 | 76 | 30 | 400 | 71 | 0 | 110 | 89 | 0 | 17 | 0 | 52 | 0 | 260 | 0 | 0 |  | 893 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 22 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 94 | 15 | 107 | 0 | 0 | 35 | 680 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 356 | 0 | 154 | 599 | 0 | 0 |  | 10776 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 400 | 300 | 0 | 0 | 400 | 270 | 92 | 80 | 55 | 160 | 0 | 0 | 90 | 102 | 115 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 17 | 28 | 33 | 33 | 51 | 0 | 25 | 0 | 0 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 18 | 40 | 85 | 55 | 5 | 20 | 5 | 15 | 0 | 0 | 0 | 0 | 240 | 210 | 0 | 0 | 47 | 53 | 0 | 51 | 0 | 35 | 52 | 19 | 11 | 33 | 18 | 153 | 100 | 0 | 19 | 0 | 44 | 42 | 51 | 50 | 112 | 0 | 65 | 86 | 0 | 0 | 0 | 0 | 10 | 300 | 16 | 8 |  | 300 | 0 | 0 | 160 | 0 | 149 | 0 | 100 | 180 | 150 | 368 | 115 | 105 | 34 | 0 | 230 | 17 | 54 | 114 | 113 | 100 | 400 | 72 | 0 | 162 | 107 | 0 | 54 |  | 115 | 0 | 320 |  |  |  | 909 | 0 | 200 |  | 99 | 0 | 0 | 0 | 40 | 65 | 40 | 170 | 22 | 48 | 0 | 0 | 0 | 32 | 32 | 85 | 0 | 50 | 40 | 34 | 35 | 22 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 180 |  | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 50 | 0 | 95 | 100 | 107 | 0 | 0 | 113 | 900 | 0 |  | 0 |  |  | 115 | 0 |  | 370 |  | 150 | 600 |  | 0
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 400 | 300 | 0 | 0 | 380 | 270 | 50 | 80 | 55 | 110 | 0 | 0 | 90 | 92 | 82 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 17 | 28 | 33 | 33 | 51 | 0 | 25 | 0 | 0 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 55 | 5 | 20 | 5 | 5 | 0 | 0 | 0 | 0 | 210 | 190 | 0 | 0 | 47 | 53 | 0 | 30 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 135 | 100 | 0 | 19 | 1.6 | 44 | 42 | 51 | 50 | 112 | 0 | 65 | 86 | 0 | 0 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 280 | 0 | 0 | 150 | 0 | 36 | 20 | 75 | 180 | 30 | 366 | 90 | 70 | 34 | 5 | 120 | 17 | 51 | 34 | 9 | 100 | 380 | 55 | 50 | 162 | 107 | 0 | 17 | 30 | 115 | 0 | 320 |  |  |  | 909 | 0 | 200 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 8 | 170 | 22 | 0 | 0 | 0 | 0 | 0 | 18 | 50 | 0 | 42 | 32 | 0 | 26 | 22 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 50 | 0 | 50 | 0 | 107 | 0 | 8 | 35 | 700 | 0 |  | 0 | 6 | 100 | 0 | 0 |  | 370 | 30 | 150 | 600 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 53 | 0 | 372 | 292 | 0 | 0 | 380 | 272 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 17 | 28 | 33 | 33 | 16 | 0 | 25 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 44 | 0 | 20 | 5 | 4 | 0 | 0 | 0 | 0 | 110 | 183 | 0 | 0 | 46 | 53 | 0 | 27 | 0 | 0 | 0 | 18 | 11 | 33 | 18 | 122 | 210 | 0 | 19 | 1 | 44 | 42 | 11 | 30 | 80 | 0 | 61 | 81 | 0 | 0 | 0 | 0 | 10 | 300 | 8 | 5 | 0 | 0 | 0 | 0 | 12 | 0 | 2 | 7 | 85 | 0 | 0 | 365 | 47 | 0 | 34 | 1 | 82 | 0 | 34 | 0 | 0 | 33 | 370 | 0 | 20 | 0 | 107 | 0 | 0 | 11 | 17 | 0 | 320 | 0 | 0 | 0 | 819 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 289 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 570 | 0 | 0 | 0 | 2 | 11 | 0 | 0 | 0 | 371 | 12 | 152 | 620 | 72 | 0 | 0 |  |  |  | 131.8316 | 21.4989 | 28.251 | 49.3804 | 0.6036 | 2.952 | 2.6857
237.2032
| Minimum Generation |  | 7896 | 7:00
| Highest Generation |  | 10782 | 14:00
| Day Peak Generation |  | 9974 | 12:00
| Evening Peak Generation |  | 10776 | 21:00
| HVDC Max Flow |  | 914 | 19:30
| HVDC EvPeak Flow |  | 893 | 21:00
| Load factor L.F |  | 91.67% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-03-27
Till now the maximum generation is : - |  |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  |  | 2023-03-26 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9974 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 7755
Evening Peak Generation : |  |  | 10776 | MW Hour : | 21:00 | Available Max Generation : |  | 13796
E.P. Demand (at gen end) : |  |  | 10776 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11900
Maximum Generation : |  |  | 10782 | MW Hour : | 14:00 | Reserve(Generation end) |  | 1896
Total Gen. (MKWH) : |  |  | 237.2032 | System Load Factor : | 91.67% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 280 | MW at | 20:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-03-27
Actual : |  | 76.76 | Ft.(MSL) , | Rule curve : | 89 | Ft.( MSL )
Gas Consumed : |  | Total = | 986.76 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 144002392.422
: |  |  | Coal : | 184471982 | Oil : | 363712873.48 | Total : | 692187247.902
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3948.8334 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1090.4778 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1432.9418 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1263.6312 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1079.1812 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 886.6511 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 401.0597 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 323.2277 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 700.1211 |  |  | 0 | 0%
Total |  | 0 |  | 11126.125 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
[5 empty] | 1) Barapukuria ST: Unit- 1,2 | 10) Bhula Nuton Biddut
2) Ghorasal-3,7
3) Ashuganj-5
4) Baghabari-100 MW & 71 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj-2 & 3
9) Kushiara 163 MW ST
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:46 | 08:54 | Ishurdi 132/33kV S/S 132 kV Baghabari Line Forced S/D Due to Bera power station work
08:59 | 09:13 | Bashundhara-Tongi 132 kV Ckt-2 Tripped from Tongi 230/132/33kV end showing Distance. Phase: Y&B relays Due to
Thunder.
09:03 |  | Ashuganj South 360MW ST was sync.
09:45 |  | Shikalbaha Intermediate-Baraka Scheduled S/D
09:57 |  | Shikalbaha Intermediate-Anlima is restored
10:30 |  | Shikalbaha Intermediate-Baraka is restored
10:41 | 12:37 | Shikalbaha 230/132kV S/S Intermediate-1 Scheduled S/D
11:39 | 16:26 | BIPTC S/S 20DF11 Forced S/D Due to Rectification work due to Capacitor C-1 Unbalance 60/61 Instant L2 Trip.
12:00 |  | Day peak gen: 9976 MW.
| 13:06 | Purbasadipur 132/33kV S/S T-1 Transformer (403T) LT is restored.
| 13:23 | Purbasadipur 132/33kV S/S T-3 Transformer (423T) LT is restored.
14:15 | 22:35 | Faridpur 132/33kV S/S Transformer-3 HT Tripped showing 33kv o/c relays Due to 33kv Feeder Fault | [5 empty] | 4.0MW load interrup.
14:30 |  | Ashugonj North 360MW ST was shutdown
15:10 |  | Ashugonj North 360MW GT was shutdown
15:21 |  | Khulna 330 MW CCPP GT was sync. for test purpose.
19:07 |  | Gopalganj- Gopalganj(N) 132kV Ckt-2 Tripped from Gopalganj 132/33kV end showing DIST PROTECTION OPERATED. relays Due
to Y phase IVT Blast
19:32 |  | Khulna 330 MW CCPP GT was shutdown after test.
20:01 |  | Ashuganj South 360MW ST tripped
21:00 |  | Evening Peak Generation = 10,776MW
23:21 |  | Kaliakoir 400/230/132kV S/S 400kV Bus 2 Forced S/D Due to Single portion of R phase of bus 2 has been separated and
sparked as well. Weather is stormy.
06:00 |  | Minimum Generation : 7755 MW
07:40 |  | 230 kV Zodiac bay S/D for SCADA integration work.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-03-26 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4362750
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 77 | 1304727 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 381 | 8816640 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 272 | 7054000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 360 | 8345250 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 0 | 113280 | Reserve.
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 238 | 6429295 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 50 | 220659 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 42 | 212238 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 443988
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 40 | 146563 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 160 | 3194910 | ST U/M.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 115776 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 872280
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 16 | 312480 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 176879 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 358065
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 43 | 1027020 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 712200
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 752200
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 51 | 404640 | 0:00
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 30 | 918327 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 135 | 1049040 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1159680
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 71 | 286080 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 110 | 527040 | Low demand
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 209872
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Reserve.
| Dhaka area Total |  |  |  | 5847 | 2601 | 49525879
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 2300000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 31703 | Reserve.
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 129735
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 20 | 479520 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 25 | 603600 | Low Water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 228 | 5121909
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 34 | 649018 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve.
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 377792 | Low demand
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 22 | 531360 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1673280
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 116064 | Gas shortage
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 959520
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 5 | 143040 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 30238
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 30 | 978545 | Low demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 450996 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 54 | 1153345
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 30 | 704448
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 89 | 1570691 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2382 | 730 | 18004804
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 217 | 4636000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 4124800 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 110 | 3625000 | ST Tripped at 20:01
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 260 | 5834800 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 47 | 606024 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 48 | 491520 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 888973
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 143 | 1185963 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 120 | 1846560 | Low demand
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 425124
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 210240 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 132 | 2952000
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 739800
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 16 | 263558 | Low demand
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 18 | 436660
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Fuel shortage
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 36480 | Reserve.
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 76 | 502320 | Low demand
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 362520 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 52 | 1457280 | Low demand
| Cumilla Area Total |  |  |  | 3285 | 1358 | 30625622
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 151 | 2454720 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 360864 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12550
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 164 | 1672800 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 89 | 1654800 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 242390
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 369840 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 422 | 6767964
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 38 | 952000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 970440 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2201727 | ST U/M.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 988800
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 49 | 923616
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 176352 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1394496
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1743360
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Under maint.
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 270432 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 6614500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 368 | 8593000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 194220 | Engine problem
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 8839400
| Sylhet Area Total |  |  |  | 2427 | 1505 | 33862343
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 893 | 21498909
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 0 | Reserve.
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 195 | 5284800 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Reserve.
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve.
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 52128 | Transformer O/L
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 658800
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 183665 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 356 | 8581818 | On test.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3001 | 1459 | 36260120
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 10 | 371000 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 170 | 4041518 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 680 | 18045200 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 0 | 0 | Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal 307 MW |  | BCPCL | 307*1 | 307 | 154 | 4058200 | On test.
| Barisal Area Total |  |  |  | 2265 | 1014 | 26515918
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 174 | 3922991 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 370 | 7953818 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 227892
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 409200
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 210906
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 5578 | Reserve.
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve.
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 889728 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 158208 | Low demand
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 36720
| Adani Power Jharkhanda Ltd |  | Import | 0 | 0 | 599 | 14558182 | On test.
| Rajshahi Area Total |  |  |  | 2129 | 1340 | 28373223
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4137000 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 107 | 1148592 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 32231
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 70 | 616320 | Low demand
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 226700
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 1106450
| Rangpur Area Total |  |  |  | 750 | 347 | 7267293
| Total |  |  |  | 22700 | 10776 | 237203166
| Eastern Grid Total |  |  |  | 14555 | 6616 | 138786612
| Western Grid Total |  |  |  | 8145 | 4160 | 98416554
| National Grid Total |  |  |  | 22700 | 10776 | 237203166
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-03-26
| (a) ENTIRE EASTERN GRID : |  | 6929.6 | MW | (b) ENTIRE WESTERN GRID : |  | 3317.4 | MW
| i) Dhaka area |  | 3675.2 | MW | i) Khulna area |  | 994.2 | MW
| ii) Chittagong area |  | 1083.4 | MW | ii) Rajshahi area |  | 1329.2 | MW
| iii) Comilla area |  | 782 | MW | iii) Barisal area |  | 260 | MW
| iv) Mymensingh area |  | 997 | MW | iv) Rangpur area |  | 734 | MW
| v) Sylhet area |  | 392 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10247 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 21 | 18:30 | Kamrangirchar | 49 | 13:00 | Natore | 133 | 21:00 | Shitalakhya | 98 | 14:00
2 | AKSML | 90 | 09:00 | Chowmuhani | 154 | 18:00 | Kaptai | 12 | 15:00 | Nawabganj | 39.2 | 18:30 | Sholosohor | 26 | 19:00
3 | Aftabnagar | 29 | 19:00 | Chuadanga | 93 | 20:00 | Kazla | 70 | 00:00 | Netrakona | 106 | 21:00 | Shyampur | 168 | 00:00
4 | Agargaon | 87 | 15:00 | Coxsbazar | 124 | 20:00 | Keranigonj | 60 | 19:30 | New | 51.4 | 00:00 | Siddhirganj | 82 | 22:00
5 | Agrabad | 56 | 19:00 | Cumilla(N) | 141 | 18:30 | Khagrachori | 28 | 18:30 | Niamatpur | 77 | 21:00 | Sirajganj | 105 | 19:30
6 | Amnura | 74 | 21:00 | Cumilla(S) | 152 | 18:00 | Khulna | 89 | 21:00 | Noapara | 36 | 14:00 | Sonargaon | 75 | 01:00
7 | Ashuganj | 52 | 14:00 | Daudkandi | 104 | 19:30 | Khulshi | 151 | 00:00 | PHP | 9 | 09:00 | Sreemongol | 48 | 19:00
8 | BIPTC | N/A | N/A | Dhaka | 22 | 12:00 | Kishoreganj | 124 | 18:30 | Pabna | 105 | 03:00 | Srinagar | 33.8 | 13:00
9 | BSRM | 105 | 08:00 | Dhamrai | 84 | 14:00 | Kodda | 199 | 22:00 | Palashbari | 109 | 19:00 | Sunamganj | 36 | 19:30
10 | Bagerhat | 70 | 21:00 | Dhanmondi | 94 | 14:00 | Kulaura | 36 | 19:00 | Panchagarh | 48 | 18:00 | Sylhet | 118 | 18:30
11 | Bakulia | 83 | 19:00 | Dohazari | 86 | 22:00 | Kurigram | 62 | 18:00 | Patuakhali | 71.2 | 00:00 | TK | 27.4 | 20:00
12 | Banani | 28 | 13:00 | Faridpur | 101 | 14:00 | Kushtia | 104 | 03:00 | Payra | 13.2 | 19:30 | Tangail | 213 | 18:30
13 | Bangabhaban | 5 | 11:00 | Fatullah | 54 | 00:00 | Lalbag | 68 | 16:00 | Postogola | 36 | 14:00 | Thakurgaon | 80 | 19:00
14 | Barapukuria | 45 | 20:00 | Fenchuganj | 38 | 18:30 | Lalmonirhat | 43 | 18:00 | Purbachal | 15 | 19:00 | Tongi | 91 | 15:00
15 | Barguna | 16 | 19:00 | Feni | 117 | 18:30 | Madanganj | 44 | 00:00 | Purbasadipur | 109 | 19:30 | Ullon | 39 | 12:00
16 | Barishal | 82 | 18:00 | GPH | 91 | 20:00 | Madaripur | 71 | 15:00 | Rahanpur_I | 0 | 00:00 | Uttara | 69 | 20:00
17 | Barishal-230 | 58 | 15:00 | Ghorashal | 53 | 22:00 | Madartek | 67 | 14:00 | Rahim | 33 | 14:00 | UttaraNew | 15 | 09:00
18 | Baroaulia | 57 | 01:00 | Goalpara | 30 | 18:30 | Madunaghat | 51 | 21:00 | Rajbari | 50 | 20:00 | Zigatola | 51 | 15:00
19 | Baroirhat | 42 | 19:00 | Gollamari | 35 | 19:00 | Magura | 40 | 15:00 | Rajendrapur | 100 | 19:30
20 | Bashundhara | 127 | 21:00 | Gopalganj | 70.2 | 15:00 | Mahasthangarh | 64 | 19:00 | Rajshahi | 132 | 21:00
21 | BashundharaCement | 0 | 00:00 | Gulshan | 70 | 15:00 | Manikganj | 71 | 20:00 | Rajshahi-230 | 34 | 20:00
22 | Beanibazar | 52 | 21:00 | Halishahar | 63 | 20:00 | Maniknagar | 48 | 17:00 | Ramganj | 72 | 14:00
23 | Benapole | 66 | 14:00 | HaripurSBU | 150 | 01:00 | Matarbari | 40 | 21:00 | Rampur | 26 | 19:00
24 | Bhaluka | 98 | 18:00 | Hasnabad | 70 | 00:00 | Matuail | 56 | 00:00 | Rangamati | 16 | 19:00
25 | Bhandaria | 34 | 00:00 | Hathazari | 55 | 19:00 | Millgate | 55 | 14:00 | Rangpur | 129 | 18:00
26 | Bhangura | 33 | 14:00 | Ishurdi | 56 | 21:00 | Mirpur | 104 | 14:00 | Ruppur | 3.4 | 11:00
27 | Bheramara(GK) | 49 | 19:00 | Jaldhaka | 60 | 14:00 | Mirsorai | 3.5 | 19:00 | SSM | 15 | 13:00
28 | Bhulta | 224 | 11:00 | Jamalpur | 153 | 18:00 | Mithapukur | 36 | 18:00 | Saidpur | 91 | 17:00
29 | Bog-Sherpur | 56 | 03:00 | Jashore | 110 | 13:00 | Modern | 0 | 00:00 | Satkhira | 119 | 21:00
30 | Bogura | 147 | 20:00 | Jhenaidah | 96 | 14:00 | Mogbazar | 91 | 15:00 | Satmasjid | 91 | 16:00
31 | Borhanuddin | 43 | 18:30 | Joydebpur | 113 | 21:00 | Mongla | 24 | 18:00 | Savar | 130 | 15:00
32 | Brahmanbaria | 150 | 18:30 | Joypurhat | 57 | 21:00 | Motijheel | 26 | 13:00 | Shahjadpur | 98 | 20:00
33 | Cantonment | 108 | 14:00 | Juldah | 27 | 00:00 | Munshiganj | 86 | 13:00 | Shahjibazar | 93 | 19:00
34 | Chandpur | 48 | 16:00 | KSRM | 50 | 19:00 | Mymensingh | 223 | 18:00 | Shahmirpur | 43.5 | 00:00
35 | Chandraghona | 27 | 19:00 | Kabirpur | 207 | 00:00 | Naogaon | 120 | 21:00 | Shariatpur | 52 | 14:00
36 | Chapai | 61 | 21:00 | Kachua | 51 | 00:00 | Narail | 34 | 15:00 | Sherpur | 126 | 19:00
37 | Charsaidpur | 47 | 01:00 | Kallyanpur | 75 | 13:00 | Narinda | 55 | 14:00 | Shikalbaha | 28 | 00:00
38 | Chauddagram | 42 | 18:00 | Kalurghat | 22 | 00:00 | Narshingdi | 150 | 22:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-03-26 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 409 | 19:00 | 388 | 13:00 | Kaliakoir | 398 | 18:00 | 382 | 16:00
| Bhulta | 394 | 18:30 | 382 | 16:00 | Madunaghat_I | 400 | 03:00 | 386 | 22:00
| Bibiana | 407 | 22:00 | 397 | 16:00 | Payra | 419 | 18:30 | 408 | 13:00
| BIPTC | 403 | 06:00 | 387 | 12:00 | Rahanpur_I | 413 | 12:00 | 403 | 14:00
| Gopalganj | 420 | 06:00 | 390 | 13:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 238 | 18:30 | 223 | 13:00 | Hasnabad | 239 | 18:30 | 225 | 12:00
| AKSML | 233 | 18:30 | 218 | 05:00 | Hathazari | 234 | 18:00 | 220 | 06:00
| Aminbazar | 238 | 19:30 | 227 | 12:00 | Ishurdi | 237 | 06:00 | 225 | 13:00
| Ashuganj | 245 | 18:30 | 233 | 12:00 | Jhenaidah | 235 | 06:00 | 221 | 13:00
| Baghabari | 232 | 04:00 | 225 | 10:00 | Kaliakoir | 237 | 18:00 | 225 | 13:00
| Barapukuria | 222 | 06:00 | 213 | 17:00 | Keranigonj | 239 | 18:30 | 224 | 13:00
| Barishal | 241 | 18:30 | 230 | 13:00 | Khulna(S) | 240 | 06:00 | 229 | 13:00
| Bheramara | 233 | 06:00 | 222 | 13:00 | Madunaghat_I | 232 | 03:00 | 224 | 00:00
| Bhulta | 238 | 18:30 | 228 | 13:00 | Maniknagar | 236 | 18:30 | 226 | 13:00
| Bibiana | 240 | 19:00 | 234 | 13:00 | Meghnaghat | 240 | 18:30 | 231 | 11:00
| BIPTC | 237 | 18:30 | 223 | 13:00 | Mirsorai | 236 | 18:30 | 223 | 08:00
| Bogura | 228 | 18:30 | 218 | 11:00 | Rajshahi | 231 | 05:00 | 222 | 13:00
| Borhanuddin | 241 | 18:30 | 232 | 14:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 235 | 18:30 | 223 | 05:00 | Rampura | 235 | 18:00 | 225 | 13:00
| Cumilla(N) | 236 | 18:30 | 228 | 12:00 | Shikalbaha | 234 | 19:00 | 221 | 05:00
| Fenchuganj | 245 | 22:00 | 240 | 12:00 | Shyampur | 238 | 18:30 | 224 | 13:00
| Ghorashal | N/A | N/A | N/A | N/A | Siddhirganj | 238 | 18:30 | 229 | 13:00
| GPH | 232 | 18:30 | 220 | 05:00 | Sirajgonj | 232 | 04:00 | 227 | 09:00
| Haripur | 235 | 20:00 | 227 | 13:00 | Tongi | 234 | 18:00 | 224 | 15:00
| 132 kV | KV |  | KV
| Aftabnagar | 135 | 03:00 | 130 | 14:00 | Lalbag | 139 | 18:30 | 128 | 13:00
| Agargaon | 137 | 18:30 | 128 | 13:00 | Lalmonirhat | 128 | 18:30 | 120 | 17:00
| Agrabad | 132 | 14:00 | 127 | 05:00 | Madanganj | 139 | 18:30 | 129 | 13:00
| AKS | 131 | 14:00 | 126 | 05:00 | Madaripur | 138 | 18:30 | 128 | 13:00
| Aminbazar | 137 | 18:00 | 128 | 12:00 | Madartek | 135 | 06:00 | 128 | 13:00
| Amnura | 134 | 05:00 | 127 | 13:00 | Madunaghat | 134 | 18:30 | 127 | 05:00
| Ashuganj | 137 | 06:00 | 134 | 13:00 | Magura | 141 | 22:00 | 130 | 13:00
| Bagerhat | 137 | 23:00 | 126 | 13:00 | Mahasthangarh | 132 | 02:00 | 124 | 10:00
| Bakulia | 135 | 18:30 | 126 | 05:00 | Manikganj | 137 | 18:00 | 130 | 16:00
| Banani | 135 | 08:00 | 128 | 13:00 | Maniknagar | 137 | 18:30 | 130 | 13:00
| Bangabhaban | 136 | 18:00 | 130 | 13:00 | Matarbari | 119 | 08:00 | 109 | 22:00
| Barapukuria | 135 | 06:00 | 127 | 17:00 | Matuail | 138 | 18:30 | 129.6 | 13:00
| Barguna | 130 | 06:00 | 126 | 13:00 | Millgate | 137 | 05:00 | 130 | 13:00
| Barishal | 137 | 18:30 | 128 | 13:00 | Mirpur | 137 | 18:30 | 127 | 13:00
| Barishal-230 | 136 | 06:00 | 128 | 13:00 | Mithapukur | 130 | 01:00 | 121 | 09:00
| Baroaulia | 134 | 18:00 | 129 | 10:00 | Modern | 133 | 18:00 | 128 | 04:00
| Baroirhat | 136 | 18:30 | 126 | 05:00 | Mogbazar | 135 | 00:00 | 130 | 13:00
| Bashundhara | 138 | 18:30 | 130 | 12:00 | Mongla | 136 | 00:00 | 126 | 13:00
| BashundharaCement | 139 | 18:30 | 129 | 13:00 | Motijheel | 136 | 18:00 | 130 | 13:00
| Beanibazar | 137 | 23:00 | 127 | 15:00 | Munshiganj | 138 | 18:30 | 129 | 13:00
| Benapole | 136 | 22:00 | 123 | 13:00 | Mymensingh | 136 | 04:00 | 111 | 18:00
| Bhaluka | 131 | 06:00 | 111 | 17:00 | Naogaon | 129 | 00:00 | 120 | 10:00
| Bhandaria | 138 | 18:30 | 126 | 14:00 | Narail | 139 | 06:00 | 128 | 13:00
| Bhangura | 138 | 02:00 | 132 | 09:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 136 | 06:00 | 130 | 13:00 | Narshingdi | 134 | 18:30 | 124 | 13:00
| Bheramara(GK) | 138 | 05:00 | 133 | 14:00 | Natore | 133 | 05:00 | 126 | 13:00
| Bhulta | 131 | 18:00 | 121 | 12:00 | Nawabganj | 137 | 18:30 | 127 | 13:00
| Bog-Sherpur | 134 | 02:00 | 126 | 10:00 | Netrakona | 125 | 04:00 | 113 | 17:00
| Bogura | 133 | 00:00 | 127 | 10:00 | New | 139 | 18:00 | 131 | 13:00
| Bogura-230 | 133 | 01:00 | 126 | 11:00 | Niamatpur | 128 | 00:00 | 116 | 10:00
| Brahmanbaria | 133 | 05:00 | 129 | 12:00 | Noapara | 138 | 23:00 | 127 | 13:00
| Cantonment | 136 | 18:30 | 127 | 13:00 | Pabna | 136 | 06:00 | 130 | 11:00
| Chandpur | 142 | 18:30 | 124 | 08:00 | Palashbari | 128 | 06:00 | 120 | 10:00
| Chandraghona | 135 | 18:00 | 128 | 05:00 | Panchagarh | 132 | 02:00 | 116 | 17:00
| Chapai | 134 | 01:00 | 129 | 14:00 | Patuakhali | 137 | 14:00 | 127 | 01:00
| Charsaidpur | 139 | 18:30 | 129 | 13:00 | Payra | 131 | 06:00 | 129 | 00:00
| Chauddagram | 138 | 20:00 | 127 | 13:00 | PHP | 136 | 20:00 | 125 | 13:00
| Chhatak | 136 | 23:00 | 127 | 19:00 | Postogola | 138 | 18:30 | 129 | 13:00
| Chowmuhani | 139 | 18:30 | 124 | 04:00 | Purbachal | 136 | 03:00 | 124 | 20:00
| Chuadanga | 139 | 22:00 | 123 | 13:00 | Purbasadipur | 129 | 20:00 | 118 | 09:00
| Coxsbazar | 121 | 14:00 | 108 | 21:00 | Rahim | 137 | 18:30 | 131 | 12:00
| Cumilla(N) | 139 | 18:30 | 130 | 14:00 | Rajbari | 135 | 18:30 | 126 | 13:00
| Cumilla(S) | 139 | 18:30 | 126 | 15:00 | Rajendrapur | 139 | 18:30 | 129 | 16:00
| Daudkandi | 136 | 18:00 | 127 | 12:00 | Rajshahi | 132 | 05:00 | 127 | 13:00
| Dhaka | 136 | 18:30 | 129 | 13:00 | Rajshahi-230 | 135 | 06:00 | 127 | 13:00
| Dhamrai | 136 | 18:30 | 128 | 13:00 | Ramganj | 141 | 19:00 | 121 | 08:00
| Dhanmondi | 138 | 18:30 | 130.5 | 13:00 | Rampur | 132 | 15:00 | 126 | 05:00
| Dohazari | 132 | 02:00 | 121 | 23:00 | Rampura | 135 | 04:00 | 129 | 13:00
| Faridpur | 135 | 06:00 | 126 | 13:00 | Rangamati | 133 | 14:00 | 128 | 10:00
| Fatullah | 139 | 18:30 | 129 | 13:00 | Rangpur | 129 | 05:00 | 121 | 10:00
| Fenchuganj | 138 | 22:00 | 134 | 12:00 | Ruppur | 137 | 06:00 | 132 | 12:00
| Feni | 138 | 20:00 | 127 | 04:00 | Saidpur | 130 | 18:30 | 121 | 09:00
| Ghorashal | 139 | 18:00 | 134 | 13:00 | Satkhira | 137 | 06:00 | 127 | 13:00
| Goalpara | 139 | 06:00 | 128 | 13:00 | Satmasjid | 137 | 18:30 | 128 | 13:00
| Gollamari | 136 | 23:00 | 126 | 13:00 | Savar | 137 | 18:00 | 126 | 13:00
| Gopalganj | 136 | 23:00 | 126 | 13:00 | Shahjadpur | 144 | 04:00 | 134 | 12:00
| Gopalganj-400 | 137 | 18:30 | 130 | 12:00 | Shahjibazar | 135 | 04:00 | 131 | 13:00
| Gulshan | 135 | 04:00 | 129 | 13:00 | Shahmirpur | 136 | 18:00 | 128 | 10:00
| Halishahar | 135 | 18:30 | 127 | 05:00 | Shariatpur | 137 | 18:00 | 126 | 13:00
| Haripur | 137 | 18:30 | 131 | 12:00 | Sherpur | 135 | 15:00 | 119 | 08:00
| HaripurSBU | 137 | 18:30 | 131 | 12:00 | Shikalbaha | 134 | 14:00 | 129 | 04:00
| Hasnabad | 137 | 18:30 | 130 | 10:00 | Shikalbaha-230 | 135 | 19:00 | 126 | 10:00
| Hathazari | 136 | 18:00 | 130 | 06:00 | Shitalakhya | 139 | 18:30 | 128 | 13:00
| Ishurdi | 138 | 06:00 | 130 | 13:00 | Sholosohor | 134 | 18:30 | 127 | 05:00
| Jaldhaka | 128 | 01:00 | 117 | 17:00 | Shyampur | 137 | 18:30 | 130 | 00:00
| Jamalpur | 138 | 15:00 | 120 | 08:00 | Shyampur-230 | 138 | 18:30 | 128 | 13:00
| Jashore | 137 | 22:00 | 124 | 13:00 | Siddhirganj | 138 | 18:30 | 131 | 12:00
| Jhenaidah | 142 | 22:00 | 131 | 13:00 | Sirajganj | 135 | 05:00 | 127 | 10:00
| Jhenaidah-230 | 141 | 06:00 | 131 | 13:00 | Sonargaon | 135 | 21:00 | 130 | 00:00
| Joydebpur | 145 | 18:30 | 133 | 11:00 | Sreemongol | 135 | 23:00 | 131 | 17:00
| Joypurhat | 130 | 02:00 | 117 | 13:00 | Srinagar | 138 | 18:30 | 128 | 13:00
| Juldah | 133 | 14:00 | 127 | 00:00 | SSM | 139 | 14:00 | 132 | 07:00
| Kabirpur | 139 | 18:30 | 129 | 13:00 | Sunamganj | 136 | 23:00 | 125 | 18:30
| Kachua | 140 | 18:30 | 126 | 07:00 | Sylhet | 136 | 23:00 | 129 | 15:00
| Kaliakoir | 141 | 18:00 | 133 | 01:00 | Tangail | 137 | 00:00 | 127 | 03:00
| Kallyanpur | 136 | 18:00 | 129 | 12:00 | Thakurgaon | 130 | 02:00 | 116 | 09:00
| Kalurghat | 133 | 14:00 | 127 | 05:00 | TK | 136 | 18:00 | 126 | 05:00
| Kamrangirchar | 135 | 06:00 | 128 | 13:00 | Tongi | 140 | 18:00 | 133 | 15:00
| Kaptai | 132 | 00:00 | 130 | 01:00 | Ullon | 143 | 03:00 | 129 | 13:00
| Kazla | 137 | 18:30 | 130 | 13:00 | Uttara | 137 | 19:00 | 127 | 13:00
| Keranigonj | 138 | 18:30 | 127 | 13:00 | UttaraNew | 137 | 06:00 | 130 | 13:00
| Khagrachori | 133 | 18:30 | 128 | 05:00 | Zigatola | 136 | 18:30 | 128 | 13:00
| Khulna | 139 | 23:00 | 129 | 13:00
| Khulna(S) | 140 | 23:00 | 130 | 13:00
| Khulshi | 132 | 15:00 | 125 | 04:00
| Kishoreganj | 135 | 06:00 | 120 | 18:00
| Kodda | 141 | 19:30 | 130 | 15:00
| KSRM | 136 | 18:00 | 127 | 04:00
| Kulaura | 139 | 23:00 | 133 | 16:00
| Kurigram | 128 | 18:30 | 120 | 17:00
| Kushtia | 139 | 22:00 | 130 | 13:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2023-03-26
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1026 | 4922 | 3759 | 8681 |  |  |  | QF-LDC-11
0:30 | 1033 | 5256.5 | 3940.5 | 9197 | Date: | 2023-03-26
1:00 | 1040 | 5591 | 4122 | 9713
1:30 | 1000 | 5531 | 4060.5 | 9591.5
2:00 | 960 | 5471 | 3999 | 9470
2:30 | 930 | 5603.5 | 4030.5 | 9634 | [5 empty] | Gen. at Eve. Peak | 10776 | 10776 MW (21:00 )
3:00 | 900 | 5736 | 4062 | 9798 | [6 empty] | 21:00
3:30 | 930 | 5769 | 4076.5 | 9845.5 | [5 empty] | Gen. at Day Peak | 9974 | 9974 MW (12:00 )
4:00 | 960 | 5802 | 4091 | 9893 | [6 empty] | 12:00
4:30 | 1010 | 5479 | 3895.5 | 9374.5 | [5 empty] | Highest Generation | 10782
5:00 | 1060 | 5156 | 3700 | 8856 | [6 empty] | 14:00
5:30 | 1050 | 4866.5 | 3568 | 8434.5
6:00 | 1040 | 4577 | 3436 | 8013
6:30 | 980 | 4502.5 | 3452 | 7954.5
7:00 | 920 | 4428 | 3468 | 7896
7:30 | 910 | 4478.5 | 3513.5 | 7992
8:00 | 900 | 4529 | 3559 | 8088
8:30 | 797 | 4736 | 3617 | 8353
9:00 | 694 | 4943 | 3675 | 8618
9:30 | 749 | 5178.5 | 3713 | 8891.5
10:00 | 804 | 5414 | 3751 | 9165
10:30 | 818 | 5515.5 | 3814 | 9329.5
11:00 | 832 | 5617 | 3877 | 9494
11:30 | 816 | 5736.5 | 3997.5 | 9734
12:00 | 800 | 5856 | 4118 | 9974
12:30 | 900 | 5961.5 | 4267.5 | 10229
13:00 | 1000 | 6067 | 4417 | 10484
13:30 | 904 | 6195.5 | 4437.5 | 10633
14:00 | 808 | 6324 | 4458 | 10782
14:30 | 839 | 6369.5 | 4395 | 10764.5
15:00 | 870 | 6415 | 4332 | 10747
15:30 | 878 | 6384 | 4314 | 10698
16:00 | 886 | 6353 | 4296 | 10649
16:30 | 885 | 6280.5 | 4209.5 | 10490
17:00 | 884 | 6208 | 4123 | 10331
17:30 | 712 | 6269.5 | 4072 | 10341.5
18:00 | 540 | 6331 | 4021 | 10352
18:30 | 465 | 6367 | 3992 | 10359
19:00 | 390 | 6403 | 3963 | 10366
19:30 | 350 | 6515 | 4079 | 10594
20:00 | 280 | 6548 | 4048 | 10596 |  |  |  | Executive Engineer
20:30 | 440 | 6582 | 4104 | 10686 |  |  |  | Network Operation Division
21:00 | 600 | 6616 | 4160 | 10776
21:30 | 803 | 6432.5 | 4072.5 | 10505
22:00 | 1006 | 6249 | 3985 | 10234 |  |  |  |  | Page 6 of 7
22:30 | 1043 | 5710.5 | 3913 | 9623.5
23:00 | 1080 | 5172 | 3841 | 9013
23:30 | 1053 | 5047 | 3800 | 8847
24:00 | 1026 | 4922 | 3759 | 8681
10776 MW (21:00 )
9974 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-03-26 |  | Energy |  | 237203166
[13 empty] | 2023-03-26 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3079 | 892 | 1876 | 0 | 715 | 1936 | 25 | 0 | 34 | 124 | 0 | 0
0:30 | 3337 | 901 | 1901.5 | 0 | 821 | 2053.5 | 25 | 0 | 33 | 125 | 0 | 0 | Date: | 2023-03-26
1:00 | 3595 | 910 | 1927 | 0 | 927 | 2171 | 25 | 0 | 32 | 126 | 0 | 0
1:30 | 3589 | 910 | 1877.5 | 0 | 888 | 2146 | 25 | 0 | 32 | 124 | 0 | 0 | [7 empty] | Total Energy | 237.2032 | Total Energy Gen 237.203 MKWHr Energy Not Served 0.086 MKWHr Energy Requirement 237.290 MKWHr
2:00 | 3583 | 910 | 1828 | 0 | 849 | 2121 | 25 | 0 | 32 | 122 | 0 | 0 | [7 empty] | Energy not Served | 0.0864
2:30 | 3597.5 | 909.5 | 1936.5 | 0 | 868.5 | 2128 | 25 | 0 | 48 | 121 | 0 | 0 | [7 empty] | Energy Requirement | 237.2896
3:00 | 3612 | 909 | 2045 | 0 | 888 | 2135 | 25 | 0 | 64 | 120 | 0 | 0
3:30 | 3625 | 909 | 2079 | 0 | 880 | 2143.5 | 25 | 0 | 64 | 120 | 0 | 0 | [5 empty] | Shortage
4:00 | 3638 | 909 | 2113 | 0 | 872 | 2152 | 25 | 0 | 64 | 120 | 0 | 0
4:30 | 3597 | 909.5 | 2060 | 0 | 634.5 | 1997.5 | 25 | 0 | 32 | 119 | 0 | 0
5:00 | 3556 | 910 | 2007 | 0 | 397 | 1843 | 25 | 0 | 0 | 118 | 0 | 0
5:30 | 3430.5 | 874.5 | 1826 | 0 | 350.5 | 1819 | 25 | 0 | 0 | 109 | 0 | 0
6:00 | 3305 | 839 | 1645 | 0 | 304 | 1795 | 25 | 0 | 0 | 100 | 0 | 0
6:30 | 3299 | 839.5 | 1645.5 | 0 | 230 | 1791.5 | 25 | 0 | 0 | 102 | 22 | 0 |  |  |  | Coal
7:00 | 3293 | 840 | 1646 | 0 | 156 | 1788 | 25 | 0 | 0 | 104 | 44 | 0
7:30 | 3333 | 827.5 | 1653 | 0 | 156 | 1810.5 | 25 | 0 | 0 | 100 | 87 | 0 |  |  | Oil |  |  |  | ,
8:00 | 3373 | 815 | 1660 | 0 | 156 | 1833 | 25 | 0 | 0 | 96 | 130 | 0
8:30 | 3431.5 | 827.5 | 1733 | 0 | 207.5 | 1846.5 | 25 | 0 | 0 | 103 | 179 | 0
9:00 | 3490 | 840 | 1806 | 0 | 259 | 1860 | 25 | 0 | 0 | 110 | 228 | 0
9:30 | 3503.5 | 851 | 1898 | 0 | 358 | 1863.5 | 25 | 0 | 0 | 113 | 279.5 | 0
10:00 | 3517 | 862 | 1990 | 0 | 457 | 1867 | 25 | 0 | 0 | 116 | 331 | 0
10:30 | 3522.5 | 880.5 | 2026 | 0 | 536.5 | 1874 | 25 | 0 | 0 | 116 | 349 | 0
11:00 | 3528 | 899 | 2062 | 0 | 616 | 1881 | 25 | 0 | 0 | 116 | 367 | 0
11:30 | 3591.5 | 899.5 | 2090.5 | 0 | 721 | 1919.5 | 25 | 0 | 0 | 122 | 365 | 0
12:00 | 3655 | 900 | 2119 | 0 | 826 | 1958 | 25 | 0 | 0 | 128 | 363 | 0
12:30 | 3749 | 900 | 2137 | 0 | 896 | 2009.5 | 25 | 0 | 0 | 133 | 379.5 | 5
13:00 | 3843 | 900 | 2155 | 0 | 966 | 2061 | 25 | 0 | 0 | 138 | 396 | 10
13:30 | 3843 | 900 | 2155 | 0 | 966 | 2061 | 25 | 0 | 0 | 138 | 396 | 10
14:00 | 3843 | 900 | 2155 | 0 | 966 | 2061 | 25 | 0 | 0 | 138 | 396 | 10
14:30 | 3730.5 | 900 | 2084 | 0 | 1328.5 | 2066 | 25 | 0 | 17 | 139 | 325.5 | 13.5
15:00 | 3618 | 900 | 2013 | 0 | 1691 | 2071 | 25 | 0 | 34 | 140 | 255 | 17
15:30 | 3602 | 900 | 2043 | 0 | 1650 | 2061.5 | 25 | 30 | 37.5 | 135 | 214 | 8.5
16:00 | 3586 | 900 | 2073 | 0 | 1609 | 2052 | 25 | 60 | 41 | 130 | 173 | 0
16:30 | 3615 | 900 | 2068.5 | 0 | 1504.5 | 2024.5 | 25 | 55 | 48.5 | 132 | 117 | 0
17:00 | 3644 | 900 | 2064 | 0 | 1400 | 1997 | 25 | 50 | 56 | 134 | 61 | 0
17:30 | 3550.5 | 896.5 | 2036 | 0 | 1563.5 | 1965.5 | 25 | 50 | 79 | 143 | 32.5 | 3
18:00 | 3457 | 893 | 2008 | 0 | 1727 | 1934 | 25 | 50 | 102 | 152 | 4 | 6
18:30 | 3358.5 | 899 | 1913 | 0 | 1997.5 | 1879.5 | 25 | 50 | 101.5 | 133 | 2 | 26.5
19:00 | 3260 | 905 | 1818 | 0 | 2268 | 1825 | 25 | 50 | 101 | 114 | 0 | 47
19:30 | 3330 | 914 | 1937 | 0 | 2243 | 1903 | 25 | 50 | 86 | 106 | 0 | 23.5
20:00 | 3365 | 914 | 1942 | 0 | 2224 | 1920 | 25 | 0 | 86 | 120 | 0 | 0
20:30 | 3387 | 903.5 | 2006 | 0 | 2213.5 | 1939.5 | 25 | 0 | 85.5 | 126 | 0 | 0
21:00 | 3409 | 893 | 2070 | 0 | 2203 | 1959 | 25 | 0 | 85 | 132 | 0 | 0
21:30 | 3395.5 | 892.5 | 2061 | 0 | 1951 | 1963 | 25 | 0 | 85 | 132 | 0 | 0
22:00 | 3382 | 892 | 2052 | 0 | 1699 | 1967 | 25 | 0 | 85 | 132 | 0 | 0
22:30 | 3319 | 891.5 | 1968 | 0 | 1247.5 | 1964 | 25 | 0 | 77.5 | 131 | 0 | 0
23:00 | 3256 | 891 | 1884 | 0 | 796 | 1961 | 25 | 0 | 70 | 130 | 0 | 0
23:30 | 3167.5 | 891.5 | 1880 | 0 | 755.5 | 1948.5 | 25 | 0 | 52 | 127 | 0 | 0 | Max Temp. in Dhaka |  | 33.6° C
24:00 | 3079 | 892 | 1876 | 0 | 715 | 1936 | 25 | 0 | 34 | 124 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 237.203 MKWHr Energy Not Served 0.086 MKWHr Energy Requirement 237.290 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-03-26
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 603600
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 130 | 130 | 130 | 130 | 125 | 125 | 125 | 125 | 130 | [9 empty] | 2300000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 1 |  | 23 | 8 |  |  |  |  | 0 | 31703
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 3 | 9 | 14 | 18 | 20 | 20 | 19 |  | 14 | 9 | 3 | 0 | [8 empty] | 129735
6 | Sikalbaha 225MW CCPP (Gas) | 224 | 227 | 225 | 224 | 229 | 227 | 229 | 227 | 227 | 224 | 222 | 225 | 220 | 223 | 222 | 225 | 224 | 228 |  | 184 | 182 | 182 | 228 | 228 | 207 | 207 | 5121909
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [13 empty] | 30 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 377792
12 | Hathazari 100 MW peaking PP | [26 empty] | 0
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 34 | 34 | 34 | 34 | 17 | 17 | 17 | 17 | 0 | 0 | 1 | 17 | 21 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 28 | 649018
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 140 | 140 | 140 | 140 | 90 | 90 | 90 | 90 | 90 | 130 | 130 | 130 | 150 | 145 | 145 | 146 | 145 | 145 |  | 130 | 133 | 130 | 160 | 155 | 140 | 140 | 3194910
18 | Kodda 300 MW PP Unit-2 (Summit) | [12 empty] | 0 | 30 | 30 | 30 | 30 | 35 |  | 80 | 45 | 30 | 30 |  |  | 0 | 918327
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4362750
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 28 | 30 | 30 | 30 | 30 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 30 | 30 | 30 |  | 37 | 45 | 45 | 47 | 48 | 48 | 48 | 606024
33 | Ashuganj 225 MW CCPP | 182 | 159 | 151 | 144 | 137 | 167 | 178 | 187 | 199 | 212 | 216 | 215 | 207 | 178 | 192 | 194 | 200 | 202 |  | 210 | 204 | 208 | 217 | 220 | 219 | 186 | 4636000
34 | Ashuganj 450 MW CCPP(South) | 14 | 66 | 95 | 95 | 114 | 66 | 80 | 55 | 70 | 95 | 110 | 135 | 180 | 235 | 260 | 320 | 350 | 355 |  | 280 | 280 | 280 | 110 | 120 | 120 | 18 | 3625000
| Ashuganj 450 MW CCPP(North) | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 225 | 70 | [10 empty] | 0 | 4124800
| Ashuganj 420 MW CCPP(East) | 250 | 250 | 240 | 240 | 230 | 230 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 260 | 240 | 240 | 240 | 5834800
35 | Ashuganj 55 MW PP (Precision) | 25 | 15 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 20 | 30 | 30 |  | 30 | 30 | 40 | 48 | 52 | 53 | 52 | 491520
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 372 | 343 | 335 | 371 | 368 | 318 | 302 | 302 | 350 | 360 | 353 | 378 | 405 | 406 | 402 | 374 | 373 | 371 |  | 331 | 351 | 351 | 381 | 406 | 377 | 364 | 8816640
40 | Meghnaghat 450 MW CCPP(MPL) | 400 | 340 | 420 | 420 | 400 | 350 | 330 | 330 | 370 | 400 | 400 | 400 | 380 | 360 | 360 | 360 | 350 | 350 |  | 310 | 310 | 310 | 360 | 370 | 330 | 330 | 8345250
41 | Haripur 360MW CCPP(HPL) | 283 | 282 | 283 | 348 | 307 | 275 | 259 | 283 | 352 | 342 | 332 | 312 | 303 | 282 | 282 | 292 | 282 | 281 |  | 257 | 257 | 257 | 272 | 287 | 322 | 303 | 7054000
42 | RPCL 210MW CCPP | 82 | 83 | 82 | 83 | 83 | 83 | 85 | 105 | 106 | 105 | 105 | 102 | 102 | 102 | 102 | 99 | 100 | 102 |  | 102 | 115 | 132 | 151 | 152 | 154 | 153 | 2454720
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 3 | 7 | 7 | 20 | 43 | 32 | 49 | 43 | 33 | 19 | 7 | 0 | [8 empty] | 242390
44 | Fenchugonj CCPP Phase-1 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 40 | 38 | 38 | 38 | 38 | 38 | 41 | 952000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 970440
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 65 | 65 | 65 | 64 | 64 | 40 | 40 | 40 | 40 | 63 | 63 | 63 | 60 | 60 | 61 | 61 | 60 | 61 |  | 61 | 60 | 60 | 61 | 62 | 62 | 62 | 1394496
48 | Shahjibazar 86MW PP (Shahjibazar) | 40 | 89 | 89 | 89 | 89 | 20 | 10 | 10 | 30 | 86 | 86 | 89 | 89 | 89 | 89 | 89 | 89 | 86 |  | 86 | 86 | 86 | 86 | 84 | 84 | 84 | 1743360
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 10 | 10 | 10 | 10 | 194220
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 |  | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 176352
55 | Fenchugonj 51 MW PP (Barakatullah) | 22 | 22 | 53 | 53 | 53 | 11 | 11 | 11 | 28 | 53 | 53 | 50 | 53 | 53 | 53 | 50 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 11 | 988800
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 14 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 8 | 8 | 8 | 8 | 8 | 270432
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 260 | 270 | 270 | 270 | 260 | 265 | 270 | 270 | 280 | 280 | 270 | 280 | 270 | 260 | 280 | 280 | 275 |  | 260 | 280 | 280 | 270 | 260 | 260 | 280 | 6614500
| Bibiyana South 400 MW | 370 | 370 | 400 | 400 | 380 | 330 | 330 | 380 | 400 | 370 | 370 | 400 | 394 | 400 | 350 | 350 | 350 | 335 |  | 360 | 360 | 360 | 400 | 360 | 360 | 340 | 8839400
58 | Nababganj 55 MW PP (Southern power ) | 17 | [12 empty] | 17 | 17 | 17 | 17 | 25 |  | 55 | 55 | 55 | 55 | 55 |  | 0 | 358065
59 | Tangail Palli Power Gen 22 MW | 16 | 17 | 18 | 18 | 18 |  |  | 0 | 1 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 8 | 10 | 18 | 18 | 18 | 18 | 369840
60 | Barabkunda 22 MW PP (Regent) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 |  | 5 | 5 | 5 | 116064
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 443988
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 19 | 19 |  | 19 |  |  |  |  | 19 | 19 | 360864
63 | Impoprt (Tripura) | 126 | 122 | 120 | 120 | 118 | 100 | 104 | 96 | 110 | 116 | 116 | 128 | 138 | 142 | 140 | 130 | 134 | 152 |  | 114 | 106 | 120 | 132 | 132 | 130 | 124 | 2952000
64 | Malancha, Ctg. EPZ (United) | 37 | 39 | 39 | 40 | 38 | 36 | 42 | 40 | 38 | 20 | 28 | 31 | 31 | 36 | 37 | 37 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 959520
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 425124
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 11 | 11 |  | 11 |  |  |  | 11 | 11 | 11 | 210240
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 8 | 8 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  |  | 10 | 33 | 33 | 33 | 33 | 33 | 739800
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 18 | 18 | 18 | 18 | 15 | 15 | 15 | 15 | 15 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 436660
69 | Summit Ashulia | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  | 17 | 408000
70 | Summit Madhabdi | 27 | 27 | 27 | 27 | 20 | 27 | 27 | 27 | 27 | 25 | 27 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 28 | 28 | 28 | 619020
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 28 | 28 | 28 | 28 | 16 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 16 | 712200
72 | Rupganj 33 MW PP(Summit) | 28 | 29 | 30 | 30 | 30 | 30 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 31 | 31 | 31 | 32 | 16 |  | 10 | 33 | 33 | 33 | 33 | 33 | 33 | 752200
73 | Ghorashal 108MW PP (Regent) | 45 | 43 | 43 | 43 | 12 | 12 | 12 | 12 | 12 | 55 | 73 | 78 | 78 | 75 | 75 | 78 | 78 | 78 |  | 42 | 78 | 78 | 77 | 75 | 42 | 42 | 1304727
| Feni Lanka Power | [17 empty] | 34 |  | 14 | [5 empty] | 0 | 36480
| Chowmuhani 113 MW | 6 | 5 | 9 | 9 | 9 | 9 |  | 0 | 2 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 23 | 40 |  | 75 | 75 | 76 | 76 | 55 | 15 | 9 | 502320
| Manikgonj 162MW PP(MPGL) | 17 | [10 empty] | 0 | 1 | 17 | 17 | 17 | 17 | 30 |  | 90 | 90 | 90 | 110 | 72 |  | 0 | 527040
77 | Siddhirganj 100 PP(Dutch Bangla) | [14 empty] | 5 | 9 | 9 | 14 |  | 40 | 40 | 40 | 40 |  |  | 0 | 146563
78 | Gazipur 52 MW PP | [12 empty] | 0 | 18 | 42 | 42 | 50 | 51 |  | 51 | 51 | 51 | 51 | 33 | 8 | 0 | 404640
79 | Kodda 150 MW PP | 32 | 32 | 64 | 64 | [11 empty] | 7 | 16 | 32 |  | 32 | 16 | 16 | 16 | 16 |  | 0 | 312480
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 16 | 16 | 16 | 16 | [9 empty] | 19 | 50 | 8 | 8 | 12 |  | 30 | 16 | 16 | 16 | 16 |  |  | 263558
| Gazipur 100 MW PP | 17 | 52 | 70 | 70 | 34 | [5 empty] | 0 | 3 | 17 | 70 | 70 | 90 | 90 | 90 |  | 105 | 105 | 105 | 105 | 105 | 17 | 0 | 1159680
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 2 | 4 | 4 | 3 | 2 | 1 | [9 empty] | 30238
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 450996
| Karnaphuli Power Ltd. | 54 | 54 | 46 | 54 | 17 | 17 | 17 | 17 | 24 | 51 | 52 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1153345
82 | Madanganj 102 PP(Summit) | [14 empty] | 12 | 17 | 17 | 18 |  | 58 | 55 | 53 | 50 | 15 |  | 0 | 220659
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 276 | 271 | 300 | 291 | 288 | 266 | 300 | 287 | 278 | 285 | 278 | 272 | 265 | 255 | 247 | 252 | 245 | 235 |  | 227 | 271 | 266 | 238 | 239 | 234 | 270 | 6429295
87 | Meghnaghat 100 MW(IEL) | [14 empty] | 6 | 8 | 9 | 12 |  | 39 | 42 | 40 |  |  |  | 0 | 113280
| Meghnaghat 104 MW PP (OPCL) | [13 empty] | 1 | 15 | 17 | 17 | 18 |  | 37 | 69 | 68 | 71 |  |  | 0 | 286080
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 33 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 41 | 44 | 44 | 44 | 44 | 55 | 10 | 10 |  | 10 | 10 | 10 | 22 | 22 | 33 | 44 | 531360
92 | Fenchuganj 44MW (Energyprima) | 20 | 20 | 46 | 50 | 50 | 10 | 10 | 10 | 26 | 50 | 50 | 50 | 49 | 46 | 49 | 49 | 49 | 49 |  | 49 | 49 | 49 | 49 | 49 | 10 | 10 | 923616
93 | Ashuganj 51 MW PP (Midland) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 24 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 35 | 51 | 51 | 51 | 51 | 10 | 10 | 888973
94 | Gagnagar 102 MW PP (Digital Power) | [14 empty] | 8 | 8 | 8 | 24 |  | 24 | 24 | 24 | 8 |  |  | 0 | 115776
95 | Patenga 50MW PP (Baraka) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 20 | 20 | 19 |  | 19 | 19 | 20 | 20 | 20 | 19 | 19 | 479520
96 | Chattogram 108 MW PP (ECPV) | 6 | 5 | 5 | 5 | 5 | 6 | 6 | 5 | 6 | 5 | 5 | 5 | 6 | 4 | 5 | 5 | 6 | 6 |  | 5 | 5 | 4 | 5 | 5 | 5 | 5 | 143040
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [14 empty] | 5 | 15 | 15 | 16 |  | 36 | 40 | 36 | 42 | 42 |  | 0 | 212238
100 | Manikganj 55 MW PP (Northern) | 17 | [16 empty] | 17 |  | 17 | 35 | 35 | 35 | 35 |  | 0 | 176879
101 | Kushiara 163 MW CCPP (KP) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 112 | 112 | 112 | 112 | 112 | 80 | 80 | 80 | 112 |  | 80 | 80 | 80 | 112 | 112 | 80 | 80 | 2201727
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [8 empty] | 12550
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 |  |  |  |  | 0 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 |  | 54 | 54 | 54 | 54 | 54 | 17 | 0 | 872280
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0 | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 47 | 47 | 43 | 75 | 24 | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 12 | 65 | 140 | 111 | 115 | 145 |  | 155 | 155 | 164 | 164 | 164 | 35 | 35 | 1672800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 55 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 19 | 34 | 35 | 35 | 35 | 34 | 27 | 17 | 41 |  | 138 | 149 | 149 | 135 | 71 | 42 | 16 | 1049040
115 | Juldah 100 MW PP Unit-3 (Acorn) | 76 | 76 | 76 | 76 | 20 | 20 | 20 | 20 | 20 | 40 | 76 | 76 | 88 | 100 | 100 | 100 | 50 | 50 |  | 65 | 100 | 100 | 100 | 100 | 100 | 100 | 1673280
116 | Chandpur 200MW (Desh energy) | 51 | 51 | 51 | 51 | 17 | 17 |  | 0 | 13 | 19 | 35 | 64 | 71 | 122 | 161 | 180 | 136 | 136 |  | 120 | 120 | 120 | 120 | 120 | 51 | 51 | 1846560
117 | Ashuganj 150MW PP (Midland) | 5 | 5 | 5 | 5 | [8 empty] | 0 | 32 | 103 | 132 | 137 | 134 |  | 130 | 133 | 134 | 143 | 140 | 10 | 0 | 1185963
118 | Bibiyana-III 400 MW CCPP | 365 | 367 | 365 | 365 | 367 | 323 | 318 | 364 | 365 | 316 | 316 | 365 | 375 | 368 | 368 | 368 | 368 | 368 |  | 354 | 368 | 368 | 368 | 367 | 318 | 327 | 8593000
| Jamalpur 115 MW PP (United) | 49 | 49 | 77 | 78 | 55 | 45 | 24 | 24 | 73 | 88 | 98 | 99 | 100 | 98 | 88 | 49 | 49 | 80 |  | 89 | 89 | 89 | 89 | 89 | 65 | 35 | 1654800
| Anwara 300 MW PP (United) | 100 | 100 | 100 | 50 |  |  |  | 0 | 15 | 45 | 45 | 45 | 45 | 45 | 45 | 30 | 30 | 65 |  | 65 | 50 | 50 | 30 |  |  | 15 | 978545
| Juldah unit-2 (Acorn) | 12 | 12 | 12 | 12 | [5 empty] | 0 | 1 | 12 | 15 | 62 | 100 | 60 | 60 | 60 |  | 60 | 30 | 30 | 30 | 12 | 12 | 45 | 704448
| Anlima Energy Ltd. | 89 | 89 | 89 | 82 | 51 | 51 |  |  |  |  | 0 | 11 | 89 | 89 | 89 | 89 | 89 | 89 |  | 89 | 89 | 89 | 89 | 89 | 91 | 89 | 1570691
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 14 | 17 |  |  |  | 0 | 4 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 362520
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 1 | 5 | 18 | 27 | 31 | 32 | 31 | 27 | 21 | 13 | 3 | 0 | [8 empty] | 209872
| Chandpur 115(Doreen) | 52 | 52 | 52 | 52 | 52 | 17 |  | 1 | 33 | 54 | 65 | 115 | 115 | 98 | 92 | 93 | 56 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 34 | 1457280
| Kanchan Purbachal Power Generation Ltd. | [25 empty] | 0 | 0
| Mirsharai 150 MW (Oil) | [25 empty] | 0 | 0
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 5591 | 5471 | 5736 | 5802 | 5156 | 4577 | 4428 | 4529 | 4943 | 5414 | 5617 | 5856 | 6067 | 6324 | 6415 | 6353 | 6208 | 6331 |  | 6403 | 6515 | 6548 | 6616 | 6249 | 5172 | 4922 | 138786612
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [25 empty] | 0 | 0
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL) | [15 empty] | 60 | 50 | 50 |  | 50 | 50 | [5 empty] | 183665
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [25 empty] | 0 | 0
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 12 | 34 | 59 | 80 | 90 | 93 | 91 | 80 | 65 | 40 | 8 | 1 | [8 empty] | 658800
131 | Rampal 1320 MW (BIFPCL) | 372 | 374 | 375 | 374 | 375 | 369 | 368 | 367 | 374 | 367 | 370 | 366 | 367 | 366 | 369 | 319 | 303 | 302 |  | 309 | 309 | 309 | 356 | 376 | 373 | 373 | 8581818
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [25 empty] | 0 | 0
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 201 | 201 | 202 | 200 | 150 | 151 | 150 | 151 | 150 | 150 | 150 | 148 | 149 | 200 | 199 | 200 | 171 | 173 |  | 147 | 152 | 152 | 154 | 151 | 153 | 153 | 4058200
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 171 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 171 | 170 | 170 | 170 | 170 | 170 | 155 | 170 | 147 |  | 147 | 147 | 148 | 170 | 150 | 170 | 170 | 4041518
140 | Bhola 33 MW PP (Venture) | 19 | 18 | 17 | 20 | 17 | 14 | 13 | 13 | 13 | 15 | 16 | 17 | 19 | 20 | 19 | 20 | 18 | 20 |  | 5 | 7 | 9 | 10 | 12 | 15 | 14 | 371000
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [25 empty] | 0 | 0
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [22 empty] | 15 | 15 | 15 | 15 | 52128
146 | Bheramara HVDC | 910 | 910 | 909 | 909 | 910 | 839 | 840 | 815 | 840 | 862 | 899 | 900 | 900 | 900 | 900 | 900 | 900 | 893 |  | 905 | 914 | 914 | 893 | 892 | 891 | 892 | 21498909
147 | Bheramara 410 MW CCPP | 230 | 230 | 230 | 235 | 230 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 270 | 230 | 230 | 225 | 215 | 200 |  | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 5284800
148 | Payra 1320 MW | 820 | 770 | 790 | 810 | 560 | 500 | 500 | 540 | 560 | 570 | 580 | 670 | 780 | 840 | 750 | 750 | 740 | 680 |  | 600 | 690 | 680 | 680 | 660 | 650 | 630 | 18045200
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 169 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4137000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 5 | 5 | 3 | 2 | 0 | 0 | [8 empty] | 36720
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 170 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 130 | 130 | 130 | 130 | 145 | 160 | 160 | 160 | 160 | 160 |  | 153 | 173 | 174 | 174 | 174 | 150 | 130 | 3922991
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 356 | 305 | 356 | 360 | 354 | 262 | 265 | 265 | 264 | 234 | 270 | 355 | 415 | 421 | 381 | 390 | 392 | 318 |  | 313 | 313 | 312 | 370 | 338 | 336 | 335 | 7953818
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 22 | 21 | 20 | 19 | 17 | 17 | 17 | 17 | 17 | 20 |  | 21 | 22 | 21 | 22 | 18 | 3 | 3 | 409200
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 0 | 0 | 210906
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [16 empty] | 6 | 36 |  | 35 | 36 | 36 | 35 | 35 | 36 | 0 | 227892
169 | Natore 52 MW PP (Rajlanka) | [19 empty] | 8 | [5 empty] | 0 | 5578
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | 35 | [5 empty] | 0 | 1 | 35 | 35 | 35 | 50 | 35 | 35 | 40 |  | 81 | 94 | 94 | 94 | 94 |  | 0 | 889728
172 | Confidence Power Bogura Unit-1 113 MW | [17 empty] | 30 |  | 35 | 35 | 35 | 35 |  |  | 0 | 158208
173 | Rangpur 20 MW GTPP | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 34 | [5 empty] | 0 | 30 | 34 | 47 | 95 | 106 | 107 | 70 | 106 |  | 107 | 107 | 107 | 107 | 49 | 34 | 34 | 1148592
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 1 | 2 | 3 | 4 | 4 | 5 | 4 | 2 | 2 | 0 | [8 empty] | 32231
178 | Energypac Power Venture Thakurgaon Ltd. | [9 empty] | 0 | 2 | 34 | 36 | 17 | 35 | 35 | 35 | 52 |  | 72 | 72 | 72 | 70 | 35 | 35 | 35 | 616320
| Intraco Solar 30 MW | [6 empty] | 3 | 9 | 19 | 26 | 28 | 33 | 31 | 27 | 21 | 14 | 6 | 0 | [8 empty] | 226700
| Adani Power Jharkhanda Ltd | 608 | 606 | 598 | 598 | 588 | 605 | 600 | 605 | 607 | 610 | 611 | 604 | 595 | 592 | 583 | 613 | 613 | 609 |  | 599 | 582 | 609 | 599 | 610 | 615 | 610 | 14558182
178 | Teesta Solar Limited | [6 empty] | 21 | 62 | 103 | 148 | 141 | 140 | 160 | 97 | 89 | 71 | 31 | 3 | [8 empty] | 1106450