## Daily Gen
Hourly Generation & Demand
Date: | 2017-03-29
Time | Generation | Demand | Loadshed | Remarks
Hour | MW | MW | MW
1:00 | 7125 | 7125 | 0
2:00 | 6736 | 6736 | 0
3:00 | 6500 | 6500 | 0
4:00 | 6307 | 6307 | 0
5:00 | 6197 | 6197 | 0
6:00 | 6145 | 6145 | 0
7:00 | 6012 | 6012 | 0
8:00 | 5819 | 5819 | 0
9:00 | 6210 | 6210 | 0
10:00 | 6374 | 6374 | 0
11:00 | 6548 | 6548 | 0
12:00 | 6650 | 6650 | 0 | Day peak
13:00 | 6700 | 6700 | 0
14:00 | 6612 | 6612 | 0
15:00 | 6858 | 6858 | 0
16:00 | 6646 | 6646 | 0
17:00 | 6460 | 6460 | 0
18:00 | 6873 | 6873 | 0
18:30 | 0 | 0 | 0
19:00 | 7955 | 7955 | 0
19:30 | 8099 | 8099 | 0 | Evening peak
20:00 | 8027 | 8027 | 0
21:00 | 7901 | 7901 | 0
22:00 | 7924 | 7924 | 0
23:00 | 7639 | 7639 | 0
24:00 | 7357 | 7357 | 0

## forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [7 empty] | 2017-03-30 | Thursday
|  | Date (day): | 2017-03-30 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 8130 | MW |  |  | (b) At Evening Peak Hour : |  | 9415 | MW
Sl. No. | Name of the Power Stations |  | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
[8 empty] | On | 2017-03-29 | 2017-03-30 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Nos. of Unit X Capacity (MW) | MW | MW | MW | MW | MW | MW | MW | MW
1 | a) Ghorasal ST: Unit-1, 2 |  | Gas | PDB | 2*55 | 110 | 85 | 40 | 40 | 40 | 40 |  | 45 | # 1 under maint.
| b) Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 175 | 175 | 180 | 180
| c) Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  |  | Under maint. |  | unknown.
| d) Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | 2016-01-10 |  | Long term maint.
| e) Ghorasal ST: Unit-6 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | #6(18/07/10)(18/07/10) |  | Long term maint.
2 | Ghorashal 100MW(Aggreko) |  | Gas | QRPP | 128*0.85 | 100 | 100 | 98 | 97 | 100 | 100 |  | 3
3 | Ghorashal 45MW (Aggreko) |  | Gas | QRPP | 58*0.85 | 45 | 45 | 43 | 45 | 45 | 45
4 | Ghorashal 78.5MW (MAX) |  | Gas | QRPP | 4*21.5 | 78 | 78 | 70 | 40 | 78 | 78
5 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 88 | 85 | 97 | 100 |  | 23
6 | Haripur GT: Unit-1, 2 |  | Gas | PDB | 2*32 | 64 | 40 | 20 | 20 | 20 | 20 |  | 40 | #2,3 Under maint.
7 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 405 | 350 | 412 | 412
8 | Haripur NEPC (HFO) |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 96 | 110 | 110
9 | Haripur Power CCPP |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 276 | 278 | 300 | 300 | 82 |  | Gas shortage
10 | Meghnaghat CCPP |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 430 | 390 | 450 | 450
11 | Meghnaghat (IEL) |  | HFO | RPP | 12*8.9 | 100 | 100 | 10 | 100 | 90 | 100
12 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 305 |  |  | Reserve.
13 | Madanganj (Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 97 | 97 | 80 | 100
14 | Madanganj-55 MW |  | HFO | IPP | 5*17.08+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55
15 | Keraniganj (Powerpac) |  | HFO | RPP | 8*13.45 | 100 | 100 | 30 | 93 | 93 | 93 |  | 7 | Engine problem
16 | Narshingdi (Doreen) |  | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
17 | Siddhirgonj ST |  | Gas | PDB | 1*210 | 210 | 150 | 117 | 110 | 110 | 110
18 | Siddhirgonj GT: Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 40 | 0 | 210
19 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 18 | 100 | 100
20 | Siddhirganj (Dutch Bangla) |  | HFO | RPP | 12*8.9 | 100 | 100 | 85 | 100 | 90 | 100
| Siddhirganj CCPP-335 MW |  | Gas | EGCB |  |  |  | 0 | 0 | 0 | 0 |  |  | On test
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 0 | 0 | 50 | 50
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 93 | 94 | 94 |  | 9
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 6 | 42 | 40 | 43
24 | Kodda Peaking |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 84 | 150 | 149 | 149
25 | Northern 55 MW |  | HFO | RPP |  | 55 | 55 | 18 | 54 | 55 | 55
26 | Southern Power |  | HFO | RPP | 3*19.3 | 55 | 55 | 18 | 55 | 55 | 55
27 | CLCPC Keranigonj 108 MW |  | HFO | IPP | 12*8.924 | 108 | 108 | 8 | 103 | 80 | 104
28 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 6*3.67+7*8.73 | 80 | 80 | 57 | 57 | 57 | 58 |  | 23
29 | Summit Power, Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
30 | Summit Power, Rupganj |  | Gas | SIPP,REB | 4*8.74 | 33 | 33 | 17 | 33 | 33 | 33
31 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 34 | 26 | 43 | 43 |  | 26 | Engine problem
32 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| Dhaka Area Total |  |  |  |  | 4854 | 4633 | 2304 | 2857 | 3201 | 3537 | 397 | 556
33 | a) Chittagong ST: Unit-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  |  | Gas shortage
| b) Chittagong ST: Unit-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  |  | Under maint.
34 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 17 | 17 | 25 | 25
35 | Patenga 50MW (Barakatullah) |  | HFO | IPP | 8*6.984 | 50 | 50 | 50 | 49 | 50 | 50
36 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40, 3*50 | 230 | 230 | 85 | 109 | 130 | 130 |  | 100 | Unit-2 & 5 Under maint.
37 | Sikalbaha ST |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
| Sikalbaha 225 MW |  | Gas | PDB |  |  |  | 0 | 0 |  |  |  |  | On test
38 | Sikalbaha Peaking GT |  | Gas | PDB | 1*150 | 150 | 150 | 80 | 110 | 110 | 120 | 150 |  | Gas shortage
39 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 51 | 51 | 51 | 51 |  | 0
40 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 67 | 0 | 60
41 | Dohazari-Kalaish Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 16 | 83 | 16 | 102
42 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 90 | 100 | 90 | 100
43 | Barabkunda (Regent) |  | Gas | SIPP,PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Transformer problem.
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  |  | 2 | 15 | 10 | 20
44 | Chittagong ECPV 108 MW |  | HFO | IPP |  | 108 | 108 | 98 | 98 | 97 | 100 |  | 10 | Engine problem
| Chittagong area Total |  |  |  |  | 1416 | 1336 | 489 | 699 | 579 | 758 | 190 | 132
45 | a) Ashuganj ST: Unit- 1 & 2 |  | Gas | APSCL | 2*64 | 64 | 53 | 0 | 0 | 0 | 0 |  | 53 | #1,2 Under maint.
| b) Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 132 | 132 | 132 | 132
| c) Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 |  |  | under maint. |  | 31/03/2017
| d) Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 135 | 135 | 135 | 135
46 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 226 | 200 | 221 | 221
| Ashuganj CCPP(North) |  | Gas | APSCL |  |  |  | 0 | 0 | 0 | 0 |  |  | On test
47 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 361 | 330 | 220 | 360
48 | Ashuganj Engines |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 32 | 30 | 32 |  | 13 | Engine problem
49 | Ashuganj (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 10 | 20 | 52 | 20 | 35
50 | Ashuganj (Aggrekko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 0 | 0 | 0 |  |  | Date expired
51 | Ashuganj (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 10 | 53 | 53 | 43
52 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.7+1*16 | 195 | 195 | 88 | 110 | 110 | 110 | 85 |  | Gas shortage
53 | Ashuganj (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
54 | Brahmanbaria (Aggreko) |  | Gas | QRPP | 86*1.10 | 85 | 85 | 61 | 85 | 85 | 85
55 | Titas (Daudkandi) Peaking |  |  | PDB | 6*8.92 | 52 | 52 | 0 | 41 | 0 | 42
56 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 50 | 50 |  | 113 | ST under maint.
57 | Feni (Doreen) |  | Gas | SIPP,PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 20
58 | Feni, Mohipal (Doreen) |  | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3
** | Tripura |  |  | Imported Power |  | 100 | 100 | 83 | 104 | 92 | 100
59 | Jangalia (Summit) |  | Gas | SIPP,PDB | 4*8.73 | 33 | 33 | 31 | 33 | 33 | 33
60 | Lakdhanvi-52 MW |  | HFO | (IPP) |  | 52 | 52 | 0 | 25 | 44 | 52
61 | Summit Power, Comilla |  | Gas | SIPP,REB | 3*3.6+2*6.9 | 25 | 25 | 22 | 0 | 22 | 22
| Comilla Area Total |  |  |  |  | 2140 | 2069 | 1311 | 1385 | 1357 | 1526 | 163 | 182
62 | RPCL CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 103 | 103 | 100 | 100 | 99 |  | Gas shortage
63 | Tangail (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 20 | 22
64 | Jamalpur IPP |  | HFO | IPP | 12*8.9 | 95 | 95 | 8 | 93 | 95 | 95
| Mymensingh Area Total |  |  |  |  | 327 | 319 | 131 | 218 | 215 | 217 | 99 | 0
65 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 80 | 60 | 60 | 60 | 60
66 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 73 | 73 | 73 | 73
67 | Shahjibazar 330 MW |  | Gas | PDB | 2*110 | 330 | 330 | 148 | 117 | 140 | 165 |  |  | GT-2 Under maint.
68 | Fenchugonj (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 53 | 53 | 51
69 | Fenchuganj (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 40 | 42 | 40 | 42
70 | Hobiganj (Confidence-EP) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 8 | 8 |  | 3
71 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 53 | 40 | 35 | 66
72 | Shahjibazar (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 50 | 40 | 86 | 86
73 | Shahjibazar (Energyprima) |  | Gas | RPP | 27*2.0 | 50 | 50 | 47 | 46 | 50 | 50
74 | Sylhet 150 MW GT |  | Gas | PDB | 1*142 | 142 | 142 | 78 | 79 | 70 | 75 | 63
75 | Sylhet 20 MW GT |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20
76 | Sylhet (Energyprima) |  | Gas | RPP | 27*2 | 50 | 50 | 40 | 47 | 40 | 48
77 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 22 | 24 | 22 | 24
78 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 230 | 220 | 220 | 220 |  |  | DP high.
79 | Sylhet (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 8 | 10
| Sylhet Area Total |  |  |  |  | 1431 | 1396 | 888 | 851 | 925 | 998 | 63 | 3
80 | Bheramara GT: Unit- 1,2,3 |  | HSD | PDB | 3X20 | 60 | 46 | 0 | 16 | 0 | 30 |  | 30 | # 2 under maint.
81 | Bheramara (Quantum) |  | HSD | RPP | 12*8.5+2*6+2*13 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Long term maintenance
** | Bheramara Interconnector(HVDC ) |  |  | Imported Power |  | 500 | 500 | 492 | 497 | 491 | 504
82 | a) Khulna ST 110MW |  | HFO | PDB | 1*110 | 110 | 55 | 0 | 0 | 0 | 0 |  | 55 | 2014-04-11
| b) Khulna ST 60 MW |  | HFO | PDB | 1*60 |  |  | 0 | 0 | 0 | 0 |  |  | Plant retired in FY 2013-2014
83 | Khulna (KPCL-1) |  | HFO | IPP | 19*6.5 | 110 | 110 | 51 | 110 | 110 | 110
84 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 66 | 115 | 115 | 115 |  | 0
85 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 51 | 18 | 50
86 | Khulna CCPP |  | HSD | NWZPGCL | 1*158+1*72 | 230 | 230 | 150 | 120 | 120 | 230
87 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 74 | 28 | 83
Fuel shortage
88 | Noapara (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 32 | 40 | 40
89 | Khulna (Aggreko) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 55 | 0 | 0 | 0 | 40 |  |  | Reserve.
| Khulna Area Total |  |  |  |  | 1488 | 1419 | 767 | 1015 | 922 | 1202 | 0 | 190
90 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 64 | 95 | 110 | 110
91 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
92 | Bhola (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 3 | 16 | 11 | 16 |  | 17 | Engine problem
93 | Bhola CCPP GT-1,2,ST |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 168 | 163 | 187 | 180 |  |  | ST under maint.
| Barisal Area Total |  |  |  |  | 377 | 367 | 235 | 274 | 308 | 336 | 0 | 17
94 | a) Baghabari GT |  | Gas | PDB | 1*71 | 71 | 71 | 60 | 50 | 70 | 70
| b) Baghabari GT |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
95 | Baghabari Peaking |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 0 | 40
96 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 50 | 0 | 50
97 | Amnura |  | HFO | QRPP | 7*7.79 | 50 | 50 | 12 | 50 | 50 | 50
98 | Katakhali (Northern) |  | HFO | QRPP | 6*8.92 | 50 | 50 | 16 | 50 | 50 | 50
99 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 48 | 0 | 44
100 | Sirajganj CCPP |  | Gas | NWPGCL | 1*150+1*75 | 210 | 210 | 214 | 205 | 210 | 210
101 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 36 | 0 | 36
102 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
103 | Bogra (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 7 | 7 | 5 | 7 |  | 3 | Engine problem
104 | Ullapara (Summit) |  | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
105 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 25 | 52 | 52 | 52
| Rajshahi Area Total |  |  |  |  | 809 | 799 | 367 | 621 | 470 | 642 | 0 | 103
106 | a) Barapukuria ST: Unit-1 |  | Coal | PDB | 1*125 | 125 | 100 | 67 | 82 | 74 | 81
| b) Barapukuria ST: Unit-2 |  | Coal | PDB | 1*125 | 125 | 100 | 81 | 79 | 79 | 82
107 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 10 | 0 | 0 | 17
108 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 18 | 0 | 19
109 | Thakurgaon (RZ) |  | HSD | RPP | 20*1.5+21*1.1 | 47 | 0 | 0 | 0 | 0 | 0 |  |  | Under maint.
| Rangpur Area Total |  |  |  |  | 337 | 240 | 158 | 179 | 153 | 199 | 0 | 0
| Total |  |  |  |  | 13179 | 12578 | 6650 | 8099 | 8130 | 9415 | 912 | 1183
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6295.2895 | 7667 | 7696.3465 | 8912.8047
A. |  | 2017-03-29 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 8099 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 5819 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8099 | MW
3 | Day peak Generation : |  |  | 6650 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 7667 | MW
4 | Evening peak Generation : |  |  | 8099 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  |  | 164.8025 | MKWHr |  |  | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 107.7511 | MKWHr |  | By Oil: | 37.1928 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.6833 | MKWHr |  | By Hydro: | 2.114 | MKWHr | Area | Demand | Supply | Loadshed | (Duration) |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Gas: | 912 | For Oil: | 0 | MW | Dhaka | 3050 | 3050 | 0
|  |  | For Water Shortage: |  |  | 100 | MW | Chittagong | 920 | 920 | 0 |  |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob: |  |  | 1183 | MW | Khulna | 918 | 918 | 0 |  |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 922.39 | MMCFD |  |  | Rajshahi | 924 | 924 | 0 |  |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 64501550.534 | ii) Oil : | Taka | 359881639.882 | Comilla | 585 | 585 | 0 |  |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 14335578.74 | Total | Taka | 438718769.156 | Mymensingh | 471 | 471 | 0 |  |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 7.8675 | MKWHr. | Sylhet | 197 | 197 | 0 |  |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -580 | MW at | 19:30 | hrs | Barisal | 136 | 136 | 0 |  |  | 22:00 |  | 0
| iii) Maximum : |  |  | -190 | MW at | 10:00 | hrs | Rangpur | 466 | 466 | 0 |  |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30.1° C |  |  | Total | 7667 | 7667 | 0
B. |  | 2017-03-30 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 36.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 9415 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 6700 | MW
4 | Reserve (Generation end) |  |  |  | 715 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 170 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5367 | MW at | 4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.9127 | MKWHr. | ii) During Peak demand: |  | 497 | MW at | 19:30 | hrs. | iii)Maximum: | 497 | 11:00
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.1485 | MKWHr.
*Cost for HVDC & Tripura energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 89.17 |  | (b) Today: | 88.94 |  | (c) Rule Curve: |  | 88.51
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2017-03-30
Till now the maximum generation is : - |  |  | 9036 MW | 21:00 | Hrs on | 2016-06-30
The Summary of Yesterday's |  | 2017-03-29 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6650 | MW Hour : | 12:00 | Min. Gen. at | 4:00 | 5367 | MW
Evening Peak Generation : |  | 8099 | MW Hour : | 19:30 | Max Generation : |  | 9415 | MW
E.P. Demand (at gen end) : |  | 8099 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 8700 | MW
Maximum Generation : |  | 8099 | MW Hour : | 19:30 | Reserve (Generation end) |  | 715 | MW
Total Gen. (MKWH) : |  | 164.8025 | System L/ Factor : | 84.79% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -190 | MW at | 10:00 | Energy | 7.8675 | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2017-03-30
Actual : | 88.94 | Ft.(MSL) , | Rule curve : | 88.51 | Ft.( MSL )
Gas Consumed : | Total | 922.39 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 64501550.534
|  | Coal : | 14335578.74 | Oil : | 359881639.882 | Total : | 438718769.156
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3286 |  |  | - | -
Chittagong Area | 0 | 0:00 | 919 |  |  | - | -
Khulna Area | 0 | 0:00 | 933 |  |  | - | -
Rajshahi Area | 0 | 0:00 | 900 |  |  | - | -
Comilla Area | 0 | 0:00 | 675 |  |  | - | -
Mymensingh Area | 0 | 0:00 | 513 |  |  | - | -
Sylhet Area | 0 | 0:00 | 331 |  |  | - | -
Barisal Area | 0 | 0:00 | 179 |  |  | - | -
Rangpur Area | 0 | 0:00 | 500 |  |  | - | -
Total | 0 |  | 8236 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Ghorasal ST: Unit-6 (18/07/10) |  | 10) Sikalbaha ST
| Nil |  |  | 2) Kaptai Unit-2 & 5 |  | 11) Ghorasal ST: Unit-1
3) Ashuganj ST: Unit- 1,2,4
4) Khulna ST 110 MW (04/11/2014)
5) Ghorasal Unit-4,5
6) Baghabari 100 MW
14) Tongi GT
8) Chittagong Unit-2
9)Thakurgaon (RZ)
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
| Description |  |  | Comments on Power Interruption
a) Natore-Ishurdi 132 kV Ckt-1 was under shut down from 09:15 to 10:31 for red hot maintenance at Y-phase CB
terminal at Natore end.
b) Rajshahi 132/33 kV T3 transformer was under shut down from 11:55 to 12:31 for red hot maintenance at 33 kV |  |  |  | About 40 MW power interruption occurred under Rajshahi S/S
airport feeder. |  |  |  | areas from 11:55 to 12:31.
c) Sikalbaha 225 MW (new) was synchronized at 13:10.
d) Bogra 230/132 kV TR1 transformer tripped at 13:02 showing lock out relay at HV side and was switched on at 13:21.
e) Barishal 132/33 kV T1 & T2 transformer tripped at 11:53 showing O/C & instantaneous relay and were switched on |  |  |  | About 68 MW power interruption occurred under Barishal S/S
at 12:09. |  |  |  | areas from 11:53 to 12:09.
f)Bakulia-Khulshi 132 kV Ckt-1 was under shut down from 12:50 to 13:39 for red hot maintenance at R-phase CB
g) Sikalbaha 150 MW was shut down due to gas shortage.
h) Savar 132/33 kV T1 & T2 transformer tripped at 15:18 from 33 kV side showing O/C & E/F relay and were |  |  |  | About 20 MW power interruption occurred under Savar S/S
switched on at 15:49 & 16:17 respectively. |  |  |  | areas from 15:18 to 15:49.
i) After maintenance Kulaura 132/33 kV T2 transformer switched on at 15:57.
j) Barishal-Patuakhali 132 kV Ckt tripped at 17:04 from Barisal end Showing O/C & E/F relay and was switched on |  |  |  | About 25 MW power interruption occurred under Patuakhali S/S
at 23:40. |  |  |  | areas from 17:04 to 23:40.
k) Barishal-Bhandaria 132 kV Ckt tripped at 19:42 from Barisal end Showing O/C relay and was switched on
at 23:48.
l) Barisal 132/33 kV T1 & T2 transformer tripped at 19:42 from 33 kV side showing O/C relay at 33 kV Jhalakhati |  |  |  | About 80 MW power interruption occurred under Barisal S/S
feeder and were switched on at 19:55. |  |  |  | areas from 19:42 to 19:55.
m) Bashundhara-Rampura 132 kV Ckt-1 & 2 tripped at 21:54 from both end showing dist Z1 at Rampura end and |  |  |  | About 35 MW power interruption occurred under Basundhara S/S
protection operated LBP-1 at Basundhara end and were switched on at 22:18 & 22:49 respectively. |  |  |  | areas from 21:54 to 22:49.
n) Bashundhara-Tongi 132 kV Ckt-1 tripped at 21:54 from Basundhara end Showing high speed BBS at Basundhara
end and was switched on at 22:25 .
o) Ashuganj(S) 450MW CCPP ST is under shut down since at 04:28(30/3/17) due to problem of HPST line.
p) Bheramara HVDC pole got tripped at 03:56 showing group differential operated and was switched on at 07:20.
q) Khulna© -Noapara 132 kV Ckt-1 & 2 tripped at 07:37 from Khulna © end showing E/F & instantaneous relay and |  |  |  | About 215 MW power interruption occurred under Noapara, Jessore
were switched on at 07:47 & 07:48(30/3/17) respectively |  |  |  | Jhenaidah, Magura S/S areas from 07:37 to 07:47(30/3/17)..

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2017-03-29 | [6 empty] | Page -2
[5 empty] | Present | Peak Hour | Energy
| Name of Power Station |  | Unit | Producer | Generation | Generation | Generated |  | Remarks
Capacity
[5 empty] | MW | MW | KWHr
1a | Ghorasal ST: Unit-1, 2 |  | 2*55 | PDB | 85 | 0 | 856000 | Under maint.
40
1b | Ghorasal ST: Unit-3 |  | 1*210 | PDB | 170 | 175 | 4261005 | 0
1c | Ghorasal ST: Unit-4 |  | 1*210 | PDB | 180 | 0 | 0 | Under maint.
1d | Ghorasal ST: Unit-5 |  | 1*210 | PDB | 190 | 0 | 0 | Under maint.
1e | Ghorasal ST: Unit-6 |  | 1*210 | PDB | 190 | 0 |  | Long term maint.
2 | Ghorashal 100MW(Agreko) |  | 128*0.85 | QRPP | 100 | 97 | 2249940 | 0
3 | Ghorashal 45MW(Agreko) |  | 58*0.85 | QRPP | 45 | 45 | 1012260 | 0
4 | Ghorashal 78.5 MW (MAX) |  | 4*21.5 | QRPP | 78 | 40 | 1423744 | Frequency control
5 | Ghorashal (Regent) |  | 34*3.35 | IPP | 108 | 85 | 2103454 | Frequency control
6 |  |  | 1*32 | PDB | 20 | 20 | 484200
| Haripur GT: Unit-1, 2, 3 |  | 1*32 | PDB | 20 | 0
|  |  | 1*32 | PDB | 0 | 0 |  | Under maint.
7 | Haripur EGCB 412 MW CCPP |  | 1*273+1*139 | EGCB | 412 | 350 | 9098000 | Frequency control
8 | Haripur NEPC(HFO) |  | 8*15 | IPP | 110 | 96 | 256600 | Low demand
9 | Haripur Power CCPP |  | 1*235+1*125 | IPP | 360 | 278 | 6736000 | Gas shortage
10 | Meghnaghat CCPP |  | 2*150+1*150 | IPP | 450 | 390 | 9062000 | Frequency control
11 | Meghnaghat (IEL) |  | 12*8.9 | RPP | 100 | 100 | 602880 | 0
12 | Meghnaghat CCPP(Summit) |  | 2*110+1*110 | IPP | 305 | 0 | 0 | Reserve
13 | Madanganj (Summit) |  | 6*17 | QRPP | 100 | 97 | 1793856 | 0
14 | Madanganj-55 MW |  | 5*17.08+1*11.3 | IPP | 55 | 55 | 351511 | 0
15 | Keraniganj (Powerpac) |  | 8*13.45 | RPP | 100 | 93 | 749561 | 0
16 | Narsingdi (Doreen) |  | 8 * 2.9 | SIPP, REB | 22 | 22 | 494388 | 0
17 | Siddhirgonj ST |  | 1*210 | PDB | 150 | 110 | 2523150 | 0
18 | Siddhirgonj GT : Unit-1 & 2 |  | 2*105 | EGCB | 210 | 0 | 809000 | Gas shortage
19 | Siddhirgonj (Desh) |  | 96*1.2 | QRPP | 100 | 18 | 70080 | Low demand
20 | Siddhirgonj (Dutch Bangla) |  | 12*8.9 | RPP | 100 | 100 | 1752000 | 0
| Siddhirganj CCPP-335 MW |  |  | EGCB |  | 0 | 0 | On test.
21 | Pagla (DPA) |  | 100*0.5 | QRPP | 50 | 0 | 9540 | Reserve
22 | Gagnagar (Orion) |  | 12*8.924 | IPP | 102 | 93 | 716832 | 0
23 | Katpotti 52 MW |  |  | RPP | 51 | 42 | 200160 | Engine problem
24 | Kodda Peaking |  | 9*17.06 | BPDB-RPCL | 149 | 150 | 1835520 | 0
25 | Northern 55 MW |  |  | RPP | 55 | 54 | 551105 | 0
26 | Southern Power |  |  | RPP | 55 | 55 | 779000 | 0
27 | CLCPC Keranigonj 108 MW |  |  |  | 108 | 103 | 465600 | 0
28 | Summit Power,(Madhabdi+Ashulia) |  | 6*3.67+7*8.73 | SIPP, REB | 80 | 57 | 1264100 | 0
29 | Summit Power, Maona |  | 4*8.73 | SIPP, REB | 33 | 33 | 800500 | 0
30 | Summit Power, Rupganj |  | 4*8.74 | SIPP, REB | 33 | 33 | 713800
31 | Gazipur (RPCL) |  | 6*8.9 | IPP | 52 | 26 | 806052 | Engine problem
32 | Tongi GT |  | 1*105 | PDB | 105 | 0 | 0 | Under maintenance.
| Dhaka Area Total |  |  |  | 4633 | 2857 | 54831838
33 | a) Chitagong ST:Unit-1 |  | 1*210 | PDB | 180 | 0 | 0 | Gas shortage
| b) Chitagong ST:Unit-2 |  | 1*210 | PDB | 180 | 0 | 0 | Under maint.
34 | Raozan 25 MW (RPCL) |  | 3*8.9 | IPP | 25 | 17 | 414720 | 0
35 | Patenga 50 MW(Barakatulla) |  | 8*6.89 | IPP | 50 | 49 | 1043040 | 0
36 | Chittagong ECPV 108 MW |  |  | IPP | 108 | 98 | 2203200 | Engine problem
37 |  |  | 1*40 | PDB | 40 | 39 | 1091042
|  |  | 1*40 | PDB | 40 | 40
| Karnafuli Hydro Power Station |  | 1*50 | PDB | 50 | 0 |  | Under maint.
|  |  | 1*50 | PDB | 50 | 30 | 1023000
|  |  | 1*50 | PDB | 50 | 0 |  | Under maint.
38 | Shikalbaha ST |  | 1*60 | PDB | 40 | 0 | 0 | Gas shortage
| Shikalbaha 225 MW |  |  | PDB
39 | Shikalbaha peaking GT |  | 1*150 | PDB | 150 | 110 | 1749150 | 0
40 | Hathazari peaking |  | 11*8.9 | PDB | 98 | 67 | 600280 | 0
41 | Dohazari-Kalaish peaking |  | 6*17 | PDB | 102 | 83 | 1085670 | Low demand
42 | Juldah (Acorn) |  | 8*13.45 | QRPP | 100 | 100 | 2036400 | 0
43 | Shikalbaha (Energis) |  |  | RPP | 51 | 51 | 1105440 | 0
44 | Barabkunda (regent) |  | 8*2.90 | SIPP, PDB | 22 | 0 | 0 | Transformer problem
* | Malancha, Ctg EPZ(United) |  |  |  |  | 15 | 420000
| Chittagong Area Total |  |  |  | 1336 | 699 | 12771942
45 | a) Ashuganj ST: Unit- 1 & 2 |  | 1*64 | APSCL | 53 | 0 | 0 | Under maint.
|  |  | 1*64 | APSCL |  | 0 |  | 0
| b) Ashuganj ST: Unit- 3 |  | 1*150 | APSCL | 135 | 132 | 3123976 | 0
| c) Ashuganj ST: Unit- 4 |  | 1*150 | APSCL | 129 | 0 | 0 | Under maintenance.
| d) Ashuganj ST: Unit- 5 |  | 1*150 | APSCL | 134 | 135 | 3235814
46 | Ashuganj CCPP 225 MW |  | 1*142+1*75 | APSCL | 221 | 200 | 8700120 | frequency control.
| Ashuganj CCPP(North) |  |  | APSCL |  | 0 | 0 | On test
47 | Ashuganj CCPP(South) |  |  | APSCL | 360 | 330 | 5194300 | frequency control.
48 | Ashuganj-Engines |  | 14*3.968 | APSCL | 45 | 32 | 744120 | Engine problem
49 | Ashugonj (Precision) |  | 15*4 | RPP | 55 | 20 | 390720 | Gas shortage
50 | Ashuganj (Aggrekko) |  | 82*1.1 | RPP | 95 | 0 | 0 | Date expired
51 | Ashuganj (United) |  | 14*4 | RPP | 53 | 10 | 170000 | Gas shortage
52 | Ashuganj Modular 200 MW |  | 20*9.7+1*16 | IPP | 195 | 110 | 2810181 | Gas shortage
53 | Ashuganj (Midland) |  | 6*9.34 | IPP | 51 | 51 | 921548
54 | Brahmanbaria (Aggreko) |  | 72*1.1 | QRPP | 85 | 85 | 1180236 | 0
55 | Titas (Daudkandi) Peaking |  | 6 * 8.92 | PDB | 52 | 41 | 41688 | 0
56 | Chandpur CCPP |  | 1*106+1*57 | PDB | 163 | 50 | 1157990 | ST under maint.
57 | Feni(Doreen) |  | 8 *2.94 | SIPP, PDB | 22 | 19 | 406944
58 | Feni Mohipal (Doreen) |  | 4*2.9 | SIPP, REB | 11 | 8 | 180540 | 0
** | Tripura |  |  |  | 100 | 104 | 2148480 | 0
59 | Jangalia (Summit) |  | 4*8.73 | SIPP, PDB | 33 | 33 | 802100 | 0
60 | Lakdanavi-52 MW |  |  | IPP | 52 | 25 | 45000 | Low demand
61 | Summit Power,Comilla |  | 3*3.67+2*6.9 | SIPP, REB | 25 | 0 | 508900 | Engine problem
| Comilla Area Total |  |  |  | 2069 | 1385 | 31762657
62 | RPCL CCPP |  | 4*35+1*70 | IPP | 202 | 103 | 2674000 | Gas shortage
63 | Tangail (Doreen) |  | 8 *2.9 | SIPP,PDB | 22 | 22 | 488016 | 0
64 | Jamalpur RPP |  |  | IPP | 95 | 93 | 589014 | 0
| Mymensingh Area Total |  |  |  | 319 | 218 | 3751030
65 | Fenchugonj CCPP-1 |  | 2*32+1*33 | PDB | 80 | 60 | 1365000 | 0
66 | Fenchugonj CCPP-2 |  | 2*35+1*35 | PDB | 90 | 73 | 1741880 | 0
67 | Shahjibazar CCPP 330 MW |  | 2*110 | PDB | 330 | 117 | 3402057 | GT-2 under maint.
68 | Fenchugonj RPP (51 MW) |  | 2.9*19 | RPP | 51 | 53 | 1255200
69 | Fenchuganj (Energyprima) |  | 12*3.3+5*2 | RPP | 44 | 42 | 970000 | 0
70 | Hobiganj (Confidence-EP) |  | 4*2.9 | SIPP, REB | 11 | 0 | 109920 | 0
0
71 | Shahjibazar GT: Unit-8,9 |  | 32*2.9 | PDB | 66 | 40 | 776000 | 0
72 | Shahjibazar (Shahjibazar) |  | 32*2.9 | RPP | 86 | 40 | 1099200 | frequency control.
73 | Shahjibazar (Energyprima) |  | 27*2.0 | RPP | 50 | 46 | 1001880 | 0
74 | Sylhet 150 MW GT |  | 1*142 | PDB | 142 | 79 | 1824840 | 0
75 | Sylhet 20 MW GT |  | 1*20 | PDB | 20 | 0 | 0 | Gas shortage
76 | Sylhet (Energyprima) |  | 27 * 2.0 | RPP | 50 | 47 | 922580 | 0
77 | Shahjahanulla 25MW |  | 3 * 9.34 | CIPP,REB | 25 | 24 | 558888 | 0
78 | Summit Bibiana-2 |  | 1*222+1*119 | IPP | 341 | 220 | 5708450 | Machine problem.
79 | Sylhet (Desh) |  | 6*1.95 | RPP | 10 | 10 | 121320 | 0
| Sylhet Area Total |  |  |  | 1396 | 851 | 20857215
|  |  | 1*20 | PDB | 16 | 16 | 819072
80 | Bheramara GT: Unit-1,2,3 |  | 1*20 | PDB | 14 | 0
|  |  | 1*20 | PDB | 16 | 0 |  | Long term maint.
** | Bheramara Interconnector(HVDC) |  |  | Imported Power | 500 | 497 | 11912727 | 0
81 | a) Khulna ST 110 MW |  | 1*110 | PDB | 55 | 0 | 0 | Under maint.
| b) Khulna ST 60 MW |  | 1*60 | PDB |  | 0 | 0 | Plant Retired in FY 2013-2014
82 | Khulna (KPCL-1) |  | 19*6.5 | IPP | 110 | 110 | 1133760 | 0
83 | Khulna (KPCL-2) |  | 7*17 | QRPP | 115 | 115 | 1872960
84 | Faridpur Peaking |  | 8*6.89 | PDB | 54 | 51 | 312480 | 0
85 | Khulna 150 MW GT |  | 1*150 | NWZPGCL | 230 | 120 | 3190080 | Low demand
86 | Gopalganj Peaking |  | 16*6.98 | PDB | 109 | 74 | 40500 | Low demand
87 | Bheramara (Quantum) |  | 12*8.5+2*6+2*13 | RPP | 105 | 0 | 0 | All Engine problem, Long term maint
88 | Noapara (Khanjahan Ali) |  | 5*8.5 | QRPP | 40 | 32 | 481500 | 0
89 | Khulna (Aggreko) 55MW |  | 71*0.85 | QRPP | 55 | 0 | 10250 | Low demand
| Khulna Area Total |  |  |  | 1419 | 1015 | 19773329
90 | Summit Barisal 110MW |  | 7*17.076 | IPP | 110 | 95 | 2152320 | 0
91 | Barisal GT: Unit-1,2 |  | 1*20 | PDB | 16 | 0 | 0 | Reserve
|  |  | 1*20 | PDB | 14 | 0 |  | Reserve
92 | Bhola (Venture) |  | 1*34.5 | RPP | 33 | 16 | 245308 | Engine problem
93 | Bhola CCPP GT-1,2,ST |  | 2*63+1*68 | PDB | 194 | 163 | 4337582 | 0
| Barisal Area Total |  |  |  | 367 | 274 | 6735210
94 | a) Baghabari GT |  | 1*71 | PDB | 71 | 50 | 1520000 | frequency control.
| b) Baghabari GT |  | 1*100 | PDB | 100 | 0 | 0 | Under maint.
95 | Baghabari Peaking |  | 6*8.9 | PDB | 52 | 40 | 216098 | 0
96 | Bera Peaking |  | 9*8.29 | PDB | 71 | 50 | 211070 | 0
97 | Amnura |  | 7*7.79 | QRPP | 50 | 50 | 426580 | 0
98 | Katakhali (Northern) |  | 6*8.92 | QRPP | 50 | 50 | 391928 | 0
99 | Katakhali Peaking |  | 6*8.7 | PDB | 50 | 48 | 307702 | 0
100 | Sirajganj CCPP |  | 1*50+1*75 | NWPGCL | 210 | 205 | 5318473 | 0
101 | Santahar Peaking |  | 6*8.7 | PDB | 50 | 36 | 210305 | 0
102 | Bogra (GBB) |  | 6*4 | RPP | 22 | 22 | 506200 | 0
103 | Bogra (Energyprima) |  | 5*3.3+5*2 | RPP | 10 | 7 | 157932 | Engine problem
104 | Ullapara (Summit) |  | 4 *2.90 | SIPP, REB | 11 | 11 | 222876 | 0
105 | Rajlanka 52 MW |  | 6*8.92 | IPP | 52 | 52 | 484320 | 0
| Rajshahi Area Total |  |  |  | 799 | 621 | 9973484
106 | a) Barapukuria ST: Unit-1 |  | 1*125 | PDB | 100 | 82 | 1806545 | 0
| b) Barapukuria ST: Unit-2 |  | 1*125 | PDB | 100 | 79 | 1876800 | 0
107 | Rangpur GT |  | 1*20 | PDB | 20 | 0 | 20500 | Reserve
108 | Saidpur GT |  | 1*20 | PDB | 20 | 18 | 73000 | 0
109 | Thakurgaon (RZ) |  | 20*1.5+21*1.1 | RPP | 0 | 0 | 0 | Under maint.
| Rangpur Area Total |  |  |  | 240 | 179 | 3776845
| Total |  |  |  | 12578 | 8099 | 164233550
| Eastern Grid Total |  |  |  | 8488 | 6010 | 123974682
| Western Grid Total |  |  |  | 2600 | 2089 | 40258868
| National Grid Total |  |  |  | 11088 | 8099 | 164233550
*Data collected from respective power station over telephone.

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2017-03-29 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 5223 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2444 | MW
i) Dhaka area |  |  | 3050 | MW | i) Khulna area |  |  | 918 | MW
ii) Chittagong area |  |  | 920 | MW | ii) Rajshahi area |  |  | 924 | MW
iii) Comilla area |  |  | 585 | MW | iii) Barisal area |  |  | 136 | MW
iv) Mymensingh area |  |  | 471 | MW | iv) Rangpur area |  |  | 466 | MW
v) Sylhet area |  |  | 197 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 7667 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 112 | 1500 | Kishorganj | 54 | 2000 | Jessore | 131 | 1930
Munsiganj | 84 | 2100 | Netrokona | 45 | 2000 | Jhenida | 76 | 2300
Megnaghat | 61 | 1900 | Jamalpur | 78 | 2100 | Bottail | 92 | 1900
Shyampur | 152 | 1000 | Sherpur | 50 | 1900 | G.K Project | 40 | 1900
Bhulta | 129 | 100 | Srimongal | 28 | 1830 | Faridpur | 96 | 2200
Madanganj | 45 | 800 | Shahjibazar | 40 | 100 | Madaripur | 80 | 100
Shitalakhya | 99 | 1600 | Fenchuganj | 26 | 1800 | Gopalganj | 58 | 1900
Rahim steel | 14 | 800 | Khulawara | 16 | 1800 | Bagerhat | 62 | 2000
Matuail | 62 | 200 | Sylhet | 107 | 2100 | Mongla | 36 | 900
Ghorasal | 85 | 2000 | Chatak | 29 | 2200 | Satkhira | 76 | 1900
Narsingdi | 81 | 1930 | Comilla (S) | 114 | 2200 | Gallamari | 41 | 1830
Haripur (SBU) | 47 | 100 | Comilla(N) | 61 | 2300 | Magura | 32 | 1830
Ullon | 54 | 1830 | Chandpur | 91 | 1900 | Chuadanga | 60 | 1900
Hasnabad | 142 | 2000 | Feni | 79 | 2100 | Barisal | 90 | 2200
Magbazar | 107 | 1300 | Chowmuhani | 156 | 2000 | Patuakhali | 40 | 100
Maniknagar | 70 | 1300 | Ashuganj | 41 | 2200 | Bhandaria | 36 | 2100
Bangabhaban | 34 | 1500 | Daudkandi | 68 | 2200 | Ishurdi | 41 | 1900
Narinda | 80 | 1200 | B.Baria | 66 | 2100 | Natore | 92 | 1930
Dhanmondi | 132 | 1300 | Madanhat | 54 | 1830 | Bogra | 188 | 1900
Lalbag | 90 | 1200 | Hathazari | 88 | 2100 | Noagaon | 83 | 1900
Madartek | 52 | 2000 | Khulshi | 164 | 1900 | Rajshahi | 123 | 1900
Mirpur | 101 | 1900 | Halishahar | 113 | 1700 | C.Nawabganj | 59 | 1900
Kalyanpur | 99 | 1830 | Baraulia | 115 | 1100 | Amnura | 34 | 1900
Gulshan | 101 | 1400 | Sikalbaha | 33 | 1900 | Pabna | 90 | 1900
Uttara | 75 | 1900 | Dohazari | 88 | 2200 | Shahjadpur | 77 | 2000
Kamrangirchar | 80 | 1900 | Cox'sbazar | 60 | 1830 | Serajganj | 78 | 2000
Savar | 96 | 1830 | Chandraghona | 29 | 1830 | Niyamatpur | 60 | 1930
Bhasantec | 101 | 1830 | Kaptai | 4 | 1900 | Joypurhat | 29 | 1900
Agargaon | 36 | 1900 | A. Khaer Stl. | 22 | 1000 | Rangpur | 91 | 1930
Satmosjid | 50 | 1900 | Bakulia | 97 | 1830 | Lalmonirhat | 48 | 2000
Tongi | 116 | 1100 | Julda | 18 | 100 | Saidpur | 93 | 1900
Kabirpur | 171 | 1830 | TK chemical | 3 | 1200 | Purbasadipur | 67 | 1900
Basundhara | 101 | 1900 | Modern Steel | 16 | 1600 | Thakurgaon | 51 | 2000
Manikganj | 79 | 2100 | Shahmirpur | 26 | 2300 | Palashbari | 67 | 2000
Joydevpur | 190 | 1800 | Abul Khair 230 | 183 | 2400 | Barapukuria | 36 | 2000
New Tongi | 101 | 1700 | BSRM | 85 | 200 | Panchagar | 28 | 1900
Korda | 74 | 1930 | Goalpara | 13 | 2000
Tangail | 138 | 1930 | Central s/s | 87 | 1900
Mymensing | 141 | 1930 | Noapara | 75 | 2200
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB |  |  |  | Page 4 of 7

## L.curve
Date | 2017-03-29 | [8 empty] | QF-LDC-11
TIME | E-W INT. | EAST GRID | WEST GRID | TOTAL |  | Demand | Hour
0:00 | -680 | 5884 | 1666 | 7550 | -680 | 7550 | 0:00 | DAILY LOAD CURVE | 2017-03-29
0:30 | -620 | 5680.5 | 1657 | 7337.5 | -560 | 7337.5 | 1:00
1:00 | -560 | 5477 | 1648 | 7125 | -520 | 7125 | 2:00
1:30 | -540 | 5318 | 1612.5 | 6930.5 | -440 | 6930.5 | 3:00
2:00 | -520 | 5159 | 1577 | 6736 | -400 | 6736 | 4:00
2:30 | -480 | 5059.5 | 1558.5 | 6618 | -400 | 6618 | 5:00
3:00 | -440 | 4960 | 1540 | 6500 | -380 | 6500 | 6:00
3:30 | -420 | 4907 | 1496.5 | 6403.5 | -380 | 6403.5 | 7:00
4:00 | -400 | 4854 | 1453 | 6307 | -280 | 6307 | 8:00
4:30 | -400 | 4790.5 | 1461.5 | 6252 | -220 | 6252 | 9:00
5:00 | -400 | 4727 | 1470 | 6197 | -190 | 6197 | 10:00
5:30 | -390 | 4718 | 1453 | 6171 | -230 | 6171 | 11:00
6:00 | -380 | 4709 | 1436 | 6145 | -240 | 6145 | 12:00
6:30 | -380 | 4640.5 | 1438 | 6078.5 | -320 | 6078.5 | 13:00
7:00 | -380 | 4572 | 1440 | 6012 | -320 | 6012 | 14:00 |  |  |  | 8099 | 19:30
7:30 | -330 | 4474.5 | 1441 | 5915.5 | -300 | 5915.5 | 15:00 |  |  |  | 6650 | 12:00
8:00 | -280 | 4377 | 1442 | 5819 | -360 | 5819 | 16:00
8:30 | -250 | 4541.5 | 1473 | 6014.5 | -280 | 6014.5 | 17:00
9:00 | -220 | 4706 | 1504 | 6210 | -200 | 6210 | 18:00
9:30 | -205 | 4790.5 | 1501.5 | 6292 | -340 | 6292 | 18:30
10:00 | -190 | 4875 | 1499 | 6374 | -580 | 6374 | 19:00
10:30 | -210 | 4942 | 1519 | 6461 | -580 | 6461 | 19:30
11:00 | -230 | 5009 | 1539 | 6548 | -560 | 6548 | 20:00
11:30 | -235 | 5066 | 1533 | 6599 | -580 | 6599 | 21:00
12:00 | -240 | 5123 | 1527 | 6650 | -540 | 6650 | 22:00
12:30 | -280 | 5131 | 1544 | 6675 | -520 | 6675 | 23:00
13:00 | -320 | 5139 | 1561 | 6700 | -520 | 6700 | 24:00
13:30 | -320 | 5217.5 | 1545 | 6762.5 |  | 6762.5
14:00 | -320 | 5296 | 1529 | 6825 | 128.92 | 6825
14:30 | -310 | 5197 | 1545.5 | 6742.5 | 86.5 | 6742.5
15:00 | -300 | 5098 | 1562 | 6660 |  | 6660
15:30 | -330 | 5098 | 1555 | 6653 | 7867500 | 6653
16:00 | -360 | 5098 | 1548 | 6646 |  | 6646
16:30 | -320 | 4995.5 | 1557.5 | 6553 |  | 6553
17:00 | -280 | 4893 | 1567 | 6460 | 700 | 6460
17:30 | -280 | 4995 | 1671.5 | 6666.5 | 1800 | 6666.5
18:00 | -280 | 5097 | 1776 | 6873 | 100 | 6873
18:30 | -340 | 5481.5 | 1932.5 | 7414 | 1400 | 7414
19:00 | -580 | 5866 | 2089 | 7955 | 100 | 7955
19:30 | -580 | 6010 | 2089 | 8099 | 1800 | 8099
20:00 | -560 | 5939 | 2088 | 8027 | 1800 | 8027
20:30 | -570 | 5879 | 2085 | 7964 | 1800 | 7964
21:00 | -580 | 5819 | 2082 | 7901 | 2100 | 7901
21:30 | -560 | 5829.5 | 2083 | 7912.5 | 1900 | 7912.5
22:00 | -540 | 5840 | 2084 | 7924 | 1900 | 7924
22:30 | -530 | 5766.5 | 2015 | 7781.5 |  | 7781.5
23:00 | -520 | 5693 | 1946 | 7639 |  | 7639
23:30 | -520 | 5614 | 1884 | 7498 |  | 7498
24:00 | -520 | 5535 | 1822 | 7357 |  | 7357
*MAX.GEN.(E.P.) |  | 8099 |  | 19:30
*MAX.GEN.(D.P.) |  | 6650 |  | 12:00
|  |  |  | min | max
|  | 3063.9 | 3349 | 8:00 | 1:00
|  | 2664.1 | 3286.1 | 13:00 | 11:00
|  | 2910.2 | 3139.4 | 18:30 | 24:00
|  | 2664.1 | 3349 | 13:00 | 1:00
|  | 282 |  | 4:00
|  | 276 |  | 18:00
|  | 348 |  | 21:00
|  | 348 |  | 21:00
| Deputy Manager |  |  | Manager |  |  | Deputy General Manager
| Load Despatch Division |  |  | Load Despatch Division |  |  | Load Despatch Circle
NATIONAL LOAD DESPATCH CENTER
3595 MW (09:00 )
4008 MW(05:00 )
.4MW (19:30)
8099 MW (19:30)
6650 MW (12:00)

## En.Curve
QF-LDC-12
Date | 2017-03-29 |  | Energy | 164802550 | 0
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | Tripura |  | DAILY ENERGY CURVE |  | 2017-03-29
0:00 | 1125 | 491 | 3406 | 1273 | 153 | 115 | 290 | 0 | 90
0:30 | 1113 | 491.5 | 3432 | 1077 | 153 | 97.5 | 288 | 0 | 87
1:00 | 1101 | 492 | 3458 | 881 | 153 | 80 | 286 | 0 | 84
1:30 | 1090 | 492 | 3402.5 | 809 | 153 | 80 | 244 | 0 | 83 | [5 empty] | 164.8025
2:00 | 1079 | 492 | 3347 | 737 | 153 | 80 | 202 | 0 | 82 | [5 empty] | 0
2:30 | 1086.5 | 492 | 3303 | 690 | 153 | 80 | 177.5 | 0 | 81 | [5 empty] | 164.8025
3:00 | 1094 | 492 | 3259 | 643 | 153 | 80 | 153 | 0 | 80
3:30 | 1093.5 | 491.5 | 3227.5 | 600.5 | 153 | 80 | 133.5 | 0 | 74
4:00 | 1093 | 491 | 3196 | 558 | 153 | 80 | 114 | 0 | 68
4:30 | 1095.5 | 491.5 | 3169.5 | 561.5 | 152.5 | 80 | 85 | 0 | 69
5:00 | 1098 | 492 | 3143 | 565 | 152 | 80 | 56 | 0 | 70
5:30 | 1101.5 | 492 | 3139 | 532 | 154 | 83.5 | 56 | 0 | 68
6:00 | 1105 | 492 | 3135 | 499 | 156 | 87 | 56 | 0 | 66
6:30 | 1080.5 | 491.5 | 3076.5 | 542.5 | 156 | 86 | 50 | 0 | 63
7:00 | 1056 | 491 | 3018 | 586 | 156 | 85 | 44 | 0 | 60
7:30 | 1042 | 491 | 2899.5 | 633 | 154.5 | 72.5 | 44 | 0 | 61
8:00 | 1028 | 491 | 2781 | 680 | 153 | 60 | 44 | 0 | 62
8:30 | 1043 | 492 | 2842.5 | 766.5 | 154.5 | 72.5 | 44 | 0 | 62
9:00 | 1058 | 493 | 2904 | 853 | 156 | 85 | 44 | 0 | 62
9:30 | 1045 | 492.5 | 2987.5 | 930 | 150.5 | 75 | 30 | 0 | 67
10:00 | 1032 | 492 | 3071 | 1007 | 145 | 65 | 16 | 0 | 72
10:30 | 1051 | 492 | 3115 | 1025 | 144.5 | 75 | 16 | 0 | 73
11:00 | 1070 | 492 | 3159 | 1043 | 144 | 85 | 16 | 0 | 74
11:30 | 1067.5 | 492 | 3212 | 1036 | 146 | 85 | 21 | 0 | 74
12:00 | 1065 | 492 | 3265 | 1029 | 148 | 85 | 26 | 0 | 74
12:30 | 1069 | 492.5 | 3247 | 1066 | 150.5 | 70 | 29.5 | 0 | 75
13:00 | 1073 | 493 | 3229 | 1103 | 153 | 55 | 33 | 0 | 76
13:30 | 1038 | 493 | 3210.5 | 1062 | 154 | 70 | 32.5 | 0 | 77
14:00 | 1003 | 493 | 3192 | 1021 | 155 | 85 | 32 | 0 | 78
14:30 | 1015 | 493 | 3265.5 | 1039.5 | 157.5 | 75 | 32 | 0 | 77
15:00 | 1027 | 493 | 3339 | 1058 | 160 | 65 | 32 | 0 | 76
15:30 | 1009 | 493 | 3302 | 1039 | 161 | 65.5 | 32 | 0 | 77
16:00 | 991 | 493 | 3265 | 1020 | 162 | 66 | 32 | 0 | 78
16:30 | 1002 | 493 | 3175.5 | 1048.5 | 162.5 | 71 | 32 | 0 | 75
17:00 | 1013 | 493 | 3086 | 1077 | 163 | 76 | 32 | 0 | 72
17:30 | 996.5 | 494.5 | 3088 | 1179.5 | 160.5 | 100 | 141 | 0 | 73 | Max Temp. in Dhaka |  | MMCFD
18:00 | 980 | 496 | 3090 | 1282 | 158 | 124 | 250 | 0 | 74
18:30 | 981.5 | 496.5 | 3188 | 1551.5 | 159 | 116 | 377.5 | 0 | 92
19:00 | 983 | 497 | 3286 | 1821 | 160 | 108 | 505 | 0 | 90
19:30 | 1093 | 497 | 3255 | 1887 | 161 | 109 | 506 | 0 | 92
20:00 | 1096 | 497 | 3242 | 1830 | 159 | 104 | 459 | 0 | 92
20:30 | 1143.5 | 494 | 3297 | 1700.5 | 160 | 114.5 | 446.5 | 0 | 92
21:00 | 1191 | 491 | 3352 | 1571 | 161 | 125 | 434 | 0 | 92
21:30 | 1166.5 | 490.5 | 3428 | 1524 | 160.5 | 125.5 | 427.5 | 0 | 91
22:00 | 1142 | 490 | 3504 | 1477 | 160 | 126 | 421 | 0 | 90
22:30 | 1157 | 490.5 | 3494.5 | 1376 | 159 | 126 | 396 | 0 | 87
23:00 | 1172 | 491 | 3485 | 1275 | 158 | 126 | 371 | 0 | 84
23:30 | 1159.5 | 491 | 3479 | 1206 | 158.5 | 105.5 | 331 | 0 | 81
24:00 | 1147 | 491 | 3473 | 1137 | 159 | 85 | 291 | 0 | 78
|  | 1490 |  |  |  |  | 2380 | 0
|  | Deputy / Asstt. Manager |  |  | Manager
|  | Load Despatch Division |  |  | Load Despatch Division
NATIONAL LOAD DESPATCH CENTER
Tripura

## volt
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS.
Date: | 2017-03-29
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 230 | 1:00 | 222 | 14:00 | Tongi | 218 | 4:00 | 208 | 10:00
Ishurdi | 235 | 18:00 | 224 | 21:00 | Comilla (N) | 229 | 4:00 | 218 | 12:00
Ashuganj | 235 | 1:00 | 230 | 16:00 | Hathazari | 215 | 13:00 | 201 | 17:00
Serajganj | 225 | 3:00 | 216 | 20:00 | Megnaghat | 220 | 1:00 | 214 | 14:00
Baghabari | 222 | 4:00 | 217 | 21:00 | Fenchuganj | 237 | 23:00 | 233 | 12:00
Barapukuria | 228 | 5:00 | 219 | 20:00 | Siddhirganj | 229 | 19:00 | 211 | 12:00
Bogra | 224 | 6:00 | 212 | 20:00 | Maniknagar | 227 | 19:00 | 209 | 12:00
Khulna South | 236 | 18:00 | 223 | 20:00 | Old Airport | 215 | 4:00 | 205 | 14:00
Rampura | 219 | 4:00 | 211 | 11:00 | Barisal | 236 | 6:00 | 231 | 14:00
Haripur | 216 | 1:00 | 210 | 15:00 | AKSML | 216 | 22:00 | 201 | 14:00
Hasnabad | 216 | 1:00 | 209 | 12:00 | BSRM | 216 | 1:00 | 205 | 17:00
Aminbazar | 217 | 4:00 | 209 | 12:00 | Bibiyana | 0 | 1:00 | 0 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 137 | 1830 | 127 | 1100 | Madanhat | 131 | 100 | 124 | 1200
Munsiganj | 136 | 1900 | 128 | 1100 | Hathazari | 130 | 2200 | 121 | 1700
Megnaghat | 133 | 1800 | 125 | 1100 | Khulshi | 126 | 2200 | 117 | 1700
Shyampur | 129 | 1830 | 120 | 1100 | Halishahar | 128 | 200 | 121 | 1500
Bhulta | 125 | 1930 | 118 | 1100 | Baraulia | 126 | 1300 | 118 | 1700
Madanganj | 134 | 1930 | 125 | 500 | Sikalbaha | 129 | 600 | 122 | 1100
Shitalakhya | 136 | 2000 | 124 | 1200 | Dohazari | 129 | 700 | 120 | 1700
Rahim steal | 135 | 1900 | 129 | 900 | Cox'sbazar | 126 | 2200 | 117 | 1100
Matuail | 135 | 1900 | 125 | 1200 | Chandraghona | 130 | 700 | 120 | 1700
Ghorasal | 137 | 1800 | 135 | 1300 | Kaptai | 130 | 100 | 125 | 1200
Narsinghdi | 132 | 1900 | 124 | 1200 | A. Khaer Stl. | 126 | 100 | 122 | 1100
Haripur (SBU) | 135 | 1830 | 126 | 1300 | Bakulia | 126 | 200 | 118 | 1700
Ullon | 132 | 700 | 124 | 1200 | Julda | 129 | 400 | 122 | 1100
Hasnabad | 134 | 300 | 126 | 1100 | TK Chemical | 130 | 100 | 122 | 1700
Magbazar | 132 | 500 | 124 | 1100 | Modern Steel | 126 | 2400 | 118 | 1700
Maniknagar | 136 | 1900 | 124 | 1200 | Shahmirpur | 127 | 300 | 121 | 1700
Bangabhaban | 130 | 500 | 124 | 1500 | Goalpara | 138 | 1800 | 132 | 2000
Narinda | 133 | 500 | 124 | 1500 | Central s/s | 138 | 1700 | 133 | 2000
Dhanmondi | 132 | 500 | 124 | 1100 | Noapara | 135 | 1800 | 129 | 2000
Lalbag | 130 | 500 | 122 | 1500 | Jessore | 128 | 1800 | 121 | 2000
Madartek | 133 | 500 | 123 | 1500 | Jhenida | 128 | 1800 | 120 | 2000
Mirpur | 131 | 300 | 123 | 1200 | Bottail | 133 | 300 | 122 | 1930
Kalyanpur | 132 | 300 | 127 | 1200 | G.K.Project | 136 | 700 | 131 | 1100
Gulshan | 133 | 400 | 124 | 1200 | Faridpur | 135 | 1800 | 127 | 100
Uttara | 133 | 300 | 122 | 1000 | Madaripur | 134 | 1900 | 125 | 1600
Kamrangirchar | 132 | 400 | 124 | 1100 | Gopalganj | 140 | 1800 | 125 | 1600
Savar | 129 | 500 | 124 | 1100 | Bagerhat | 136 | 600 | 130 | 2000
Bhasantec | 131 | 500 | 124 | 1100 | Mongla | 135 | 1800 | 128 | 1930
Agargaon | 132 | 500 | 125 | 1200 | Satkhira | 134 | 300 | 127 | 1930
Satmosjid | 131 | 400 | 125 | 1200 | Gallamari | 139 | 1800 | 133 | 2000
Tongi | 132 | 400 | 124 | 1000 | Magura | 130 | 1800 | 112 | 2000
Kabirpur | 131 | 1930 | 126 | 1600 | Chuadanga | 126 | 600 | 111 | 2000
Basundhara | 128 | 300 | 121 | 1300 | Barisal | 138 | 1800 | 132 | 2100
Manikganj | 134 | 600 | 129 | 1400 | Patuakhali | 138 | 1800 | 132 | 2100
Joydevpur | 135 | 1930 | 128 | 1600 | Bhandaria | 135 | 600 | 130 | 100
New Tongi | 131 | 700 | 124 | 1100 | Ishurdi | 135 | 700 | 126 | 2000
Kodda | 135 | 700 | 126 | 1600 | Natore | 131 | 1800 | 125 | 2000
Tangail | 133 | 700 | 126 | 1000 | Bogra | 135 | 800 | 124 | 2000
Mymensing | 138 | 400 | 130 | 2100 | Noagaon | 131 | 800 | 121 | 2000
Kishorganj | 139 | 800 | 132 | 2100 | Rajshahi | 132 | 700 | 123 | 1500
Netrokona | 142 | 800 | 130 | 2100 | C.Nawabganj | 130 | 1800 | 122 | 2000
Jamalpur | 138 | 900 | 130 | 2100 | Amnura | 134 | 1800 | 125 | 1300
Sherpur | 139 | 800 | 129 | 2100 | Pabna | 130 | 300 | 123 | 2000
Srimongal | 141 | 400 | 140 | 900 | Shahjadpur | 136 | 1800 | 131 | 2000
Shahjibazar | 141 | 1500 | 140 | 100 | Serajganj | 132 | 300 | 125 | 1900
Fenchuganj | 138 | 700 | 136 | 900 | Niyamatpur | 129 | 300 | 117 | 2000
Khulawara | 137 | 100 | 136 | 900 | Joypurhat | 134 | 500 | 121 | 2000
Sylhet | 137 | 100 | 135 | 1200 | Rangpur | 128 | 500 | 115 | 2000
Chatak | 137 | 700 | 135 | 1000 | Lalmonirhat | 124 | 300 | 110 | 2000
Comilla(s) | 133 | 400 | 128 | 900 | Saidpur | 127 | 400 | 112 | 2000
Comilla(n) | 135 | 1930 | 129 | 1200 | Purbasadipur | 128 | 300 | 115 | 2000
Chandpur | 125 | 1700 | 123 | 2200 | Thakurgaon | 124 | 700 | 110 | 1900
Feni | 122 | 800 | 116 | 1700 | Palashbari | 130 | 400 | 117 | 2000
Chowmuhani | 128 | 800 | 120 | 2000 | Barapukuria | 128 | 500 | 119 | 2000
Ashuganj | 141 | 100 | 140 | 2100 | Panchagar | 120 | 600 | 108 | 1900
Daudkandi | 134 | 1900 | 127 | 1100
B.Baria | 141 | 1830 | 138 | 1400
Page 7 of 7