## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-01-06 | Thursday
|  | Date (day): | 2022-01-06 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11581.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12473 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-01-05 | 2022-01-06 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 220 | 320 | 320 | 320 | 45 |  | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 191 | 162 | 200 | 250 | 110 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 180 | 180 | 180 | 180 | 270 |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 3 | 12 | 11 | 11 |  | 89 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  | 3 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 82 | 102 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 44 | 44
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | Engine problem
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 82 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 |  | 20 | Engine problem
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 25 | 25 | 35 | 35 |  | 45 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 20 | 20 | 20 | 20 |  | 13 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 51 | 51 | 51 | 51
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 260 | 278 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 300 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 70 | 149 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 90 | 105 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 95 | 104 | 104
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 126 | 162 | 162 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 20 | 0 | 30 | 0
| Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 55 | 0 | 0 | 55 | 55 | 55 | 55
| Dhaka area Total |  |  |  |  | 6178 | 5560 | 1689 | 2030 | 2699 | 2769 | 1640 | 1214
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 120 | 100 | 100 |  | 80 | Gas shortage
41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 8 | 17 | 25 | 25
42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 45 | 46 | 50 | 50
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 86 | 86 | 86 |  | 144 | Low Water Level & Unit 4 & 5 U/M.
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 34 | 105 | 105 | 105
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 70 |  | 32 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 0 | 100 | 100
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 90 | 90 | 90 |  | 10 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 21 | 20 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 17 | 5 | 15
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 79 | 90 | 90 | 90 |  | 18 | Engine problem
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 30 | 100 | 300 | 300
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 54 | 54 | 54
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 81 | 110 | 110 | 110
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 70 | 100 | 100 | 100
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 73 | 116 | 116 | 116 |  | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 643 | 1123 | 1427 | 1432 | 0 | 937
60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 130 | 100 | 100 | 100 | 34 |  | Gas shortage
61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 0 | 0 | 0 |  |  | Umder maint
62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 265 | 270 | 270 | 270 | 90 |  | ST S/D due to gas shortage.
63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 300 | 350 | 350 |  |  | FGMO
64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 30 | 30 | 15 |  | Gas shortage
65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 55 | 54 | 55 | 55
66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 185 | 73 | 65 | 65 | 130 |  | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 128 | 148 | 150 | 150
69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 50 | 50
70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 136 | 129 | 135 | 135 |  | 28 | Machine problem.
71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 17 | 200 | 200
72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 21 | 22 | 22
73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 91 | 100 | 138 | 163
74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 17 | 25 | 33 | 33
75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 52 | 52
76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 9 | 9 | 9 | 9
77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 50 | 113 | 113 | 113
80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 0 | 17 | 17 |  | 37 | 33 kV feeder fault
| Chandpur 115(Doreen) |  | HFO | IPP | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1500 | 1502 | 1965 | 2190 | 533 | 65
81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 33 | 50 | 100 | 100 | 102 |  | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 22 | 22
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 150 | 184 | 200 | 200
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 45 | 104 | 115 | 115
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 0 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 19 | 22 | 22 | 22
| Mymensingh Area Total |  |  |  |  | 717 | 622 | 265 | 377 | 510.6 | 459 | 102 | 8
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 42 | 42 | 42 |  | 28 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Under maintenance
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 51 | 50 | 51 | 51
| Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 72 | 34 | 72 | 72
96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 81 | 81 | 81
97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 190 | 185 | 190 | 190 |  | 41
99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 21 | 24 | 24 | 24
101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 275 | 330 | 330 |  | 341
102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint
103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 320 | 400 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1218 | 1293 | 1392 | 1392 | 0 | 1330
105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 672 | 720 | 676 | 724
106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 25 | 0 | 30 |  | 24 | Engine problem
108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 70 | 105 | 105 | 105
113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 0 | 100
| Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 0 | 0 | 77 | 0 | 11 | 0
| Khulna Area Total |  |  |  |  | 2248 | 2129 | 819 | 850 | 842 | 1319 | 410 | 93
114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 13 | 21 | 24 | 24 |  | 9 | Engine problem
116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 92 | 91 | 91 | 91 | 103 |  | Gas shortage
117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 11 | 11 | 11 | 84 |  | Gas shortage
118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 300 | 400 | 620 | 620
119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 150 | 206 | 200 | 220
120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 150
| Barisal Area Total |  |  |  |  | 2046 | 2046 | 566 | 729 | 1056 | 1226 | 187 | 9
121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 50 | 50
123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 |  | 41 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 25 | 25 |  | 25 | Engine problem
125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 34 | 43 | 43 |  |  | Engine problem
126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 32 | 32 | 32 | 32 |  | 18 | Engine problem
127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 117 | 165 | 200 | 200 |  |  | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 354 | 360 | 400 | 400 |  |  | FGMO
131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 0 |  | 50 | Under maint from (5-1-22 to 9-1-22)
132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 34 | 34 | 34 | 34
136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 100 | 90 | 100
137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 70 | 113 | 113 | 113
139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 95 | 113 | 113 | 113
140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
| Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 769 | 1024 | 1369 | 1373 | 600 | 134
141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 199 | 200 | 200 | 74 |  | Coal shortage
143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 83 | 112 | 113 | 113
146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
| Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 0 | 0 | 0 | 0 | 0 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 287 | 311 | 321 | 313 | 74 | 210
| Total |  |  |  |  | 22031 | 20934 | 7756 | 9239 | 11581.6 | 12473 | 3546 | 4000
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7387.4662 | 8800 | 11031.2891 | 11880.3334
A. |  | 2022-01-05 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 9239 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5648 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9239 | MW
3 | Day peak Generation : |  |  | 7756 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8800 | MW
4 | Evening peak Generation : |  |  | 9239 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 180.7502 | MKWHr | By Solar | 0.82648 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 95.0107 | MKWHr |  | By Oil: | 52.1763 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 13.6467 | MKWHr |  | By Hydro: | 1.9988 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3546 | MW | Dhaka | 3152 | 3152 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 4000 | MW | Chittagong | 958 | 958 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 7546 | MW | Khulna | 1069 | 1069 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 759.7 | MMCFD |  |  | Rajshahi | 906 | 906 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 95459721.53 | ii) Oil : | Taka | 356262846.58 | Comilla | 742 | 742 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : |  | 64916461 | Total | Taka | 516639029.11 | Mymensingh | 760 | 760 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.147 | MKWHr. | Sylhet | 334 | 334 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -72 | MW (E to W) at | 19:00 | hrs | Barisal | 249 | 249 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -136 | MW at | 18:30 | hrs | Rangpur | 630 | 630 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 23.8° C |  |  | Total | 8800 | 8800 |  | 0
B. |  | 2022-01-06 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 25.6° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12473 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8200 | MW
4 | Reserve(Generation end) |  |  |  | 2973 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 185.8564 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5805 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 15.1185 | MKWHr. | ii) HVDC Flow at Peak Time |  | 720 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9728 | MKWHr. | iii) Maximum HVDC Flow : |  | 720 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 97.72 |  | (b) Today: | 97.6 |  | (c) Rule Curve: |  | 102.05
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-01-05
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 185 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 9 | 16 | 33 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 79 | 46 | 20 | 38 | 0 | 0 | 80 | 150 | 265 | 208 | 8 | 127 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 9 | 72 | 97 | 0 | 22 | 0 | 42 | 0 | 51 | 0 | 130 | 0 | 70 | 79 | 0 | 190 | 18 | 0 | 10 | 30 | 21 | 11 | 0 | 95 | 0 | 0 | 150 | 0 | 0 | 0 | 90 | 0 | 147 | 0 | 0 | 50 | 17 | 0 | 0 | 54 | 110 | 0 | 17 | 50 | 401 | 53 | 0 | 126 | 116 | 0 | 17 | 0 | 0 | 0 |  | 484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 161 | 0 | 364 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 70 | 360 | 220 | 0 | 0 | 0 | 0 | 0 |  | 4520 | 2183 | 6703 | 2484 | 484 | 1401 | 0 | 1616 | 560 | 86 | 0 | 0 | 72 | 0 | 0 | 97.74
2:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 185 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 9 | 16 | 33 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 80 | 46 | 20 | 38 | 0 | 0 | 80 | 150 | 270 | 213 | 8 | 124 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 9 | 72 | 97 | 0 | 22 | 0 | 42 | 0 | 51 | 0 | 130 | 0 | 69 | 79 | 0 | 190 | 18 | 0 | 10 | 35 | 21 | 5 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 90 | 0 | 143 | 0 | 0 | 50 | 17 | 0 | 0 | 54 | 68 | 0 | 17 | 10 | 400 | 17 | 0 | 72 | 116 | 0 | 17 | 0 | 0 | 0 |  | 484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 168 | 0 | 364 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 70 | 320 | 220 | 0 | 0 | 0 | 0 | 0 |  | 4214 | 2114 | 6328 | 2490 | 484 | 1405 | 0 | 1271 | 520 | 86 | 0 | 0 | 72 | 0 | 0 | 97.74
3:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 179 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 9 | 16 | 33 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 82 | 41 | 20 | 38 | 0 | 0 | 80 | 150 | 265 | 215 | 8 | 124 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 9 | 72 | 97 | 0 | 22 | 0 | 42 | 0 | 51 | 0 | 130 | 0 | 70 | 79 | 0 | 190 | 18 | 0 | 10 | 60 | 21 | 5 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 60 | 0 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 34 | 0 | 17 | 0 | 400 | 10 | 0 | 17 | 116 | 0 | 17 | 0 | 0 | 0 |  | 484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 157 | 0 | 375 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 35 | 300 | 220 | 0 | 0 | 0 | 0 | 0 |  | 3970 | 2057 | 6027 | 2477 | 484 | 1434 | 0 | 975 | 499 | 86 | 0 | 0 | 72 | 0 | 0 | 97.73
4:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 183 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 35 | 19 | 25 | 9 | 16 | 33 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 76 | 46 | 20 | 38 | 0 | 0 | 80 | 150 | 263 | 220 | 8 | 129 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 9 | 70 | 100 | 0 | 22 | 0 | 42 | 0 | 51 | 0 | 130 | 0 | 69 | 79 | 0 | 190 | 18 | 0 | 10 | 100 | 21 | 5 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 60 | 0 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 17 | 0 | 400 | 0 | 0 | 17 | 69 | 0 | 17 | 0 | 0 | 0 |  | 484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 154 | 0 | 360 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 35 | 290 | 220 | 0 | 0 | 0 | 0 | 0 |  | 3883 | 1958 | 5841 | 2484 | 484 | 1463 | 0 | 765 | 489 | 86 | 0 | 0 | 70 | 0 | 0 | 97.73
5:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 194 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 25 | 9 | 16 | 33 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 77 | 46 | 20 | 40 | 0 | 0 | 80 | 0 | 265 | 227 | 8 | 132 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 9 | 72 | 101 | 0 | 22 | 0 | 42 | 0 | 51 | 0 | 100 | 0 | 70 | 79 | 0 | 190 | 18 | 0 | 10 | 160 | 21 | 5 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 30 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 17 | 0 | 360 | 0 | 0 | 17 | 69 | 0 | 17 | 0 | 0 | 0 |  | 484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 156 | 0 | 373 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 290 | 220 | 0 | 0 | 0 | 0 | 0 |  | 3711 | 1937 | 5648 | 2310 | 484 | 1518 | 0 | 689 | 489 | 86 | 0 | 0 | 72 | 0 | 0 | 97.72
6:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 193 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 25 | 9 | 16 | 33 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 77 | 46 | 20 | 38 | 0 | 0 | 100 | 0 | 295 | 228 | 8 | 128 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 9 | 76 | 103 | 0 | 22 | 0 | 42 | 0 | 51 | 0 | 100 | 0 | 71 | 78 | 0 | 190 | 18 | 0 | 10 | 250 | 21 | 5 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 60 | 0 | 142 | 0 | 2 | 0 | 8 | 0 | 30 | 54 | 24 | 0 | 28 | 20 | 400 | 0 | 0 | 17 | 70 | 0 | 17 | 0 | 0 | 0 |  | 484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 147 | 0 | 379 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 10 | 310 | 220 | 0 | 0 | 0 | 0 | 0 |  | 4004 | 1968 | 5972 | 2391 | 484 | 1610 | 0 | 816 | 509 | 86 | 0 | 0 | 76 | 0 | 0 | 97.72
7:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 193 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 9 | 16 | 33 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 77 | 46 | 20 | 36 | 0 | 0 | 130 | 0 | 295 | 182 | 36 | 135 | 5 | 20 | 0 | 51 | 0 | 0 | 8 | 18 | 11 | 33 | 9 | 70 | 94 | 0 | 22 | 0 | 42 | 0 | 48 | 0 | 130 | 0 | 40 | 79 | 0 | 190 | 18 | 0 | 10 | 285 | 21 | 5 | 0 | 25 | 0 | 0 | 65 | 0 | 0 | 1 | 60 | 0 | 143 | 0 | 8 | 10 | 34 | 0 | 80 | 54 | 51 | 0 | 45 | 40 | 400 | 14 | 0 | 100 | 111 | 0 | 17 | 0 | 0 | 0 |  | 566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 142 | 0 | 292 | 0 | 0 | 29 | 0 | 90 | 0 | 0 | 35 | 270 | 180 | 0 | 0 | 0 | 0 | 0 |  | 4459 | 1983 | 6442 | 2334 | 566 | 1586 | 0 | 1330 | 469 | 86 | 0 | 0 | 70 | 1 | 0 | 97.71
8:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 194 |  | 0 | 180 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 0 | 16 | 33 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 77 | 47 | 20 | 12 | 0 | 0 | 130 | 0 | 355 | 182 | 65 | 135 | 23 | 20 | 0 | 51 | 0 | 0 | 8 | 18 | 11 | 33 | 9 | 73 | 71 | 0 | 22 | 0 | 42 | 0 | 45 | 0 | 130 | 0 | 72 | 79 | 0 | 190 | 18 | 0 | 10 | 325 | 21 | 5 | 0 | 69 | 0 | 0 | 84 | 0 | 5 | 7 | 90 | 0 | 135 | 0 | 32 | 50 | 34 | 1 | 50 | 54 | 51 | 0 | 16 | 40 | 400 | 35 | 0 | 124 | 116 | 0 | 17 | 2 | 0 | 0 |  | 671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 136 | 0 | 340 | 0 | 0 | 35 | 0 | 100 | 0 | 1 | 35 | 300 | 150 | 0 | 0 | 0 | 17 | 0 |  | 4754 | 2165 | 6919 | 2406 | 671 | 1648 | 0 | 1508 | 499 | 86 | 0 | 0 | 73 | 28 | 0 | 97.71
9:00 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 190 |  | 0 | 180 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 0 | 16 | 33 | 18 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 79 | 46 | 20 | 5 | 0 | 0 | 130 | 0 | 305 | 0 | 120 | 135 | 26 | 35 | 0 | 51 | 0 | 0 | 8 | 18 | 11 | 22 | 9 | 74 | 71 | 0 | 20 | 0 | 42 | 0 | 45 | 0 | 163 | 0 | 73 | 78 | 0 | 190 | 18 | 0 | 10 | 341 | 21 | 5 | 0 | 188 | 0 | 0 | 127 | 0 | 18 | 13 | 90 | 0 | 137 | 0 | 42 | 105 | 34 | 2 | 30 | 54 | 72 | 0 | 34 | 90 | 370 | 59 | 0 | 162 | 116 | 0 | 17 | 6 | 0 | 10 |  | 671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 128 | 0 | 373 | 24 | 0 | 52 | 0 | 105 | 0 | 1 | 100 | 330 | 150 | 0 | 0 | 0 | 45 | 0 |  | 4982 | 2359 | 7341 | 2077 | 671 | 1787 | 0 | 2049 | 530 | 86 | 0 | 0 | 74 | 67 | 0 | 97.7
10:00 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 192 |  | 0 | 180 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 0 | 20 | 33 | 51 | 0 | 46 | 40 | 0 | 0 | 7 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 77 | 46 | 18 | 5 | 0 | 0 | 130 | 0 | 300 | 0 | 187 | 134 | 29 | 51 | 0 | 51 | 0 | 0 | 8 | 18 | 11 | 22 | 5 | 73 | 69 | 0 | 20 | 0 | 43 | 0 | 45 | 0 | 110 | 0 | 57 | 78 | 0 | 171 | 18 | 0 | 10 | 270 | 21 | 5 | 0 | 223 | 0 | 0 | 150 | 0 | 57 | 17 | 90 | 0 | 140 | 0 | 45 | 105 | 34 | 4 | 30 | 54 | 110 | 0 | 45 | 35 | 341 | 104 | 0 | 162 | 68 | 0 | 17 | 7 | 0 | 46 |  | 672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 9 | 34 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 119 | 0 | 261 | 65 | 0 | 109 | 0 | 112 | 0 | 2 | 113 | 300 | 150 | 0 | 0 | 0 | 62 | 0 |  | 5065 | 2387 | 7452 | 1978 | 672 | 1635 | 0 | 2407 | 500 | 86 | 0 | 9 | 73 | 92 | 0 | 97.7
11:00 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 192 |  | 0 | 180 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 0 | 20 | 33 | 51 | 0 | 46 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 77 | 45 | 18 | 3 | 0 | 0 | 130 | 270 | 305 | 0 | 185 | 135 | 29 | 55 | 0 | 51 | 0 | 0 | 8 | 18 | 11 | 21 | 5 | 83 | 33 | 0 | 20 | 1 | 43 | 0 | 48 | 0 | 110 | 0 | 40 | 78 | 0 | 191 | 18 | 0 | 10 | 280 | 21 | 5 | 0 | 255 | 0 | 0 | 150 | 0 | 71 | 19 | 90 | 0 | 138 | 0 | 45 | 90 | 34 | 4 | 30 | 35 | 100 | 0 | 45 | 35 | 320 | 104 | 0 | 126 | 68 | 0 | 17 | 10 | 0 | 29 |  | 671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 32 | 34 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 117 | 0 | 299 | 70 | 0 | 70 | 0 | 70 | 0 | 3 | 70 | 290 | 150 | 0 | 0 | 2 | 73 | 0 |  | 5232 | 2329 | 7561 | 2167 | 671 | 1685 | 0 | 2235 | 490 | 86 | 0 | 32 | 83 | 112 | 0 | 97.69
12:00 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 191 |  | 0 | 180 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 82 | 0 | 3 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 0 | 20 | 33 | 51 | 0 | 0 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 10 | 79 | 45 | 18 | 5 | 0 | 0 | 130 | 265 | 300 | 0 | 185 | 136 | 29 | 55 | 0 | 51 | 0 | 0 | 8 | 18 | 11 | 17 | 9 | 91 | 33 | 0 | 17 | 1 | 43 | 0 | 51 | 0 | 110 | 0 | 72 | 78 | 0 | 190 | 18 | 0 | 10 | 300 | 21 | 5 | 0 | 260 | 0 | 0 | 150 | 0 | 70 | 20 | 90 | 0 | 128 | 0 | 45 | 90 | 34 | 5 | 30 | 35 | 81 | 0 | 50 | 70 | 320 | 104 | 0 | 126 | 73 | 0 | 17 | 20 | 0 | 55 |  | 672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 32 | 34 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 117 | 0 | 354 | 70 | 0 | 70 | 0 | 83 | 0 | 4 | 95 | 300 | 150 | 0 | 0 | 3 | 77 | 0 |  | 5315 | 2441 | 7756 | 2186 | 672 | 1766 | 0 | 2339 | 500 | 40 | 0 | 32 | 91 | 130 | 0 | 97.69
13:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 190 |  | 0 | 180 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 102 | 0 | 11 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 0 | 20 | 33 | 25 | 0 | 46 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 10 | 84 | 46 | 18 | 2 | 0 | 0 | 80 | 250 | 280 | 0 | 73 | 138 | 29 | 55 | 0 | 51 | 0 | 0 | 25 | 21 | 11 | 17 | 9 | 97 | 33 | 0 | 17 | 2 | 43 | 0 | 51 | 0 | 110 | 0 | 40 | 78 | 0 | 190 | 18 | 0 | 10 | 280 | 21 | 5 | 0 | 270 | 0 | 0 | 150 | 0 | 59 | 19 | 90 | 11 | 133 | 0 | 45 | 70 | 65 | 3 | 65 | 54 | 110 | 0 | 84 | 70 | 318 | 104 | 0 | 148 | 99 | 0 | 17 | 29 | 0 | 55 |  | 671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 15 | 0 | 0 | 0 | 0 | 0 | 14 | 50 | 0 | 8 | 32 | 34 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 137 | 0 | 296 | 105 | 0 | 102 | 0 | 112 | 0 | 3 | 113 | 290 | 150 | 0 | 0 | 3 | 77 | 0 |  | 5450 | 2543 | 7993 | 2190 | 671 | 1574 | 0 | 2653 | 490 | 86 | 0 | 96 | 97 | 136 | 0 | 97.68
14:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 189 |  | 0 | 180 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 102 | 0 | 11 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 0 | 20 | 33 | 25 | 0 | 46 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 84 | 45 | 21 | 8 | 0 | 0 | 130 | 220 | 270 | 0 | 73 | 137 | 29 | 54 | 0 | 51 | 0 | 0 | 25 | 0 | 0 | 17 | 9 | 98 | 33 | 0 | 17 | 2 | 43 | 0 | 50 | 0 | 110 | 0 | 40 | 78 | 0 | 165 | 18 | 0 | 10 | 290 | 21 | 5 | 0 | 263 | 0 | 0 | 150 | 0 | 17 | 17 | 50 | 17 | 142 | 0 | 45 | 70 | 34 | 3 | 65 | 54 | 68 | 0 | 85 | 30 | 320 | 55 | 0 | 162 | 114 | 0 | 17 | 26 | 0 | 55 |  | 671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 13 | 0 | 0 | 0 | 0 | 0 | 15 | 50 | 0 | 8 | 32 | 34 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 165 | 0 | 324 | 70 | 0 | 35 | 0 | 70 | 0 | 3 | 70 | 300 | 150 | 0 | 0 | 3 | 63 | 0 |  | 5226 | 2408 | 7634 | 2177 | 671 | 1613 | 0 | 2276 | 499 | 86 | 0 | 97 | 98 | 117 | 0 | 97.68
15:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 182 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 74 | 0 | 12 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 0 | 20 | 33 | 25 | 0 | 46 | 40 | 0 | 34 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 84 | 45 | 21 | 4 | 0 | 0 | 80 | 220 | 270 | 0 | 73 | 136 | 29 | 55 | 0 | 51 | 0 | 0 | 25 | 10 | 0 | 16 | 9 | 97 | 32 | 0 | 17 | 1 | 43 | 0 | 51 | 0 | 110 | 0 | 40 | 79 | 0 | 190 | 18 | 0 | 10 | 295 | 21 | 5 | 0 | 273 | 0 | 0 | 150 | 0 | 17 | 13 | 50 | 17 | 135 | 0 | 24 | 70 | 34 | 2 | 65 | 54 | 68 | 0 | 85 | 30 | 320 | 54 | 0 | 162 | 116 | 0 | 17 | 19 | 0 | 55 |  | 672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 12 | 0 | 0 | 0 | 0 | 0 | 20 | 50 | 0 | 8 | 32 | 34 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 162 | 0 | 332 | 17 | 0 | 35 | 0 | 72 | 0 | 2 | 35 | 300 | 150 | 0 | 0 | 2 | 47 | 0 |  | 5187 | 2313 | 7500 | 2189 | 672 | 1617 | 0 | 2152 | 499 | 86 | 0 | 102 | 97 | 86 | 0 | 97.67
16:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 172 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 74 | 0 | 12 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 0 | 20 | 33 | 25 | 0 | 46 | 40 | 0 | 100 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 84 | 40 | 21 | 4 | 0 | 0 | 80 | 180 | 265 | 0 | 73 | 136 | 29 | 53 | 0 | 15 | 0 | 0 | 25 | 21 | 0 | 32 | 9 | 95 | 49 | 0 | 17 | 0 | 43 | 0 | 50 | 0 | 110 | 0 | 40 | 78 | 0 | 165 | 18 | 0 | 10 | 285 | 21 | 5 | 0 | 280 | 0 | 0 | 120 | 0 | 17 | 7 | 50 | 17 | 135 | 0 | 24 | 70 | 34 | 1 | 30 | 39 | 68 | 0 | 85 | 30 | 322 | 54 | 0 | 126 | 116 | 0 | 17 | 9 | 0 | 55 |  | 672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 91 | 11 | 0 | 0 | 0 | 0 | 0 | 22 | 50 | 0 | 8 | 32 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 192 | 0 | 301 | 17 | 0 | 35 | 0 | 35 | 0 | 1 | 35 | 300 | 150 | 0 | 0 | 0 | 24 | 0 |  | 5035 | 2245 | 7280 | 2261 | 672 | 1525 | 0 | 1992 | 499 | 86 | 0 | 108 | 95 | 42 | 0 | 97.67
17:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 162 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 48 | 11 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 0 | 20 | 33 | 25 | 0 | 46 | 40 | 0 | 120 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 84 | 37 | 21 | 6 | 0 | 0 | 80 | 180 | 265 | 0 | 73 | 129 | 29 | 55 | 0 | 15 | 0 | 0 | 30 | 21 | 0 | 32 | 9 | 87 | 50 | 0 | 17 | 0 | 43 | 0 | 23 | 0 | 110 | 0 | 25 | 78 | 0 | 165 | 18 | 0 | 10 | 290 | 21 | 5 | 0 | 278 | 0 | 0 | 132 | 0 | 23 | 1 | 20 | 17 | 140 | 0 | 24 | 80 | 39 | 0 | 50 | 54 | 77 | 0 | 89 | 60 | 305 | 54 | 0 | 132 | 116 | 0 | 0 | 2 | 0 | 55 |  | 672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 85 | 12 | 0 | 0 | 0 | 0 | 35 | 26 | 75 | 0 | 8 | 32 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 188 | 0 | 282 | 17 | 0 | 40 | 0 | 72 | 0 | 0 | 70 | 300 | 150 | 0 | 0 | 0 | 4 | 0 |  | 5119 | 2343 | 7462 | 2233 | 672 | 1479 | 0 | 2173 | 499 | 86 | 0 | 226 | 87 | 7 | 0 | 97.66
18:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 162 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 100 | 11 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 0 | 20 | 33 | 36 | 0 | 46 | 40 | 0 | 120 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 10 | 87 | 45 | 21 | 10 | 0 | 0 | 80 | 200 | 300 | 0 | 73 | 129 | 29 | 55 | 0 | 35 | 0 | 50 | 52 | 21 | 0 | 30 | 9 | 106 | 49 | 0 | 17 | 0 | 43 | 0 | 44 | 0 | 163 | 0 | 34 | 80 | 0 | 185 | 18 | 0 | 10 | 275 | 24 | 11 | 0 | 273 | 11 | 0 | 187 | 0 | 85 | 0 | 90 | 17 | 138 | 0 | 46 | 105 | 84 | 0 | 130 | 54 | 110 | 0 | 113 | 100 | 400 | 68 | 0 | 162 | 116 | 0 | 0 | 0 | 0 | 55 |  | 719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 91 | 18 | 0 | 0 | 0 | 0 | 43 | 29 | 100 | 0 | 34 | 32 | 30 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 4 | 160 | 0 | 333 | 68 | 0 | 94 | 0 | 112 | 0 | 0 | 113 | 300 | 220 | 0 | 0 | 0 | 0 | 0 |  | 6114 | 2747 | 8861 | 2396 | 719 | 1691 | 15 | 2937 | 499 | 86 | 0 | 412 | 106 | 0 | 0 | 97.66
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 162 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 82 | 12 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 0 | 20 | 33 | 51 | 0 | 46 | 40 | 0 | 120 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 0 | 90 | 46 | 21 | 17 | 0 | 0 | 100 | 270 | 300 | 0 | 73 | 129 | 29 | 54 | 0 | 51 | 0 | 0 | 52 | 21 | 11 | 25 | 9 | 100 | 50 | 0 | 17 | 0 | 42 | 0 | 50 | 0 | 163 | 0 | 34 | 81 | 0 | 185 | 18 | 0 | 10 | 275 | 24 | 11 | 0 | 278 | 0 | 0 | 184 | 0 | 149 | 0 | 90 | 17 | 148 | 0 | 104 | 105 | 105 | 0 | 100 | 54 | 110 | 0 | 113 | 100 | 400 | 95 | 0 | 162 | 116 | 0 | 0 | 0 | 0 | 55 |  | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 91 | 21 | 0 | 0 | 0 | 0 | 43 | 0 | 100 | 0 | 34 | 32 | 34 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 165 | 0 | 360 | 105 | 0 | 113 | 0 | 112 | 0 | 0 | 113 | 400 | 206 | 0 | 0 | 0 | 0 | 0 |  | 6325 | 2914 | 9239 | 2497 | 720 | 1736 | 0 | 3168 | 599 | 86 | 0 | 333 | 100 | 0 | 0 | 97.64
19:30 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 162 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 82 | 11 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 0 | 20 | 33 | 51 | 0 | 46 | 40 | 0 | 100 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 0 | 90 | 46 | 21 | 17 | 0 | 0 | 85 | 245 | 280 | 0 | 73 | 132 | 29 | 55 | 0 | 51 | 0 | 0 | 25 | 21 | 11 | 25 | 9 | 98 | 50 | 0 | 17 | 0 | 42 | 0 | 50 | 0 | 163 | 0 | 34 | 81 | 0 | 190 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 278 | 0 | 0 | 175 | 0 | 149 | 0 | 90 | 0 | 148 | 0 | 104 | 105 | 68 | 0 | 65 | 54 | 110 | 0 | 85 | 70 | 400 | 104 | 0 | 162 | 116 | 0 | 0 | 0 | 0 | 55 |  | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 91 | 21 | 0 | 0 | 0 | 0 | 43 | 0 | 100 | 0 | 34 | 0 | 34 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 163 | 0 | 409 | 105 | 0 | 113 | 0 | 112 | 0 | 0 | 113 | 420 | 220 | 0 | 0 | 0 | 0 | 0 |  | 6092 | 2969 | 9061 | 2423 | 720 | 1815 | 0 | 2993 | 619 | 86 | 0 | 307 | 98 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 162 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 82 | 11 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 0 | 20 | 33 | 51 | 0 | 46 | 40 | 0 | 100 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 0 | 90 | 46 | 21 | 20 | 0 | 0 | 80 | 240 | 280 | 0 | 16 | 132 | 29 | 55 | 0 | 51 | 0 | 0 | 25 | 21 | 11 | 30 | 9 | 100 | 51 | 0 | 17 | 0 | 42 | 0 | 51 | 0 | 163 | 0 | 34 | 81 | 0 | 190 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 278 | 0 | 0 | 175 | 0 | 149 | 0 | 90 | 0 | 148 | 0 | 104 | 105 | 68 | 0 | 65 | 54 | 110 | 0 | 85 | 70 | 400 | 104 | 0 | 162 | 116 | 0 | 4 | 0 | 0 | 55 |  | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 91 | 21 | 0 | 0 | 0 | 0 | 43 | 0 | 100 | 0 | 34 | 0 | 34 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 164 | 0 | 382 | 105 | 0 | 113 | 0 | 112 | 0 | 0 | 113 | 440 | 220 | 0 | 0 | 0 | 0 | 0 |  | 6031 | 2959 | 8990 | 2420 | 720 | 1725 | 0 | 2997 | 640 | 86 | 0 | 302 | 100 | 0 | 0 | 97.65
21:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 163 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 64 | 11 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 9 | 20 | 33 | 51 | 0 | 46 | 40 | 0 | 100 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 0 | 90 | 46 | 21 | 23 | 0 | 0 | 80 | 240 | 280 | 0 | 16 | 129 | 29 | 56 | 0 | 51 | 0 | 0 | 25 | 21 | 11 | 33 | 9 | 97 | 51 | 0 | 17 | 0 | 42 | 0 | 51 | 0 | 130 | 0 | 34 | 81 | 0 | 190 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 278 | 0 | 0 | 185 | 0 | 149 | 0 | 90 | 0 | 150 | 0 | 104 | 105 | 68 | 0 | 65 | 54 | 110 | 0 | 85 | 70 | 400 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 90 | 23 | 0 | 0 | 0 | 0 | 43 | 0 | 100 | 0 | 34 | 0 | 34 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 194 | 0 | 291 | 105 | 0 | 113 | 0 | 112 | 0 | 0 | 113 | 440 | 210 | 0 | 0 | 0 | 0 | 0 |  | 6016 | 2889 | 8905 | 2458 | 720 | 1598 | 0 | 3022 | 640 | 86 | 0 | 284 | 97 | 0 | 0 | 97.64
22:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 155 |  | 0 | 180 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 84 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 9 | 20 | 33 | 25 | 0 | 46 | 40 | 0 | 100 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 90 | 46 | 21 | 30 | 0 | 0 | 80 | 240 | 270 | 0 | 16 | 131 | 29 | 55 | 0 | 51 | 0 | 0 | 25 | 21 | 11 | 33 | 9 | 92 | 51 | 0 | 20 | 0 | 42 | 0 | 51 | 0 | 130 | 0 | 34 | 81 | 0 | 190 | 18 | 0 | 10 | 260 | 24 | 11 | 0 | 275 | 0 | 0 | 184 | 0 | 116 | 0 | 90 | 0 | 148 | 0 | 104 | 105 | 68 | 0 | 30 | 54 | 110 | 0 | 85 | 10 | 400 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 92 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 220 | 0 | 306 | 70 | 0 | 70 | 0 | 111 | 0 | 0 | 113 | 420 | 220 | 0 | 0 | 0 | 0 | 0 |  | 5654 | 2708 | 8362 | 2481 | 720 | 1601 | 0 | 2678 | 620 | 86 | 0 | 84 | 92 | 0 | 0 | 97.64
23:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 149 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 9 | 16 | 33 | 0 | 0 | 46 | 40 | 0 | 100 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 91 | 46 | 21 | 38 | 0 | 0 | 80 | 240 | 265 | 0 | 16 | 126 | 29 | 56 | 0 | 51 | 0 | 0 | 25 | 21 | 11 | 33 | 9 | 81 | 50 | 0 | 20 | 0 | 42 | 0 | 51 | 0 | 130 | 0 | 72 | 81 | 0 | 190 | 18 | 0 | 9 | 270 | 24 | 11 | 0 | 255 | 0 | 0 | 184 | 0 | 76 | 0 | 90 | 0 | 150 | 0 | 35 | 105 | 17 | 0 | 0 | 54 | 110 | 0 | 85 | 10 | 400 | 43 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 710 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 91 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 220 | 0 | 305 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 380 | 220 | 0 | 0 | 0 | 0 | 0 |  | 5279 | 2333 | 7612 | 2503 | 710 | 1609 | 0 | 2037 | 580 | 86 | 0 | 6 | 81 | 0 | 0 | 97.63
24:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 157 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 9 | 16 | 33 | 0 | 0 | 46 | 40 | 0 | 100 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 91 | 46 | 21 | 38 | 0 | 0 | 80 | 240 | 265 | 0 | 16 | 128 | 29 | 55 | 0 | 51 | 0 | 0 | 25 | 21 | 11 | 33 | 9 | 81 | 50 | 0 | 20 | 0 | 42 | 0 | 51 | 0 | 130 | 0 | 71 | 81 | 0 | 190 | 18 | 0 | 10 | 270 | 22 | 11 | 0 | 261 | 0 | 0 | 193 | 0 | 28 | 0 | 50 | 0 | 138 | 0 | 8 | 105 | 17 | 0 | 0 | 54 | 34 | 0 | 36 | 0 | 400 | 0 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 91 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 220 | 0 | 326 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 350 | 220 | 0 | 0 | 0 | 0 | 0 |  | 4979 | 2144 | 7123 | 2502 | 527 | 1635 | 0 | 1736 | 550 | 86 | 0 | 6 | 81 | 0 | 0 | 97.63
KWH | 0 | 0 | 0 | 0 | 7315627 | 0 | 0 | 0 | 4302000 |  | 0 | 4180750 | 0 | 0 | 0 | 577295 | 0 | 0 | 0 | 0 | 1355328 | 362880 | 115485 | 0 | 0 | 0 | 845280 | 1239328 | 809698 | 442656 | 600000 | 108000 | 586600 | 821200 | 519840 | 0 | 1030800 | 968000 | 0 | 1000000 | 126223 | 0 | 0 | 0 | 0 |  | 532080 | 0 | 211116 | 58680 | 2001600 | 1085280 | 478080 | 48570 | 0 | 0 | 2254050 | 3845000 | 6982000 | 1832000 | 1421818 | 3166880 | 494928 | 939840 | 0 | 1187520 | 0 | 56032 | 486302 | 455760 | 203400 | 670600 | 233080 | 1972800 | 1522560 | 0 | 438660 | 7600 | 1009000 | 0 | 1147800 | 0 | 3306354 | 0 | 1261152 | 1879680 | 0 | 4375030 | 423000 | 0 | 251820 | 5968500 | 533664 | 163584 | 0 | 4491271 | 11060 | 0 | 3247200 | 0 | 1156608 | 133515 | 1737600 | 118560 | 3385600 | 0 | 996000 | 1738800 | 957636 | 25439 | 1106509 | 1295999 | 2009773 | 0 | 1576680 | 1007040 | 8903500 | 1441920 | 0 | 3067200 | 2565545 | 0 | 388800 | 126337 | 0 | 819000 |  | 15118545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99840 | 0 | 0 | 2214885 | 370300 | 0 | 0 | 0 | 0 | 187378 | 120349 | 694664 | 0 | 273609 | 259379 | 810278 | 0 | 520560 | 0 | 181530 | 0 | 0 | 4861600 | 0 | 0 | 0 | 0 | 0 | 0 | 272930 | 9600 | 4128800 | 0 | 8077600 | 1056960 | 0 | 1460832 | 0 | 2045164 | 0 | 30247 | 1656960 | 8785100 | 4489391 | 0 | 0 | 18780 | 484560 | 0 |  | 122520402 | 58229841 | 180750243 | 56645226 | 15118545 | 38365433 | 20660 | 50163963 | 13646700 | 1998800 | 0 | 1991638 | 1972800 | 826478 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 8120345.97 | 0 | 0 | 0 | 4431060 |  | 0 | 4557017.5 | 0 | 0 | 0 | 4883915.7 | 0 | 0 | 0 | 0 | 12360591.36 | 3570739.2 | 1064771.7 | 0 | 0 | 0 | 6170544 | 9580005.44 | 7983622.28 | 331992 | 450000 | 0 | 0 | 0 | 5026852.8 | 0 | 278316 | 261360 | 0 | 1810000 | 1172611.67 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2047825.2 | 560394 | 17413920 | 8595417.6 | 602380.8 | 144252.9 | 0 | 0 | 3313453.5 | 2845300 | 6982000 | 1685440 | 1834145.22 | 3641912 | 559268.64 | 1315776 | 0 | 2030659.2 | 0 | 565923.2 | 4644184.1 | 578815.2 | 152550 | 1173550 | 174810 | 14796000 | 1613913.6 | 0 | 557098.2 | 121144 | 1654760 | 0 | 2043084 | 0 | 3769243.56 | 0 | 2484469.44 | 3590188.8 | 0 | 7568801.9 | 926370 | 0 | 513712.8 | 6028185 | 400248 | 124323.84 | 0 | 33954008.76 | 187798.8 | 0 | 16885440 | 0 | 11381022.72 | 1560790.35 | 14161440 | 1286376 | 23868480 | 0 | 9083520 | 16431660 | 8341009.56 | 0 | 8365208.04 | 11288151.29 | 17665904.67 | 0 | 13512147.6 | 6706886.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 87082819.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1047321.6 | 0 | 0 | 2502820.05 | 573965 | 0 | 0 | 0 | 0 | 1843799.52 | 1222745.84 | 6147776.4 | 0 | 3699193.68 | 2513382.51 | 7851593.82 | 0 | 999475.2 | 0 | 137418.21 | 0 | 0 | 26349872 | 0 | 0 | 0 | 0 | 0 | 0 | 409395 | 163296 | 4830696 | 0 | 7996824 | 11034662.4 | 0 | 13863295.68 | 0 | 15870472.64 | 0 | 334229.35 | 12244934.4 | 38566589 | 0 | 0 | 0 | 0 | 0 | 0 |  | 373787110.51 | 247286577.5 | 621073688.01 | 55222737.35 | 87082819.2 | 40236984.18 | 351094.8 | 336952238.31 | 64916461 | 539676 | 0 | 18959513.47 | 14796000 | 2016163.7 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 191 |  | 0 | 180 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 82 | 0 | 3 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 0 | 20 | 33 | 51 | 0 | 0 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 10 | 79 | 45 | 18 | 5 | 0 | 0 | 130 | 265 | 300 | 0 | 185 | 136 | 29 | 55 | 0 | 51 | 0 | 0 | 8 | 18 | 11 | 17 | 9 | 91 | 33 | 0 | 17 | 1 | 43 | 0 | 51 | 0 | 110 | 0 | 72 | 78 | 0 | 190 | 18 | 0 | 10 | 300 | 21 | 5 | 0 | 260 | 0 | 0 | 150 | 0 | 70 | 20 | 90 | 0 | 128 | 0 | 45 | 90 | 34 | 5 | 30 | 35 | 81 | 0 | 50 | 70 | 320 | 104 | 0 | 126 | 73 | 0 | 17 | 20 | 0 | 55 |  | 672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 32 | 34 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 117 | 0 | 354 | 70 | 0 | 70 | 0 | 83 | 0 | 4 | 95 | 300 | 150 | 0 | 0 | 3 | 77 | 0 |  | 7756 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 162 | 0 | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 82 | 12 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 0 | 20 | 33 | 51 | 0 | 46 | 40 | 0 | 120 | 17 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 51 | 0 | 90 | 46 | 21 | 17 | 0 | 0 | 100 | 270 | 300 | 0 | 73 | 129 | 29 | 54 | 0 | 51 | 0 | 0 | 52 | 21 | 11 | 25 | 9 | 100 | 50 | 0 | 17 | 0 | 42 | 0 | 50 | 0 | 163 | 0 | 34 | 81 | 0 | 185 | 18 | 0 | 10 | 275 | 24 | 11 | 0 | 278 | 0 | 0 | 184 | 0 | 149 | 0 | 90 | 17 | 148 | 0 | 104 | 105 | 105 | 0 | 100 | 54 | 110 | 0 | 113 | 100 | 400 | 95 | 0 | 162 | 116 | 0 | 0 | 0 | 0 | 55 |  | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 91 | 21 | 0 | 0 | 0 | 0 | 43 | 0 | 100 | 0 | 34 | 32 | 34 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 165 | 0 | 360 | 105 | 0 | 113 | 0 | 112 | 0 | 0 | 113 | 400 | 206 | 0 | 0 | 0 | 0 | 0 |  | 9239 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 149 | 11 | 0 | 0 | 44 | 35 | 55 | 35 | 19 | 25 | 10 | 20 | 33 | 51 | 0 | 46 | 40 | 0 | 100 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 70 | 100 | 90 | 50 | 21 | 15 | 0 | 0 | 100 | 270 | 350 | 0 | 65 | 135 | 30 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 9 | 163 | 100 | 0 | 22 | 0 | 42 | 0 | 51 | 0 | 163 | 0 | 72 | 81 | 0 | 190 | 18 | 0 | 10 | 330 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 150 | 0 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 17 |  |  | 55 |  | 724 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 30 | 40 | 0 | 91 | 24 | 110 | 0 | 0 | 0 | 50 | 30 | 100 | 25 | 43 | 32 | 34 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 100 | 200 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 149 | 11 | 0 | 0 | 44 | 35 | 55 | 35 | 19 | 25 | 10 | 20 | 33 | 51 | 0 | 46 | 40 | 0 | 100 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 90 | 50 | 20 | 5 | 0 | 0 | 100 | 270 | 350 | 0 | 65 | 135 | 30 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 9 | 138 | 100 | 0 | 22 | 1.6 | 42 | 0 | 51 | 0 | 163 | 0 | 72 | 81 | 0 | 190 | 18 | 0 | 10 | 330 | 24 | 11 | 0 | 300 | 300 | 100 | 200 | 50 | 149 | 20 | 90 | 200 | 150 | 0 | 115 | 105 | 105 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 50 | 162 | 116 | 0 | 17 | 30 |  | 55 |  | 676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 24 | 110 | 0 | 0 | 0 | 50 | 30 | 90 | 25 | 43 | 32 | 34 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 50 | 200 | 0 | 400 | 105 | 0 | 113 | 0 | 113 | 0 | 8 | 113 | 620 | 200 |  | 0 | 6 | 11
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 170 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 9 | 20 | 0 | 0 | 0 | 46 | 40 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 85 | 47 | 21 | 13 | 0 | 0 | 80 | 275 | 300 | 0 | 16 | 127 | 29 | 55 | 0 | 51 | 0 | 0 | 8 | 16 | 8 | 25 | 9 | 71 | 52 | 0 | 20 | 0 | 42 | 0 | 51 | 0 | 130 | 0 | 72 | 78 | 0 | 190 | 18 | 0 | 10 | 310 | 21 | 5 | 0 | 173 | 0 | 0 | 180 | 0 | 38 | 3 | 90 | 0 | 130 | 0 | 19 | 90 | 20 | 1 | 15 | 36 | 97 | 0 | 52 | 80 | 370 | 27 | 0 | 162 | 116 | 0 | 17 | 4 | 0 | 0 | 0 | 663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 91 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 175 | 0 | 405 | 31 | 0 | 70 | 0 | 112 | 0 | 1 | 80 | 0 | 190 | 0 | 0 | 0 | 11 | 0 | 0
199
| Minimum Generation |  | 5648 | 5:00
| Highest Generation |  | 9239 | 19:00
| Day Peak Generation |  | 7756 | 12:00
| Evening Peak Generation |  | 9239 | 19:00
| HVDC Max Flow |  | 720 | 19:00
| HVDC EvPeak Flow |  | 720 | 19:00
| Load factor L.F |  | 81.52%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-01-06
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2022-01-05 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7756 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5805 | MW
Evening Peak Generation : |  | 9239 | MW Hour : | 19:00 | Available Max Generation : |  | 12473 | MW
E.P. Demand (at gen end) : |  | 9239 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9500 | MW
Maximum Generation : |  | 9239 | MW Hour : | 19:00 | Reserve(Generation end) |  | 2973 | MW
Total Gen. (MKWH) : |  | 180.7502 | System Load Factor : | 81.52% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -136 | MW at | 18:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-01-06
Actual : | 97.6 | Ft.(MSL) , | Rule curve : | 102.05 | Ft.( MSL )
Gas Consumed : | Total = | 759.7 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 95459721.53
: |  | Coal : | 64916461 | Oil : | 356262846.58 | Total : | 516639029.11
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3376.9694 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1144.2169 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1024.4428 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 925.4086 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 836.4228 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 674.9531 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 382.7276 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 173.9233 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 520.5319 |  |  | 0 | 0%
Total | 0 |  | 9059.5963 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 10) Meghnaghat Summit 305 MW CCPP
2) Ghorasal-3,5
3) Ashuganj-3,4,
4) Baghabari-71 MW & 100 MW
5) Shajibazar 330 MW
6) Raozan unit-1
7) Sirajganj Unit 1 & 2
8) Summit Bibiyana-3
9) Haripur 412 MW EGCB
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Bagerhat-Orion Rupsha P/P 132 kV Ckt was under shut down from 08:29 to 16:34 for A/M.
b) Agrabad 132/33 kV T-1 transformer was under shut down from 12:28 to 20:00 for A/M.
c) Bakulia-Khulshi 132 kV Ckt-1 was under shut down from 08:32 to 15:04 for A/M.
d) Barisal(N)-Bhola 230 kV Ckt-2 was under shut down from 09:10 to 17:23 for A/M.
e) Barishal(N) 132/33 kV T-4 transformer was under shut down from 09:44 to 17:35 for D/W.
f) Hathazari-Kaptai 132 kV Ckt-1 was under shut down from 09:17 to 15:47 for A/M.
g) Cumilla(N)-Ashuganj 230 kV Ckt-1 was under shut down from 08:58 to 22:42 for A/M.
h) Bheramara-Kustia 132 kV Ckt-2 was under shut down from 08:48 to 15:52 for A/M.
i) Gopalganj(N) - Madaripur 132 kV Ckt-3 was under shut down from 08:15 to 16:15 for A/M.
j) Kaliakoir 400/132 kV T01 transformer was under shut down from 09:27 to 10:44 for protection test.
k) Kaliakoir 400/132 kV T02 transformer was under shut down from 10:46 to 12:39 for protection test.
l) Kodda 132/33 kV T-5 transformer was switched on at 11:03.
m) Mirpur 132/33 kV T-1 transformer was shut down at 12:18 for C/M.
n) Madaripur 132 kV Bus-B was under shut down from 12:20 to 16:50 for C/M.
o) Mymensing-Jamalpur 132 kV Ckt-1 was under shut down from 09:30 to 13:40 for A/M.
p) Tongi-Tongi(N) 132 kV Ckt-1 was under shut down from 09:11 to 10:33 for D/W.
q) Bhangura 132/33 kV T1 transformer was under shut down from 12:27 to 13:30 for D/W.
r) Ashuganj 225 MW CCPP tripped at 08:36 showing flame monitoring trip.
s) Mymensing-Jamalpur 132 kV Ckt-2 was under shut down from 13:44 to 17:17 for A/M.
t) Raozan unit-2 was synchronized at 14:21.
u) Mymensing 132 kV Bus-A was under shut down from 09:45 to 17:24 for C/M.
v) Rajshahi 132/33 kV T2 & T3 transformer tripped at 22:51 showing O/C relay and were switched on at | [5 empty] | About 05 MW power interruption occurred under
01:56(06-01-2022), 23:16. | [5 empty] | Rajshahi S/S area from 22:51 to 23:16.
w) Haripur-Bhulta 230 MW Ckt-2 was switched on at 03:42(06-01-2022)
x) Haripur 230/132 T1 transformer was shut down at 07:04(06-01-2022) from A/M.
y) Payra unit1 was shut down at 07:19(06-01-2022).
z) Kallyanpur 132/33 T1 transformer was shut down at 07:44(06-01-2022) from A/M.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-01-05 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 320 | 7315627
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 162 | 4302000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 180 | 4180750 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 577295
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 12 | 115485 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 442656
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1355328
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 845280 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 82 | 362880 | High Voltage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1239328
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 809698 | 33 kV feeder problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 25 | 708000 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 20 | 586600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 821200
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 51 | 519840
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Machine problem
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 278 | 4491271 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 11060
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 1156608
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 1738800
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 95 | 1441920 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3067200
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 126337
| Kanchan Purbachal Power Generation Ltd. |  | IPP | 55 | 0 | 55 | 819000
| Dhaka area Total |  |  |  | 5560 | 2030 | 37034163
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 120 | 1000000 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 17 | 126223 | High Voltage
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 133515
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 46 | 1085280 | Engine problem
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 86 | 1998800 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 957636
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 211116 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 58680 | High Voltage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 1737600 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 478080
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 17 | 48570
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 90 | 2001600 | Engine problem
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25439
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 100 | 1106509 | High Voltage
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1295999
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2009773
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1007040
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 116 | 2565545
| Chattogram area Total |  |  |  | 2382 | 1123 | 17847405
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2254050 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 1832000 | #REF!
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 270 | 3845000 | Machine problem
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 6982000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 494928 | Gas shortage
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 54 | 939840
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 73 | 1421818 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1187520
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 148 | 3385600
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 56032 | High Voltage
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 129 | 3166880 | Engine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 17 | 118560 | High Voltage
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 455760
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 203400
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 100 | 1972800
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 670600
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 486302
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 9 | 233080 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | High Voltage
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 1576680
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 0 | 388800 | 33 kV feeder O/L
| Chandpur 115(Doreen) |  | IPP | 115 | 0 | 0 | 0 | On test
| Cumilla Area Total |  |  |  | 3034 | 1502 | 31671650
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 50 | 1522560 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 438660
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 7600
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 184 | 3247200 | Engine problem
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 104 | 996000 | Engine problem
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 0
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 532080
| Mymensingh Area Total |  |  |  | 622 | 377 | 6744100
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 42 | 1009000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3306354
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1147800
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 163584
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 34 | 1261152
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1879680
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 185 | 4375030 | Machine problem
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 423000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 533664
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 275 | 5968500 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 251820
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 8903500
| Sylhet Area Total |  |  |  | 2377 | 1293 | 29223084
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 720 | 15118545
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 25 | 99840
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 9600
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1056960
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Mongla Orion 100 MW Solar PP |  | IPP | 100 | 0 | 0 | 484560 | On test
| Khulna Area Total |  |  |  | 2129 | 850 | 16769505
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve.
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 21 | 370300 | Engine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 91 | 2214885 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 11 | 272930 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 400 | 8785100 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 206 | 4489391
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 729 | 16132606
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 187378
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 120349
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 273609 | Engine problem
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 259379 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 165 | 4128800 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 360 | 8077600 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 520560
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 181530
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 34 | 810278 | Engine problem
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 694664
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1460832
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1656960
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 18780
| Rajshahi Area Total |  |  |  | 2179 | 1024 | 18390719
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 199 | 4861600
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 112 | 2045164
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 30247
| Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 0 | 0 | 0 | On test
| Rangpur Area Total |  |  |  | 605 | 311 | 6937011
| Total |  |  |  | 20934 | 9239 | 180750243
| Eastern Grid Total |  |  |  | 13975 | 6325 | 122520402
| Western Grid Total |  |  |  | 6959 | 2914 | 58229841
| National Grid Total |  |  |  | 20934 | 9239 | 180750243
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-01-05
(a) ENTIRE EASTERN GRID : |  | 5946 | MW | (b) ENTIRE WESTERN GRID : |  | 2854 | MW
i) Dhaka area |  | 3152 | MW | i) Khulna area |  | 1069 | MW
ii) Chittagong area |  | 958 | MW | ii) Rajshahi area |  | 906 | MW
iii) Comilla area |  | 742 | MW | iii) Barisal area |  | 249 | MW
iv) Mymensingh area |  | 760 | MW | iv) Rangpur area |  | 630 | MW
v) Sylhet area |  | 334 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8800 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 100 | 12:00 | Tangail | 141 | 18:00 | Noapara | 37 | 18:30
Munsiganj | 59 | 21:00 | Mymensing | 162 | 18:00 | Jessore | 73 | 18:30
Sonargaon | 64 | 9:00 | Kishoreganj | 96 | 20:00 | Benapol | 38 | 18:30
Shyampur | 164 | 14:00 | Netrokona | 91 | 18:30 | Jhenida(Old) | 80 | 18:30
Bhulta | 153 | 10:00 | Jamalpur | 102 | 18:30 | Bottail | 88 | 18:30
Madanganj | 23 | 19:30 | Sherpur | 106 | 18:00 | G.K Project | 37 | 18:30
Shitalakhya | 86 | 10:00 | Srimongal | 33 | 18:30 | Faridpur | 100 | 21:00
Rahim steel | 19 | 16:00 | Shahjibazar | 76 | 19:30 | Rajbari | 38 | 18:00
Matuail | 45 | 15:00 | Fenchuganj | 27 | 19:30 | Madaripur | 62 | 20:00
Ghorasal | 60 | 10:00 | Kulawara | 28 | 18:00 | Sariatpur | 40 | 21:00
Narsingdi | 124 | 19:00 | Sylhet | 97 | 18:00 | Gopalganj | 67 | 18:30
Haripur (SBU) | 90 | 5:00 | Chatak | 13 | 18:00 | Bagerhat | 77 | 18:30
Sreenagar | 26 | 21:00 | Sunamganj | 30 | 19:00 | Mongla | 40 | 12:00
Ullon | 42 | 18:00 | Biani Bazar | 39 | 18:30 | Satkhira | 73 | 18:30
Hasnabad | 66 | 18:30 | Comilla (S) | 106 | 18:00 | Gallamari | 42 | 19:30
Magbazar | 63 | 12:00 | Comilla(N) | 82 | 18:00 | Magura | 40 | 18:00
Maniknagar | 41 | 13:00 | Chandpur | 48 | 19:30 | Norail | 36 | 18:30
Bangabhaban | 6 | 10:00 | Feni | 79 | 18:00 | Chuadanga | 66 | 18:30
Motijheel | 19 | 15:00 | Chowmuhani | 120 | 20:00 | Barisal(N) | 27 | 19:00
Narinda | 38 | 15:00 | Ashuganj | 29 | 19:30 | Barisal (S) | 76 | 19:00
Kazla | 70 | 18:30 | Daudkandi | 88 | 18:30 | Patuakhali | 77 | 21:00
Dhanmondi | 125 | 13:00 | B.Baria | 94 | 19:30 | Bhandaria | 38 | 21:00
Lalbag | 69 | 13:00 | Ramganj | 52 | 20:00 | Borguna | 12 | 19:00
Madartek | 39 | 20:00 | Chaddagram | 34 | 20:00 | Borhan Uddin | 28 | 21:00
Dhaka University | 20 | 14:00 | PHP | 7 | 13:00 | Ishurdi | 48 | 19:30
Aftabnagar | 10 | 13:00 | Kochua | 34 | 18:30 | Ruppur Paromanobik | 3 | 9:00
Fatullah | 50 | 12:00 | Madunaghat | 35 | 18:30 | Natore | 86 | 18:30
Nawabganj | 32 | 20:00 | Hathazari | 69 | 19:00 | Bogra | 97 | 19:30
Keraniganj | 32 | 18:00 | Khulshi | 136 | 12:00 | Noagaon | 77 | 19:30
Banani | 38 | 18:30 | Halishahar | 62 | 18:00 | Rajshahi | 100 | 19:30
Mirpur | 73 | 17:00 | Baraulia | 126 | 9:00 | Rajshahi New | 16 | 18:00
Kalyanpur | 63 | 18:00 | Sikalbaha | 23 | 18:30 | C.Nawabganj | 38 | 12:00
Gulshan | 70 | 1:00 | Dohazari | 64 | 18:00 | Amnura | 36 | 18:30
Uttara | 37 | 13:00 | Cox'sbazar | 62 | 22:00 | Pabna | 85 | 18:30
Uttara New | 21 | 13:00 | Chandraghona | 28 | 8:00 | Shahjadpur | 64 | 18:30
Kamrangirchar | 56 | 13:00 | Kaptai | 3.5 | 18:00 | Serajganj | 70 | 19:00
Savar | 100 | 16:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 51 | 18:30
Bhasantec | 76 | 13:00 | Bakulia | 85 | 18:30 | Joypurhat | 46 | 18:30
Agargaon | 48 | 13:00 | Julda | 21 | 10:00 | Sherpur(Bogura) | 46 | 18:00
Satmosjid | 73 | 14:00 | TK chemical | 21.6 | 19:30 | Mohastangor | 42 | 18:30
Old Tongi | 95 | 18:00 | Modern Steel | 0 | 1:00 | Bhangura | 16 | 18:00
Kabirpur | 167 | 18:00 | Shahmirpur | 30.7 | 5:00 | Rangpur | 100 | 18:30
Bashundara | 126 | 17:00 | Khagrachhari | 20 | 7:00 | Lalmonirhat | 29 | 18:30
Manikgong | 62 | 20:00 | Matarbari | 24 | 17:00 | Saidpur | 81 | 18:30
Joydevpur | 116 | 18:00 | Baroiar Hat | 42 | 17:00 | Purbasadipur | 89 | 18:30
New Tongi | 72 | 18:30 | Rangamati | 10 | 18:00 | Thakurgaon | 65 | 18:30
Kodda | 206 | 18:30 | Abul Khair 230 | 135 | 1:00 | Palashbari | 73 | 19:00
Dhamrai | 80 | 9:00 | BSRM | 156 | 12:00 | Barapukuria | 42 | 19:00
Rajendrapur | 80 | 18:30 | GPH Ispat | 14 | 11:00 | Panchagar | 46 | 18:00
Purbachal | 12 | 12:00 | Agrabad | 54 | 18:00 | Joldhaka | 41 | 18:30
Tongi Millgate | 32 | 10:00 | Goalpara | 20 | 12:00 | Kurigram | 48 | 18:00
Valuka | 80 | 18:00 | Central S/S | 56 | 18:30 | Mithapukur | 33 | 18:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-01-05 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 417 | 21:00 | 409 | 11:00 | Kaliakoir | 414 | 0.25 | 405 | 0.33333
| Bheramara | 409 | 1:00 | 394 | 18:00 | Bhulta | 408 | 0.875 | 391 | 0.33333
| Ashuganj(N) | 408 | 21:00 | 393 | 10:00 | Gopalganj | 418 | 0.625 | 406 | 0.8125
| Payra | 418 | 21:00 | 411 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 248 | 1:00 | 246 | 7:00 | Hathazari | 242 | 5:00 | 234 | 15:00
| Ishurdi | 246 | 1:00 | 238 | 18:30 | Megnaghat | 248 | 6:00 | 244 | 4:00
| Ashuganj | 252 | 11:00 | 245 | 8:00 | Fenchuganj | 247 | 20:00 | 243 | 15:00
| Serajganj | 243 | 1:00 | 238 | 8:00 | Siddhirganj | 241 | 22:00 | 236 | 10:00
| Baghabari | 244 | 17:00 | 238 | 7:00 | Maniknagar | 241 | 22:00 | 235 | 16:00
| Barapukuria | 238 | 1:00 | 231 | 18:30 | Agargaon | 244 | 4:00 | 237 | 15:00
| Bogra | 241 | 1:00 | 235 | 12:00 | Barisal | 247 | 17:00 | 239 | 19:00
| Rajshahi | 245 | 17:00 | 237 | 8:00 | Bhola 225 MW | 248 | 2:00 | 245 | 11:00
| Khulna South | 248 | 5:00 | 235 | 18:00 | AKSML | 246 | 17:00 | 234 | 11:00
| Rampura | 240 | 1:00 | 233 | 15:00 | BSRM | 244 | 1:00 | 235 | 15:00
| Haripur | 241 | 22:00 | 236 | 16:00 | Bibiyana | 249 | 21:00 | 239 | 11:00
| Hasnabad | 244 | 22:00 | 235 | 15:00 | Bhulta | 243 | 21:00 | 236 | 16:00
| Shyampur | 242 | 21:00 | 234 | 9:00 | Ashuganj (S) | 247 | 1:00 | 243 | 15:00
| Aminbazar | 245 | 1:00 | 238 | 2:00 | Kaliakoir | 244 | 23:00 | 235 | 16:00
| Tongi | 241 | 23:00 | 231 | 15:00 | GPH | 245 | 6:00 | 234 | 12:00
| Comilla (N) | 242 | 1:00 | 237 | 15:00 | Jhenaidah | 244 | 17:00 | 235 | 8:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 139 | 1:00 | 136 | 10:00 | Kachua | 143 | 0.875 | 140 | 0.20833
| Munsiganj | 142 | 1:00 | 138 | 4:00 | Madanhat | 143 | 0.083333 | 137 | 0.54167
| Sonargaon | 138 | 3:00 | 136 | 11:00 | Hathazari | 143 | 0.375 | 138 | 0.5
| Shyampur | 138 | 1:00 | 134 | 0:00 | Khulshi | 141 | 0.875 | 134 | 0.5
| Bhulta | 136 | 4:00 | 130 | 10:00 | Halishahar | 143 | 0.29167 | 135 | 0.66667
| Madanganj | 141 | 5:00 | 137 | 17:00 | Baraulia | 144 | 0.25 | 135 | 0.5
| Shitalakhya | 141 | 6:00 | 139 | 1:00 | Sikalbaha | 143 | 0.25 | 137 | 0.20833
| Rahim steal | 139 | 1:00 | 137 | 15:00 | Dohazari | 141 | 0.29167 | 134 | 0.45833
| Matuail | 139 | 1:00 | 136 | 10:00 | Cox'sbazar | 130 | 0.375 | 124 | 0.41667
| Ghorasal | 145 | 1:00 | 143 | 18:00 | Chandraghona | 144 | 0.25 | 137 | 0.66667
| Narsinghdi | 139 | 4:00 | 135 | 18:30 | Kaptai | 142 | 0.875 | 136 | 0.70833
| Haripur (SBU) | 139 | 1:00 | 137 | 9:00 | A. Khaer Stl. | 140 | 0.041667 | 133 | 0.45833
| Sreenagar | 139 | 3:00 | 134 | 18:30 | Bakulia | 143 | 0.875 | 135 | 0.5
| Ullon | 137 | 1:00 | 133 | 8:00 | Julda | 143 | 0.25 | 136 | 0.41667
| Hasnabad | 141 | 1:00 | 138 | 18:30 | TK Chemical | 144 | 0.25 | 134 | 0.5
| Magbazar | 138 | 1:00 | 134 | 15:00 | Modern Steel | 143 | 0.29167 | 135 | 0.58333
| Maniknagar | 142 | 1:00 | 138 | 10:00 | Shahmirpur | 142 | 0.25 | 135 | 0.45833
| Bangabhaban | 142 | 1:00 | 138 | 10:00 | Khagrachhari | 142 | 0.29167 | 136 | 0.45833
| Motijheel | 142 | 1:00 | 138 | 10:00 | Matarbari | 134 | 0.083333 | 123 | 0.45833
| Narinda | 142 | 1:00 | 138 | 10:00 | Baroiar Hat | 144 | 7:00 | 136 | 10:00
| Kazla | 142 | 1:00 | 138 | 10:00 | Rangamati | 143 | 6:00 | 136 | 12:00
| Dhanmondi | 140 | 1:00 | 136 | 8:00 | Agrabad | 143 | 6:00 | 136 | 0.5
| Lalbag | 138 | 1:00 | 134 | 18:00 | Goalpara S/S | 141 | 1:00 | 134 | 0.33333
| Madartek | 137 | 1:00 | 133 | 10:00 | Khulna Central S/S | 140 | 2:00 | 134 | 0.33333
| Dhaka University | 137 | 1:00 | 133 | 10:00 | Noapara | 141 | 1:00 | 134 | 0.33333
| Aftabnagar | 137 | 1:00 | 133 | 16:00 | Jessore | 138 | 0.041667 | 132 | 0.77083
| Fatullah | 139 | 1:00 | 135 | 0:00 | Benapol | 140 | 6:00 | 132 | 0.33333
| Nawabganj | 139 | 1:00 | 134 | 16:00 | Jhenida(Old) | 140 | 0.16667 | 134 | 0.33333
| Keraniganj | 137 | 1:00 | 134 | 3:00 | Bottail | 140 | 0.041667 | 134 | 0.77083
| Banani | 138 | 21:00 | 134 | 8:00 | G.K Project | 141 | 0.041667 | 136 | 0.33333
| Mirpur | 137 | 1:00 | 132 | 7:00 | Faridpur | 140 | 0.20833 | 135 | 0.8125
| Kalyanpur | 137 | 2:00 | 133 | 9:00 | Rajbari | 141 | 0.70833 | 135 | 0.8125
| Gulshan | 137 | 1:00 | 133 | 11:00 | Madaripur | 143 | 6:00 | 139 | 0.8125
| Uttara | 140 | 1:00 | 136 | 6:00 | Shariyatpur S/S | 144 | 0.29167 | 138 | 0.77083
| Uttara New | 136 | 1:00 | 131 | 15:00 | Gopalganj | 145 | 7:00 | 138 | 0.77083
| Kamrangirchar | 138 | 1:00 | 135 | 11:00 | Bagerhat | 141 | 2:00 | 130 | 0.29167
| Savar | 139 | 4:00 | 132 | 15:00 | Mongla | 140 | 5:00 | 131 | 12:00
| Bhasantec | 139 | 2:00 | 136 | 9:00 | Satkhira | 140 | 0.16667 | 131 | 8:00
| Agargaon | 141 | 1:00 | 136 | 15:00 | Gallamari | 141 | 9:00 | 135 | 0.8125
| Satmosjid | 140 | 1:00 | 136 | 11:00 | Magura | 142 | 0.041667 | 134 | 0.77083
| Old Tongi | 141 | 1:00 | 137 | 16:00 | Narail | 139 | 1:00 | 133 | 0.75
| Kabirpur | 138 | 1:00 | 133 | 12:00 | Chuadanga | 141 | 2:00 | 130 | 0.77083
| Bashundara | 140 | 17:00 | 135 | 15:00 | Barisal(N) | 146 | 4:00 | 139 | 19:00
| Manikgong | 136 | 1:00 | 130 | 8:00 | Barisal (S) | 144 | 0.083333 | 138 | 0.77083
| Joydevpur | 144 | 21:00 | 140 | 12:00 | Patuakhali(S) | 141 | 0.16667 | 136 | 0.77083
| New Tongi | 142 | 1:00 | 135 | 16:00 | Bhandaria | 143 | 0.16667 | 137 | 0.8125
| Kodda | 140 | 20:00 | 132 | 4.00 | Borguna | 144 | 1:00 | 138 | 19:30
| Dhamrai | 137 | 1:00 | 133 | 16:00 | Jhenaidah(New) | 140 | 1:00 | 134 | 18:30
| Rajendrapur | 138 | 21:00 | 131 | 6.00 | Ishurdi | 142 | 1:00 | 137 | 18:30
| Purbachal | 138 | 1:00 | 132 | 15:00 | Ruppur Paromanobik | 141 | 1:00 | 137 | 18:30
| Tongi Millgate | 140 | 1:00 | 136 | 8:00 | Natore | 143 | 1:00 | 138 | 12:00
| Valuka | 134 | 1:00 | 126 | 15:00 | Bogra | 143 | 1:00 | 139 | 12:00
| Tangail | 137 | 1:00 | 130 | 12:00 | Noagaon | 138 | 17:00 | 133 | 16:00
| Mymensing | 135 | 1:00 | 128 | 16:00 | Rajshahi | 141 | 17:00 | 134 | 8:00
| Kishorganj | 136 | 1:00 | 130 | 18:30 | Rajshahi New | 140 | 17:00 | 136 | 8:00
| Netrokona | 135 | 1:00 | 125 | 16:00 | C.Nawabganj | 140 | 18:00 | 132 | 8:00
| Jamalpur | 140 | 10:00 | 132 | 5:00 | Amnura | 140 | 17:00 | 131 | 8:00
| Sherpur | 139 | 12:00 | 128 | 5:00 | Pabna | 141 | 1:00 | 136 | 18:30
| Srimongal | 141 | 24:00 | 137 | 18:00 | Shahjadpur | 145 | 1:00 | 142 | 7:00
| Shahjibazar | 138 | 1:00 | 135 | 18:00 | Serajganj | 142 | 1:00 | 138 | 9:00
| Fenchuganj | 139 | 13:00 | 134 | 18:30 | Niyamatpur | 137 | 1:00 | 131 | 12:00
| Khulawara | 138 | 1:00 | 136 | 11:00 | Joypurhat | 140 | 17:00 | 134 | 12:00
| Sylhet | 136 | 1:00 | 135 | 8:00 | Sherpur(Bogura) | 143 | 2:00 | 138 | 12:00
| Chatak | 137 | 23:00 | 135 | 13:00 | Mohastangor | 141 | 1:00 | 137 | 18:00
| Sunamganj | 135 | 1:00 | 133 | 18:00 | Bangura | 144 | 1:00 | 140 | 19:00
| Biani Bazar | 137 | 7:00 | 134 | 17:00 | Rangpur | 138 | 1:00 | 130 | 18:00
| Comilla(s) | 132 | 22:00 | 128 | 18:00 | Lalmonirhat | 139 | 6:00 | 130 | 18:30
| Comilla(n) | 146 | 1:00 | 142 | 10:00 | Saidpur | 136 | 5:00 | 128 | 18:00
| Chandpur | 142 | 1:00 | 141 | 15:00 | Purbasadipur | 134 | 6:00 | 125 | 18:30
| Feni | 142 | 17:00 | 138 | 11:00 | Thakurgaon | 133 | 4:00 | 123 | 18:00
| Chowmuhani | 140 | 1:00 | 136 | 10:00 | Palashbari | 140 | 1:00 | 133 | 19:00
| Ashuganj | 142 | 3:00 | 140 | 11:00 | Barapukuria | 138 | 0.041667 | 131 | 0.77083
| Daudkandi | 141 | 1:00 | 139 | 7:00 | Panchagar | 134 | 0.125 | 124 | 0.77083
| B.Baria | 138 | 4:00 | 134 | 18:00 | Joldhaka | 136 | 0.16667 | 125 | 0.77083
| Ramganj | 141 | 5:00 | 135 | 10:00 | Kurigram | 137 | 0.16667 | 128 | 0.77083
| Chaddagram | 143 | 1:00 | 140 | 10:00 | Mithapukur | 140 | 1:00 | 135 | 12:00
| PHP | 143 | 6:00 | 137 | 14:00

## L-Curve
Date | 2022-01-05
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 0 | 4979 | 2144 | 7123 |  |  |  | QF-LDC-11
0:30 | 83 | 4749.5 | 2163.5 | 6913 | Date: | 2022-01-05
1:00 | 166 | 4520 | 2183 | 6703
1:30 | 218 | 4367 | 2148.5 | 6515.5
2:00 | 270 | 4214 | 2114 | 6328
2:30 | 250 | 4092 | 2085.5 | 6177.5 | [5 empty] | Gen. at Eve. Peak | 9239 | 9239 MW (19:00 )
3:00 | 230 | 3970 | 2057 | 6027 | [6 empty] | 19:00
3:30 | 232 | 3926.5 | 2007.5 | 5934 | [5 empty] | Gen. at Day Peak | 7756 | 7756 MW (12:00 )
4:00 | 234 | 3883 | 1958 | 5841 | [6 empty] | 12:00
4:30 | 242 | 3797 | 1947.5 | 5744.5 | [5 empty] | Highest Generation | 9239
5:00 | 250 | 3711 | 1937 | 5648 | [6 empty] | 19:00
5:30 | 161 | 3857.5 | 1952.5 | 5810
6:00 | 72 | 4004 | 1968 | 5972
6:30 | 65 | 4231.5 | 1975.5 | 6207
7:00 | 58 | 4459 | 1983 | 6442
7:30 | 31 | 4606.5 | 2074 | 6680.5
8:00 | 4 | 4754 | 2165 | 6919
8:30 | 64 | 4868 | 2262 | 7130
9:00 | 124 | 4982 | 2359 | 7341
9:30 | 143 | 5023.5 | 2373 | 7396.5
10:00 | 162 | 5065 | 2387 | 7452
10:30 | 177 | 5148.5 | 2358 | 7506.5
11:00 | 192 | 5232 | 2329 | 7561
11:30 | 192 | 5273.5 | 2385 | 7658.5
12:00 | 192 | 5315 | 2441 | 7756
12:30 | 187 | 5382.5 | 2492 | 7874.5
13:00 | 182 | 5450 | 2543 | 7993
13:30 | 237 | 5338 | 2475.5 | 7813.5
14:00 | 292 | 5226 | 2408 | 7634
14:30 | 327 | 5206.5 | 2360.5 | 7567
15:00 | 362 | 5187 | 2313 | 7500
15:30 | 386 | 5111 | 2279 | 7390
16:00 | 410 | 5035 | 2245 | 7280
16:30 | 365 | 5077 | 2294 | 7371
17:00 | 320 | 5119 | 2343 | 7462
17:30 | 186 | 5616.5 | 2545 | 8161.5
18:00 | 52 | 6114 | 2747 | 8861
18:30 | 62 | 6219.5 | 2830.5 | 9050
19:00 | 72 | 6325 | 2914 | 9239
19:30 | 28 | 6092 | 2969 | 9061
20:00 | 14 | 6031 | 2959 | 8990 |  |  |  | Executive Engineer
20:30 | 22 | 6023.5 | 2924 | 8947.5 |  |  |  | Network Operation Division
21:00 | 30 | 6016 | 2889 | 8905
21:30 | 72 | 5835 | 2798.5 | 8633.5
22:00 | 114 | 5654 | 2708 | 8362 |  |  |  |  | Page 6 of 7
22:30 | 96 | 5466.5 | 2520.5 | 7987
23:00 | 78 | 5279 | 2333 | 7612
23:30 | 39 | 5129 | 2238.5 | 7367.5
24:00 | 0 | 4979 | 2144 | 7123
9239 MW (19:00 )
7756 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-01-05 |  | Energy |  | 180750243
[13 empty] | 2022-01-05 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 2502 | 527 | 1635 | 0 | 1736 | 550 | 86 | 0 | 6 | 81 | 0 | 0
0:30 | 2493 | 505.5 | 1518 | 0 | 1676 | 555 | 86 | 0 | 3 | 76.5 | 0 | 0 | Date: | 2022-01-05
1:00 | 2484 | 484 | 1401 | 0 | 1616 | 560 | 86 | 0 | 0 | 72 | 0 | 0
1:30 | 2487 | 484 | 1403 | 0 | 1443.5 | 540 | 86 | 0 | 0 | 72 | 0 | 0 | [8 empty] | Total Energy | 180.7502 | Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
2:00 | 2490 | 484 | 1405 | 0 | 1271 | 520 | 86 | 0 | 0 | 72 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 2483.5 | 484 | 1419.5 | 0 | 1123 | 509.5 | 86 | 0 | 0 | 72 | 0 | 0 | [8 empty] | Energy Requirement | 180.7502
3:00 | 2477 | 484 | 1434 | 0 | 975 | 499 | 86 | 0 | 0 | 72 | 0 | 0
3:30 | 2480.5 | 484 | 1448.5 | 0 | 870 | 494 | 86 | 0 | 0 | 71 | 0 | 0 | [6 empty] | Shortage
4:00 | 2484 | 484 | 1463 | 0 | 765 | 489 | 86 | 0 | 0 | 70 | 0 | 0
4:30 | 2397 | 484 | 1490.5 | 0 | 727 | 489 | 86 | 0 | 0 | 71 | 0 | 0
5:00 | 2310 | 484 | 1518 | 0 | 689 | 489 | 86 | 0 | 0 | 72 | 0 | 0
5:30 | 2350.5 | 484 | 1564 | 0 | 752.5 | 499 | 86 | 0 | 0 | 74 | 0 | 0
6:00 | 2391 | 484 | 1610 | 0 | 816 | 509 | 86 | 0 | 0 | 76 | 0 | 0
6:30 | 2362.5 | 525 | 1598 | 0 | 1073 | 489 | 86 | 0 | 0 | 73 | 0.5 | 0 |  |  |  |  | Coal
7:00 | 2334 | 566 | 1586 | 0 | 1330 | 469 | 86 | 0 | 0 | 70 | 1 | 0
7:30 | 2370 | 618.5 | 1617 | 0 | 1419 | 484 | 86 | 0 | 0 | 71.5 | 14.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 2406 | 671 | 1648 | 0 | 1508 | 499 | 86 | 0 | 0 | 73 | 28 | 0
8:30 | 2241.5 | 671 | 1717.5 | 0 | 1778.5 | 514.5 | 86 | 0 | 0 | 73.5 | 47.5 | 0
9:00 | 2077 | 671 | 1787 | 0 | 2049 | 530 | 86 | 0 | 0 | 74 | 67 | 0
9:30 | 2027.5 | 671.5 | 1711 | 0 | 2228 | 515 | 86 | 0 | 4.5 | 73.5 | 79.5 | 0
10:00 | 1978 | 672 | 1635 | 0 | 2407 | 500 | 86 | 0 | 9 | 73 | 92 | 0
10:30 | 2072.5 | 671.5 | 1660 | 0 | 2321 | 495 | 86 | 0 | 20.5 | 78 | 102 | 0
11:00 | 2167 | 671 | 1685 | 0 | 2235 | 490 | 86 | 0 | 32 | 83 | 112 | 0
11:30 | 2176.5 | 671.5 | 1725.5 | 0 | 2287 | 495 | 63 | 0 | 32 | 87 | 121 | 0
12:00 | 2186 | 672 | 1766 | 0 | 2339 | 500 | 40 | 0 | 32 | 91 | 130 | 0
12:30 | 2188 | 671.5 | 1670 | 0 | 2496 | 495 | 63 | 0 | 64 | 94 | 133 | 0
13:00 | 2190 | 671 | 1574 | 0 | 2653 | 490 | 86 | 0 | 96 | 97 | 136 | 0
13:30 | 2190 | 671 | 1574 | 0 | 2653 | 490 | 86 | 0 | 96 | 97 | 136 | 0
14:00 | 2190 | 671 | 1574 | 0 | 2653 | 490 | 86 | 0 | 96 | 97 | 136 | 0
14:30 | 2189.5 | 671.5 | 1595.5 | 0 | 2402.5 | 494.5 | 86 | 0 | 99 | 97 | 111 | 0
15:00 | 2189 | 672 | 1617 | 0 | 2152 | 499 | 86 | 0 | 102 | 97 | 86 | 0
15:30 | 2225 | 672 | 1571 | 0 | 2072 | 499 | 86 | 0 | 105 | 96 | 64 | 0
16:00 | 2261 | 672 | 1525 | 0 | 1992 | 499 | 86 | 0 | 108 | 95 | 42 | 0
16:30 | 2247 | 672 | 1502 | 0 | 2082.5 | 499 | 86 | 0 | 167 | 91 | 24.5 | 0
17:00 | 2233 | 672 | 1479 | 0 | 2173 | 499 | 86 | 0 | 226 | 87 | 7 | 0
17:30 | 2314.5 | 695.5 | 1585 | 7.5 | 2555 | 499 | 86 | 0 | 319 | 96.5 | 3.5 | 0
18:00 | 2396 | 719 | 1691 | 15 | 2937 | 499 | 86 | 0 | 412 | 106 | 0 | 0
18:30 | 2446.5 | 719.5 | 1713.5 | 7.5 | 3052.5 | 549 | 86 | 0 | 372.5 | 103 | 0 | 0
19:00 | 2497 | 720 | 1736 | 0 | 3168 | 599 | 86 | 0 | 333 | 100 | 0 | 0
19:30 | 2423 | 720 | 1815 | 0 | 2993 | 619 | 86 | 0 | 307 | 98 | 0 | 0
20:00 | 2420 | 720 | 1725 | 0 | 2997 | 640 | 86 | 0 | 302 | 100 | 0 | 0
20:30 | 2439 | 720 | 1661.5 | 0 | 3009.5 | 640 | 86 | 0 | 293 | 98.5 | 0 | 0
21:00 | 2458 | 720 | 1598 | 0 | 3022 | 640 | 86 | 0 | 284 | 97 | 0 | 0
21:30 | 2469.5 | 720 | 1599.5 | 0 | 2850 | 630 | 86 | 0 | 184 | 94.5 | 0 | 0
22:00 | 2481 | 720 | 1601 | 0 | 2678 | 620 | 86 | 0 | 84 | 92 | 0 | 0
22:30 | 2492 | 715 | 1605 | 0 | 2357.5 | 600 | 86 | 0 | 45 | 86.5 | 0 | 0
23:00 | 2503 | 710 | 1609 | 0 | 2037 | 580 | 86 | 0 | 6 | 81 | 0 | 0
23:30 | 2502.5 | 618.5 | 1622 | 0 | 1886.5 | 565 | 86 | 0 | 6 | 81 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 23.8° C
24:00 | 2502 | 527 | 1635 | 0 | 1736 | 550 | 86 | 0 | 6 | 81 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
Note on W13: Author:

## Generation
g | 2022-01-05
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 0 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1030800
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 968000
3 | Chattogram TPP-1
4 | Chattogram TPP-2 | [14 empty] | 34 | 100 | 120 | 120 |  | 120 | 100 | 100 | 100 | 100 | 100 | 100 | 1000000
5 | Raozan 25 MW PP | [9 empty] | 7 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 |  | 17 | 17 | 17 | 17 |  |  |  | 126223
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 7 | 13 | 17 | 19 | 20 | 19 | 17 | 13 | 7 | 1 | [9 empty] | 133515
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 51 |  | 51 | 51 | 51 | 51 |  |  |  | 211116
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 |  |  |  | 8 | 34 | 34 | 34 | 34 | 34 | 34 | 65 | 34 | 34 | 34 | 39 | 84 |  | 105 | 68 | 68 | 68 | 68 | 17 | 17 | 957636
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [17 empty] | 50 | [8 empty] | 56032
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 95 | [5 empty] | 25 | 69 | 188 | 223 | 255 | 260 | 270 | 263 | 273 | 280 | 278 | 273 |  | 278 | 278 | 278 | 278 | 275 | 255 | 261 | 4491271
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 36 | 65 | 120 | 187 | 185 | 185 | 73 | 73 | 73 | 73 | 73 | 73 |  | 73 | 73 | 16 | 16 | 16 | 16 | 16 | 1421818
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 270 | 250 | 220 | 220 | 320 | 320 | 320 | 320 | 320 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7315627
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 100 | 130 | 130 | 130 | 130 | 130 | 130 | 80 | 130 | 80 | 80 | 80 | 80 |  | 100 | 85 | 80 | 80 | 80 | 80 | 80 | 2254050
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 23 | 26 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 494928
33 | Ashuganj 225 MW CCPP | 208 | 213 | 215 | 220 | 227 | 228 | 182 | 182 | [18 empty] | 1832000
34 | Ashuganj 450 MW CCPP(South) | 265 | 270 | 265 | 263 | 265 | 295 | 295 | 355 | 305 | 300 | 305 | 300 | 280 | 270 | 270 | 265 | 265 | 300 |  | 300 | 280 | 280 | 280 | 270 | 265 | 265 | 6982000
| Ashuganj 450 MW CCPP(North) | 150 | 150 | 150 | 150 | 0 | 0 |  |  |  |  | 270 | 265 | 250 | 220 | 220 | 180 | 180 | 200 |  | 270 | 245 | 240 | 240 | 240 | 240 | 240 | 3845000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 20 | 20 | 35 | 51 | 55 | 55 | 55 | 54 | 55 | 53 | 55 | 55 |  | 54 | 55 | 55 | 56 | 55 | 56 | 55 | 939840
36 | Chandpur 150 MW CCPP | 127 | 124 | 124 | 129 | 132 | 128 | 135 | 135 | 135 | 134 | 135 | 136 | 138 | 137 | 136 | 136 | 129 | 129 |  | 129 | 132 | 132 | 129 | 131 | 126 | 128 | 3166880
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4180750
41 | Haripur 360MW CCPP(HPL) | 185 | 185 | 179 | 183 | 194 | 193 | 193 | 194 | 190 | 192 | 192 | 191 | 190 | 189 | 182 | 172 | 162 | 162 |  | 162 | 162 | 162 | 163 | 155 | 149 | 157 | 4302000
42 | RPCL 210MW CCPP | 97 | 97 | 97 | 100 | 101 | 103 | 94 | 71 | 71 | 69 | 33 | 33 | 33 | 33 | 32 | 49 | 50 | 49 |  | 50 | 50 | 51 | 51 | 51 | 50 | 50 | 1522560
43 | Sutiakhali 50 MW Solar PP
44 | Fenchugonj CCPP Phase-1 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1009000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 70 | 69 | 70 | 69 | 70 | 71 | 40 | 72 | 73 | 57 | 40 | 72 | 40 | 40 | 40 | 40 | 25 | 34 |  | 34 | 34 | 34 | 34 | 34 | 72 | 71 | 1261152
48 | Shahjibazar 86MW PP (Shahjibazar) | 79 | 79 | 79 | 79 | 79 | 78 | 79 | 79 | 78 | 78 | 78 | 78 | 78 | 78 | 79 | 78 | 78 | 80 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1879680
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 171 | 191 | 190 | 190 | 165 | 190 | 165 | 165 | 185 |  | 185 | 190 | 190 | 190 | 190 | 190 | 190 | 4375030
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 423000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 251820
54 | Hobiganj 11MW PP Cofidence-E | 11 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 163584
55 | Fenchugonj 51 MW PP (Barakatullah) | 51 | 51 | 51 | 51 | 51 | 51 | 48 | 45 | 45 | 45 | 48 | 51 | 51 | 50 | 51 | 50 | 23 | 44 |  | 50 | 50 | 51 | 51 | 51 | 51 | 51 | 1147800
56 | Shahjahanulla 25 MW PP | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 22 | 533664
57 | Bibiana-II 341 MW CCPP (Summit) | 30 | 35 | 60 | 100 | 160 | 250 | 285 | 325 | 341 | 270 | 280 | 300 | 280 | 290 | 295 | 285 | 290 | 275 |  | 275 | 290 | 280 | 280 | 260 | 270 | 270 | 5968500
| Bibiyana South 400 MW | 401 | 400 | 400 | 400 | 360 | 400 | 400 | 400 | 370 | 341 | 320 | 320 | 318 | 320 | 320 | 322 | 305 | 400 |  | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 8903500
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 809698
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 21 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 532080
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 478080
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 442656
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 20 | 20 | 20 | 438660
63 | Impoprt (Tripura) | 72 | 72 | 72 | 70 | 72 | 76 | 70 | 73 | 74 | 73 | 83 | 91 | 97 | 98 | 97 | 95 | 87 | 106 |  | 100 | 98 | 100 | 97 | 92 | 81 | 81 | 1972800
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 38 | 38 | 40 | 38 | 36 | 12 | 5 | 5 | 3 | 5 | 2 | 8 | 4 | 4 | 6 | 10 |  | 17 | 17 | 20 | 23 | 30 | 38 | 38 | 48570
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 18 | 18 | 18 | 18 | 21 |  | 10 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 455760
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | [6 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 203400
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 22 | 22 | 21 | 17 | 17 | 17 | 16 | 32 | 32 | 30 |  | 25 | 25 | 30 | 33 | 33 | 33 | 33 | 670600
68 | Cumilla 25 MW PP (Summit) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 5 | 5 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 233080
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 9 | 9 | 9 | 9 | 108000
71 | Maona 33 MW PP(Summit) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 16 | 16 | 586600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 821200
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | 17 | 17 | 17 | 17 | 17 | 28 | 45 | 16 | 34 | 45 | 45 | 50 | 84 | 85 | 85 | 85 | 89 | 113 |  | 113 | 85 | 85 | 85 | 85 | 85 | 36 | 1576680
| Manikgonj 162MW PP(MPGL) | 126 | 72 | 17 | 17 | 17 | 17 | 100 | 124 | 162 | 162 | 126 | 126 | 148 | 162 | 162 | 126 | 132 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3067200
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [8 empty] | 18 | 51 | 51 | 51 | 25 | 25 | 25 | 25 | 25 | 36 |  | 51 | 51 | 51 | 51 | 25 |  |  | 519840
79 | Kodda 150MW PP | [16 empty] | 48 | 100 |  | 82 | 82 | 82 | 64 | 16 |  |  | 362880
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 25 | 25 | 25 | 25 | 30 | 52 |  | 52 | 25 | 25 | 25 | 25 | 25 | 25 | 486302
| Gazipur 100 MW PP | 50 | 50 |  |  |  |  | 10 | 50 | 105 | 105 | 90 | 90 | 70 | 70 | 70 | 70 | 80 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1738800
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 4 | 4 | 5 | 3 | 3 | 2 | 1 | [10 empty] | 25439
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 54 | 54 | 54 | 39 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1295999
| Karnaphuli Power Ltd. | 110 | 68 | 34 | 17 | 17 | 24 | 51 | 51 | 72 | 110 | 100 | 81 | 110 | 68 | 68 | 68 | 77 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 34 | 2009773
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [11 empty] | 3 | 11 | 11 | 12 | 12 | 11 | 11 |  | 12 | 11 | 11 | 11 |  |  |  | 115485
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 53 | 17 | 10 |  |  |  | 14 | 35 | 59 | 104 | 104 | 104 | 104 | 55 | 54 | 54 | 54 | 68 |  | 95 | 104 | 104 | 104 | 104 | 43 |  | 1441920
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [9 empty] | 10 | 10 | 10 | 10 |  |  |  | 10 | 10 | [8 empty] | 58680
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 15 | 15 | 35 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1187520
94 | Gagnagar 102 MW PP (Digital Power) | [6 empty] | 7 | 40 | 54 | 82 | 82 | 82 | 102 | 102 | 74 | 74 | 102 | 102 |  | 102 | 102 | 102 | 102 | 84 | 24 | 7 | 1355328
95 | Patenga 50MW PP (Baraka) | 46 | 46 | 41 | 46 | 46 | 46 | 46 | 47 | 46 | 46 | 45 | 45 | 46 | 45 | 45 | 40 | 37 | 45 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1085280
96 | Chattogram 108 MW PP (ECPV) | 79 | 80 | 82 | 76 | 77 | 77 | 77 | 77 | 79 | 77 | 77 | 79 | 84 | 84 | 84 | 84 | 84 | 87 |  | 90 | 90 | 90 | 90 | 90 | 91 | 91 | 2001600
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [7 empty] | 1 | 15 | 15 | 15 | 15 | 25 | 50 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 30 |  |  | 577295
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 17 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1239328
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 100 | 100 | 130 | 130 | 163 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 163 |  | 163 | 163 | 163 | 130 | 130 | 130 | 130 | 3306354
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 | 1 | 0 | [10 empty] | 7600
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 845280
104 | Keranigonj 300 MW PP (APR) | [17 empty] | 11 | [8 empty] | 11060
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 150 | 110 | 60 | 35 | 35 | 40 | 65 | 84 | 127 | 150 | 150 | 150 | 150 | 150 | 150 | 120 | 132 | 187 |  | 184 | 175 | 175 | 185 | 184 | 184 | 193 | 3247200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [7 empty] | 5 | 18 | 57 | 71 | 70 | 59 | 17 | 17 | 17 | 23 | 85 |  | 149 | 149 | 149 | 149 | 116 | 76 | 28 | 1156608
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 60 | 60 | 30 | 60 | 60 | 90 | 90 | 90 | 90 | 90 | 90 | 50 | 50 | 50 | 20 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 50 | 1737600
116 | Chandpur 200MW (Desh energy) | [12 empty] | 11 | 17 | 17 | 17 | 17 | 17 |  | 17 | [6 empty] | 118560
117 | Ashuganj 150MW PP (Midland) | 147 | 143 | 138 | 137 | 143 | 142 | 143 | 135 | 137 | 140 | 138 | 128 | 133 | 142 | 135 | 135 | 140 | 138 |  | 148 | 148 | 148 | 150 | 148 | 150 | 138 | 3385600
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | [5 empty] | 2 | 8 | 32 | 42 | 45 | 45 | 45 | 45 | 45 | 24 | 24 | 24 | 46 |  | 104 | 104 | 104 | 104 | 104 | 35 | 8 | 996000
| Anwara 300 MW PP (United) | [5 empty] | 30 | 80 | 50 | 30 | 30 | 30 | 30 | 65 | 65 | 65 | 30 | 50 | 130 |  | 100 | 65 | 65 | 65 | 30 |  |  | 1106509
| Juldah unit-2 (Acorn) | 50 | 10 |  |  |  | 20 | 40 | 40 | 90 | 35 | 35 | 70 | 70 | 30 | 30 | 30 | 60 | 100 |  | 100 | 70 | 70 | 70 | 10 | 10 |  | 1007040
| Anlima Energy Ltd. | 116 | 116 | 116 | 69 | 69 | 70 | 111 | 116 | 116 | 68 | 68 | 73 | 99 | 114 | 116 | 116 | 116 | 116 |  | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 2565545
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [5 empty] | 4 | 17 | 17 | 17 | 17 | 388800
| Spectra Solar Plant Ltd. | [6 empty] | 0 | 2 | 6 | 7 | 10 | 20 | 29 | 26 | 19 | 9 | 2 | [9 empty] | 126337
| Chandpur 115(Doreen) | [26 empty] | 0
| Kanchan Purbachal Power Generation Ltd. | [8 empty] | 10 | 46 | 29 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 819000
120 | Eastern Zone Total | 4520 | 4214 | 3970 | 3883 | 3711 | 4004 | 4459 | 4754 | 4982 | 5065 | 5232 | 5315 | 5450 | 5226 | 5187 | 5035 | 5119 | 6114 |  | 6325 | 6092 | 6031 | 6016 | 5654 | 5279 | 4979 | 122520402
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [15 empty] | 4 | 10 | 7 |  | 25 | 31 | 26 | 26 | 8 | 6 | 6 | 99840
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [8 empty] | 24 | 65 | 70 | 70 | 105 | 70 | 17 | 17 | 17 | 68 |  | 105 | 105 | 105 | 105 | 70 |  |  | 1056960
130 | Mongla Orion 100 MW Solar PP | [7 empty] | 17 | 45 | 62 | 73 | 77 | 77 | 63 | 47 | 24 | 4 | [9 empty] | 484560
131
132 | United Payra Power Ltd.
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 220 |  | 206 | 220 | 220 | 210 | 220 | 220 | 220 | 4489391
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 272930
| Bhola 225 MW CCPP | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 90 | 92 | 91 | 91 | 85 | 91 |  | 91 | 91 | 91 | 90 | 92 | 91 | 91 | 2214885
140 | Bhola 33 MW PP (Venture) | 17 | 16 | 15 | 15 | 14 | 14 | 13 | 14 | 13 | 12 | 11 | 13 | 15 | 13 | 12 | 11 | 12 | 18 |  | 21 | 21 | 21 | 23 | 23 | 20 | 17 | 370300
141 | Noapara 100 MW PP (Bangla Trac) | [9 empty] | 0 | [7 empty] | 4 | [8 empty] | 9600
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 484 | 484 | 484 | 484 | 484 | 484 | 566 | 671 | 671 | 672 | 671 | 672 | 671 | 671 | 672 | 672 | 672 | 719 |  | 720 | 720 | 720 | 720 | 720 | 710 | 527 | 15118545
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 360 | 320 | 300 | 290 | 290 | 310 | 270 | 300 | 330 | 300 | 290 | 300 | 290 | 300 | 300 | 300 | 300 | 300 |  | 400 | 420 | 440 | 440 | 420 | 380 | 350 | 8785100
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 199 | 199 | 199 | 199 | 199 | 199 | 200 | 200 | 200 | 200 | 200 | 199 | 199 | 199 | 199 | 199 |  | 199 | 199 | 200 | 200 | 200 | 200 | 200 | 4861600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [16 empty] | 35 | 43 |  | 43 | 43 | 43 | 43 |  |  |  | 187378
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 0 | 0 | 2 | 3 | 3 | 3 | 2 | 0 | 0 | [9 empty] | 18780
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 161 | 168 | 157 | 154 | 156 | 147 | 142 | 136 | 128 | 119 | 117 | 117 | 137 | 165 | 162 | 192 | 188 | 160 |  | 165 | 163 | 164 | 194 | 220 | 220 | 220 | 4128800
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 364 | 364 | 375 | 360 | 373 | 379 | 292 | 340 | 373 | 261 | 299 | 354 | 296 | 324 | 332 | 301 | 282 | 333 |  | 360 | 409 | 382 | 291 | 306 | 305 | 326 | 8077600
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [12 empty] | 14 | 15 | 20 | 22 | 26 | 29 | [8 empty] | 120349
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 520560
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 181530
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern) | [9 empty] | 34 | 34 | 34 | 8 | 8 | 8 | 8 | 8 | 34 |  | 34 | 34 | 34 | 34 |  |  |  | 273609
167 | Katakhali 50 MW Peaking PP | [9 empty] | 9 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | [6 empty] | 259379
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 25 | 25 | 30 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 810278
170 | Chapainawabganj 100 MW Peaking PP | [12 empty] | 50 | 50 | 50 | 50 | 75 | 100 |  | 100 | 100 | 100 | 100 | 60 |  |  | 694664
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 70 | 35 | 35 |  |  |  | 29 | 35 | 52 | 109 | 70 | 70 | 102 | 35 | 35 | 35 | 40 | 94 |  | 113 | 113 | 113 | 113 | 70 |  |  | 1460832
172 | Confidence Power Bogura Unit-1 113 MW | 70 | 70 | 35 | 35 |  | 10 | 35 | 35 | 100 | 113 | 70 | 95 | 113 | 70 | 35 | 35 | 70 | 113 |  | 113 | 113 | 113 | 113 | 113 |  |  | 1656960
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 70 | 70 | 70 | 34 | 34 | 38 | 90 | 100 | 105 | 112 | 70 | 83 | 112 | 70 | 72 | 35 | 72 | 112 |  | 112 | 112 | 112 | 112 | 111 | 106 | 112 | 2045164
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 1 | 2 | 3 | 4 | 3 | 3 | 2 | 1 | 0 | [9 empty] | 30247
178 | Energypac Power Venture Thakurgaon Ltd.
178