## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:January 2022
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2022-01-01 |  | 2021-12-01 |  | 2021-01-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 10021 | 2022-01-25 | 9588 | 2021-12-02 | 9380 | 19-01-2021 | 13792 | 2021-04-27
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 20:00
2 | Minimum Generation (MW) | 5475 | 2022-01-08 | 5167 | 2021-12-17 | 5153 | 02/01/21 | - | -
|  |  | 6:00 |  | 6:00 |  | 4:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 10021 | 2022-01-25 | 9588 | 2021-12-02 | 9380 | 19-01-2021 | 13792 | 2021-04-27
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 20:00
4 | Maximum Day Peak Generation (MW) | 8945 | 2022-01-30 | 8400 | 2021-12-02 | 8147 | 20-01-2021 | 11773 | 2021-04-27
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 10021 | 2022-01-25 | 9588 | 2021-12-02 | 9380 | 19-01-2021 | 14097 | 2021-04-27
|  |  | 12:00 |  | 12:00 |  | 19:00 |  | 19:00
6 | Average Generation (MW) at Evening Peak | 9483.1935 |  | 9041.1935 |  | 9006.2258 |  | 12676.7 | 2021-04-27
7 | Average Generation (MW) at Day Peak | 8138.6774 |  | 7577.4194 |  | 7478.5484 |  | 10379.6667 | 2021-04-27
8 | Maximum Power Import from India, BIPTC (MW) | 768 | 2022-01-31 | 736 | 2021-12-20 | 916 | 25/25/2021 | 956 | 27/3/2019
|  |  | 200:00 |  | 17:30 |  | 20:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 136 | 2022-01-26 | 112 | 2021-12-11 | 118 | 30/01/2021 | 194 | 12/06/19
|  |  | 18:30 |  | 18:00 |  | 19:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 04/05/2010
|  |  | - |  | - |  |  |  | 20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 13792 | 2021-04-27
|  | - | - | - | - | - | - |  | 20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 1181.174 |  | 1148.0976 |  | 2455.6397 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 67.0345 |  | 97.7685 |  | 60.8695
22 | Net Generation of BPDB (MKWH) | 1114.1395 |  | 1050.329 |  | 2394.7701
23 | Net Generation of IPP (MKWH) | 3576.4276 |  | 3411.0841 |  | 1839.415
24 | Net Generation of REB (MKWH) | 117.4558 |  | 126.8797 |  | 130.737
24 | Net Generation of Rental Power Plant (MKWH) | 409.5082 |  | 390.0595 |  | 490.6295
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 5217.5311 |  | 4978.3523 |  | 4855.5516 |  | 7072.7704 | April'21
26 | Energy Generation by Gas (MKWH) | 2951.4743 |  | 3368.8362 |  | 3124.5982 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 221.4774 |  | 189.0553 |  | 195.6927 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1606.076 |  | 1014.2984 |  | 1194.4037 |  | 1679.4648 | Sep-20
29 | Energy Generation by Hydro (MKWH) | 70.6636 |  | 52.2948 |  | 34.537 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 27.2583 |  | 23.3093 |  | 8.8809 |  | 27.26 | January-22
31 | Energy Generation by Coal (MKWH) | 407.6161 |  | 428.3268 |  | 358.3085 |  | 627.4399 | April'21
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 535.5104 |  | 450.7438 |  | 528.0244 |  | 775.9511 | August-20
33 | Monthly Load Factor (%) | 78.0725 |  | 77.488 |  | 80.6155 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:November 2021
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 10021 | 2022-01-25 | 19:00
Generation Period
| Dhaka | MW | 3576
| Chattogram | MW | 1108
| Cumilla | MW | 791
| Mymensingh | MW | 888
| Sylhet | MW | 343
a) | Total supply in East zone | MW | 6706
| Khulna | MW | 1097
| Barisal | MW | 246
| Rajshahi | MW | 1015
| Rangpur | MW | 706
b) | Total supply in West zone | MW | 3064
c) | Total supply in both zone ( a+b) | MW | 9770
Ref: | 27.21.0000.603.16.087.20.485 | Date: 18/02/2022
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:December 2021
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 750 | 2022-01-15 | 8:00
| b) Ishurdi end | MW | 541 | 2022-01-14 | 7:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 1000 | 201-1-22 | 16:00
| b) Ishurdi end | MW | 188 | 2022-01-29 | 18:30
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | -
| b) Ishurdi end | MKWH | -
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | -
| b) Ishurdi end | MKWH | -
23 | Transmission loss of EWI/ NO-1 | %
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 260 | 2022-01-23 | 18:30
| b)Serajganj end | MW | 250 | 2022-01-20 | 16:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 290 | 2022-01-04 | 15:00
| b)Sirajganj end | MW | 260 | 2022-01-23 | 18:30
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 2.024 | 2022-01-23
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 20.8
| b)Sirajganj end | MKWH | 42.05
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 40.86
| b)Sirajganj end | MKWH | 21.07
30 | Transmission loss of EWI /NO-2 | % | 1.48
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: January2022
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Dhamrai | 132/33 kV transformer T-1 | 2022-01-01 09:45 | 2022-01-01 10:36 | 0:51 | T | Tripped showing PRD. relay | 0 | 0 | No interruption
Bhaluka | 132/33 kV transformer T-1 | 2022-01-01 11:30 | 2022-01-01 13:06 | 1:36 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer T-03 | 2022-01-06 20:50 | 2022-01-06 21:41 | 0:51 | T | Tripped showing Lockout. relay | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformers T-1 &,T2 | 2022-01-10 22:45 | 2022-01-10 23:14 | 0:29 | E/O | Due to 33 kV feeder fault | 94 | 45.4333 | Power interruption 22:45 to 23:14
| 132/33 kV transformers T-3 | 2022-01-10 22:45 | 2022-01-11 23:53 | 25:08 | E/O
Aminbazar | 230/132 kV transformers T-1 & T2 | 2022-01-12 06:41 | 2022-01-12 06:41 | 0:00 | T | Due to winding temperature high | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformers T-1 &,T2 | 2022-01-14 15:10 | 2022-01-14 15:41 | 0:31 | E/O | Due to 33 kV feeder fault | 32 | 16.5333 | Power interruption
Kabirpur | 230/132 kV transformers T-1 & T2 | 2022-01-23 20:05 | 2022-01-23 20:19 | 0:14 | E/O | Due to 33 kV feeder fault | 90 | 21 | Power interruption 22:45 to 23:14
|  |  | Total : | 29:40 |  | Unserved Energy: |  | 82.9667
Dhaka (South) Grid Circle :
Haripur | 230/132 kV transformer T02 | 2022-01-03 08:04 | 2022-01-03 08:04 | 0:00 | T | Tripped showing Diff. relay | 0 | 0 | No interruption
Hasnabad | 132/33 kV transformers T-1 & T5 | 2022-01-04 07:37 | 2022-01-04 08:02 | 0:25 | E/O | Due to 33 kV feeder fault | 40 | 16.6667 | Power interruption
Ullon | 132/33 kV transformer T-2 | 2022-01-07 16:52 | 2022-01-07 18:27 | 1:35 | T | Tripped showing O/C relay at 33 kV side | 0 | 0 | No interruption
Sonargaon | 132/33 kV transformer T1 | 2022-01-14 16:12 | 2022-01-14 16:33 | 0:21 | E/O | Due to 33 kV feeder fault | 0 | 0 | No interruption
Keraniganj | 230/132 kV transformer T03 | 2022-01-22 23:47 | 2022-01-22 23:47 | 0:00 | T | Tripped showing lockout relay | 0 | 0 | No interruption
Hasnabad | 132/33 kV transformers T-1 & T5 | 2022-01-30 15:52 | 2022-01-30 16:25 | 0:33 | E/O | Due to Sreenagar PBS feeder fault | 40 | 33.3333 | Power interruption
|  |  | Total : | 2:54 |  | Unserved Energy: |  | 50
Chattogram Grid Circle :
Khulshi | 132/33 kV transformers T-1 & T2 | 2021-01-10 16:02 | 2021-01-10 16:33 | 0:31 | T | Due to 33 kV feeder fault | 22 | 11.3667 | Power interruption
Hathazari | 132/33 kV transformer T1 | 2021-01-13 04:10 | 2021-01-13 04:52 | 0:42 | T | Tripped showing O/V relay | 10 | 7 | Power interruption
Bhandaria | 132/33 kV transformer T1 | 2021-01-15 08:05 | 2021-01-17 17:42 | 57:37 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Hathazari | 132/33 kV transformer T1 | 2021-01-24 11:25 | 2021-01-24 16:18 | 4:53 | E/O |  | 15 | 14.25 | Power interruption 11:25 to 16:18
|  |  | Total : | 63:43 |  | Unserved Energy: |  | 32.6167
Cumilla Grid Circle :
Fenchuganj | 132/33 kV transformer T2 | 2022-01-01 09:10 | 2022-01-01 09:32 | 0:22 | T | Tripped showing O/C relay | 10 | 3.6667 | Power interruption
Chowddagram | 132/33 kV transformer T1 | 2022-01-03 14:48 | 2022-01-03 15:06 | 0:18 | T | Tripped showing O/C relay at PBS work | 0 | 0 | No interruption
Daudkandi | 132/33 kV transformer T3 | 2022-01-14 21:20 | 2022-01-14 22:12 | 0:52 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Fenchuganj | 132 kV Bus-2 | 2022-01-17 14:02 | 2022-01-17 16:46 | 2:44 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Sreemogal | 132/33 kV transformer T1 | 2022-01-20 13:45 |  |  | E/O | Due to 33 kV cable burst | 0 | 0 | No interruption
B.Baria | 132/33 kV transformers T-1 & T2 | 2022-01-24 01:27 | 2022-01-24 06:53 | 5:26 | T | Due to 33 kV feeder fault | 50 | 271.6667 | Power interruption
|  |  | Total : | 9:42 |  |  |  | 275.3333
Khulna Grid Circle :
Rampur | 132/33 kV transformer T1 | 2022-01-13 04:09 | 2022-01-13 04:09 | 0:00 | T | Tripped showing O/V relay | 0 | 0 | No interruption
Khulna© | 33 kV Bus section-3 | 2022-01-30 14:42 | 2022-01-30 15:32 | 0:50 | E/O | Due to red-hot maint | 4 | 3.3333 | Power interruption
Barisal(S) | 132/33 kV transformer T2 | 2022-01-31 12:20 | 2022-01-31 12:43 | 0:23 | E/O | Due to red-hot maint | 0 | 0 | No interruption
|  |  | Total : | 1:13 |  | Unserved Energy: |  | 3.3333
HVDC Grid Circle :
Baghabari | 230/33 kV transformer T02 | 2022-01-07 10:30 | 2022-01-07 12:39 | 2:09 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Bheramara | Bheramara HVDC 400 kV pole-1 | 2022-01-12 09:47 | 2022-01-12 11:06 | 1:19 | T | Due to external fault | 0 | 0 | No interruption
| Bheramara HVDC block-1 | 2022-01-14 15:50 | 2022-01-14 16:48 | 0:58 | T |  | 0 | 0 | No interruption
|  |  | Total : | 4:26 |  |  |  | 0
Bogura Grid Circle:
Rajshahi | 132/33 kV transformer T2 | 2022-01-05 22:51 | 2022-01-06 01:56 | 3:05 | T | Tripped showing O/C relay | 0 | 0 | No interruption
| 132/33 kV transformer T3 | 2022-01-05 22:51 | 2022-01-05 23:16 | 0:25 | T |  | 5 | 2.0833 | Power interruption 22:51 to23:16
Char-Saidpur | 132/33 kV transformer T2 | 2022-01-07 20:12 | 2022-01-07 21:10 | 0:58 | T | Tripped showing E/F relay | 10 | 9.6667 | Power interruption 22:51 to23:16
Naogaon | 132/33 kV transformer T2 | 2022-01-11 22:56 | 2022-01-11 23:55 | 0:59 | T | Due to bursting of L/A | 6 | 5.9 | Power interruption
| 132/33 kV transformer T3 | 2022-01-19 09:55 | 2022-01-19 10:54 | 0:59 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Sirajganj | 132/33 kV transformer T3 | 2022-01-29 11:16 | 2022-01-29 12:42 | 1:26 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T2 | 2022-01-30 04:15 | 2022-01-30 04:35 | 0:20 | T | Tripped showing E/F relay | 0 | 0 | No interruption
|  |  | Total : | 8:12 |  |  |  | 17.65
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 111:38 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: January2022
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kaliakoir | Kaliakoir-Dhamrai 132 kV Ckt-1 | 2022-01-04 06:26 | 2022-01-04 06:36 | 0:10 | T | Tripped showing Dist. & E/F relay | 0 | 0 | No interruption
| Kaliakoir-Dhamrai 132 kV Ckt-2 | 2022-01-15 04:44 | 2022-01-15 05:02 | 0:18 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kodda 132 kV Ckt-1 | 2022-01-24 00:57 | 2022-01-24 01:42 | 0:45 | T | Tripped showing pole discrepancy | 0 | 0 | No interruption
| Kabirpur-Kodda 132 kV Ckt-1 | 2022-01-29 03:48 | 2022-01-29 04:09 | 0:21 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
|  |  | Total : | 1:34 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Madanganj | Madanganj-Bashudhara 132 kV Ckt | 2022-01-09 23:34 | 2022-01-10 03:46 | 7:10 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Keraniganj | Keraniganj-Aurahati 132 kV Ckt | 2022-01-15 09:17 | 2022-01-15 09:17 | 11:40 | E/O | Due to SF6 gas leakage | 0 | 0 | No interruption
Bhulta | Bhulta-Ghorashal 230 kV Ckt-1 | 2022-01-16 09:51 | 2022-01-16 10:23 | 0:32 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Ullon | Ullon-Rampura 132 kV Ckt-2 | 2022-01-16 08:49 | 2022-01-16 16:21 | 7:32 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Meghangaht | Meghangaht-Cumilla(N) 230 kV Ckt-2 | 2022-01-23 06:36 | 2022-01-23 06:53 | 0:17 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Ullon | Ullon-Rampura 132 kV Ckt-1 | 2022-01-24 07:23 | 2022-01-24 07:23 | 0:00 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV Ckt-1 | 2022-01-30 17:40 | 2022-01-30 17:51 | 0:11 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
|  |  | Total : | 27:22 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Hathazari | Hathazri-Abul Khair 230 kV Ckt | 2021-12-03 14:07 | 2021-12-03 20:28 | 6:21 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Juldah | Juldah-Shahmirpur 132 kV Ckt-1 | 2021-12-06 10:36 | 2021-12-06 11:01 | 0:25 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Chandraghona | Chandraghona-Kaptai 132 kV Ckt-1 | 2022-01-19 10:47 | 2022-01-19 13:29 | 2:42 | E/O | Due to red-hot maint | 0 | 0 | No interruption
|  |  | Total : | 9:28 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Ashuganj | Ashuganj-Siraganj 230 kV Ckt-1 | 2022-01-02 05:26 | 2022-01-02 08:45 | 3:19 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sylhet 132 kV Ckt | 2022-01-03 01:08 | 2022-01-03 01:31 | 0:23 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV Ckt-1 | 2022-01-03 09:11 | 2022-01-03 09:42 | 0:31 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Chaddagram 132 kV Ckt-1 | 2022-01-03 16:46 | 2022-01-03 16:46 | 0:00 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Bibiyana 230 kV Ckt-2 | 2022-01-07 08:42 | 2022-01-07 11:33 | 2:51 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Sunamganj | Sunamganj -Chatak 132 kV Ckt | 2022-01-11 06:30 | 2022-01-11 06:48 | 0:18 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Chattak | Chattak-Sunamganj 132 kV Ckt | 2022-01-11 01:22 | 2022-01-11 01:34 | 0:12 | T | Tripped showing Dist. relay. | 15 | 3 | Power interruption
Fenchuganj | Fenchuganj S/S-Sylhet 132 kV Ckt | 2022-01-13 | 2022-01-13 06:59 | 6:59 | T | Tripped showing Dist. relay. | 28 | 195.5333 | Power interruption
Cumilla(S) | Cumilla(S)-Tripura 132 kV Ckt-1 | 2022-01-14 22:36 | 2022-01-14 23:11 | 0:35 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| Cumilla(S)-Tripura 132 kV Ckt-2 | 2022-01-14 22:36 | 2022-01-14 23:32 | 0:56 | T |  | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 230 kV Ckt-1 | 2022-01-18 09:43 | 2022-01-18 12:29 | 2:46 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV Ckt-2 | 2022-01-24 02:58 | 2022-01-24 03:14 | 0:16 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Sylhet | Sylhet-Biyanibazar -Fenchuganj 132 kV Ckt | 2022-01-25 03:25 | 2022-01-25 03:51 | 0:26 | T | Tripped showing Dist. relay. | 22 | 9.5333 | Power interruption
Ashuganj | Ashuganj-B.Baria 132 kV Ckt-2 | 2022-01-26 09:11 | 2022-01-26 11:35 | 2:24 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj S/S 132 kV Ckt-1 | 2022-01-27 19:26 | 2022-01-27 19:38 | 0:12 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV Ckt-2 | 2022-01-28 08:45 | 2022-01-28 08:56 | 0:11 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| Ashuganj-Ghorashal 230 kV Ckt-2 | 2022-01-30 12:57 | 2022-01-30 13:14 | 0:17 | T | Tripped showing Dist. relay. | 0 | 0
Bbiyana | 400 kV dia-5 mid breaker | 2022-01-30 13:26 | 2022-01-30 13:26 |  | E/O | Due to oil leakge | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj S/S 132 kV Ckt | 2022-01-31 04:20 | 2022-01-31 04:32 | 0:12 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
|  |  | Total : | 22:48 |  | Unserved Energy: |  | 208.0667
Khulna Grid Circle :
Barisal | Barisal-Bhandaria 132 kV Ckt | 2022-01-09 06:58 | 2022-01-09 09:28 | 2:30 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Goalpara | Goalpara-Khulna© 132 kV Ckt-1 | 2022-01-12 13:07 | 2022-01-12 19:04 | 5:57 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Madaripir | Madaripir-Barisal (N) 132 kV Ckt-2 | 2022-01-01 02:15 | 2022-01-01 02:15 | 0:00 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Faridpur S/S | Faridpur S/S-P.S 132 kV Ckt | 2022-01-28 12:30 | 2022-01-28 12:30 | 0:00 | E/O | Due to bursting of PT | 0 | 0 | No interruption
Patuakhali | Patuakhali-Payra 132 kV Ckt-2 | 2022-01-28 19:01 | 2022-01-28 21:47 | 2:46 | E/O | Due to red-hot maint | 0 | 0
|  |  | Total : | 11:13 |  | Unserved Energy: |  | 0
HVDC Grid Circle :Nil
No interruption
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Rangpur | Rangpur-Kurigram 132 kV Ckt | 2022-01-06 16:22 | 2022-01-06 20:15 | 3:53 | T | Tripped showing Dist. relay | 24 | 93.2 | Power interruption
Bogura | Bogura -Bogura confidence -2 132 kV Ckt | 2022-01-07 00:27 | 2022-01-07 00:35 | 0:08 | T | Tripped showing O/V. relay | 0 | 0 | No interruption
| Bogura -Naogaon 132 kV Ckt-1 | 2022-01-11 12:56 | 2022-01-11 23:16 | 10:20 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Bogura (N) | Bogura (N)-Bogura Confidence -2P.P 132 kV Ckt | 2022-01-12 23:04 | 2022-01-12 23:53 | 0:49 | T | Tripped showing master trip & O/V. relay | 0 | 0 | No interruption
Mohastanghor | Mohastanghor-Palashbari 132 kV Ckt-1 | 2022-01-24 14:30 | 2022-01-24 17:23 | 2:53 | T | Due to VT fail | 0 | 0 | No interruption
|  |  | Total : | 18:03 |  | Unserved Energy: |  | 93.2
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 90:28 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: January2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bhaluka | 132/33 kV transformer T-1 | 2022-01-01 11:30 | 2022-01-01 13:06 | 1:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 132/33 kV transformer T-2 | 2022-01-01 09:07 | 2022-01-01 13:27 | 4:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132 main bus | 2022-01-01 10:56 | 2022-01-01 17:01 | 6:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132 main bus | 2022-01-02 07:43 | 2022-01-02 17:09 | 9:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV transformer T-02 | 2022-01-02 09:02 | 2022-01-02 14:43 | 5:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-1 | 2022-01-02 09:48 | 2022-01-02 14:09 | 4:21 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2022-01-02 09:34 | 2022-01-02 16:20 | 6:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 132/33 kV transformer T-5 | 2022-01-03 12:16 | 2022-01-03 12:16 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Kallyanpur | 132 kV main bus | 2022-01-03 07:35 | 2022-01-03 07:35 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2022-01-03 07:45 | 2022-01-03 17:05 | 9:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 230 kV Bus -1 | 2022-01-03 09:47 | 2022-01-03 15:08 | 5:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer Tr-03 | 2022-01-03 10:46 | 2022-01-03 12:43 | 1:57 | S/O | Due to D/W work | 0 | 0 | No interruption
Jamalpur | 230/132 kV transformer Tr-03 | 2022-01-03 09:46 | 2022-01-03 15:08 | 5:22 | S/O | Due to D/W work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV transformer T-01 | 2022-01-03 09:44 | 2022-01-03 12:07 | 2:23 | S/O | Due to protection test | 0 | 0 | No interruption
| 400/132 kV transformer T-02 | 2022-01-03 12:12 | 2022-01-03 13:22 | 1:10 | S/O |  | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-1 | 2022-01-04 09:15 | 2022-01-04 20:04 | 10:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 33 kV Bus-B | 2022-01-03 13:10 | 2022-01-03 15:33 | 2:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132 main Bus-A | 2022-01-04 07:18 | 2022-01-04 17:18 | 10:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer T-03 | 2022-01-04 10:43 | 2022-01-04 15:25 | 4:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-3 | 2022-01-04 10:02 | 2022-01-04 15:24 | 5:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132 kV reserve Bus | 2022-01-05 07:40 | 2022-01-05 17:30 | 9:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV transformer T-01 | 2022-01-05 09:27 | 2022-01-05 10:44 | 1:17 | S/O | Due to protection test | 0 | 0 | No interruption
| 400/132 kV transformer T-02 | 2022-01-05 10:46 | 2022-01-05 12:39 | 1:53 | S/O |  | 0 | 0 | No interruption
Kadda | 132/33 kV transformer T-5 |  | 2022-01-05 11:03 |  |  | After.maint work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-1 | 2022-01-05 12:18 | 2022-01-05 12:18 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132 main Bus-A | 2022-01-05 09:45 | 2022-01-05 17:24 | 7:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV transformer T-1 | 2022-01-06 07:44 | 2022-01-06 14:55 | 7:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 132/33 kV transformer T-3 | 2022-01-06 09:17 | 2022-01-06 09:17 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-A | 2022-01-06 09:40 | 2022-01-06 19:50 | 10:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-1 | 2022-01-06 09:18 | 2022-01-06 19:14 | 9:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV transformer T-2 | 2022-01-06 15:05 | 2022-01-06 16:20 | 1:15 | S/O | Due to C/M work | 60 | 75 | Power interruption
Kadda | 132/33 kV transformer T-4 with 33 kV Bus | 2022-01-06 08:50 | 2022-01-06 18:11 | 9:21 | S/O | Due to D/W work | 75 | 701.25 | Power interruption
Jamalpur | 132/33 kV transformer T-4 | 2022-01-08 09:23 | 2022-01-08 16:22 | 6:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Kadda | 132/33 kV transformers T-1 & T2 with 33 kV Bus | 2022-01-08 09:45 | 2022-01-08 15:37 | 5:52 | S/O | Due to A/M work by PBS work | 50 | 293.3333 | Power interruption
Savar | 132 kV main Bus | 2022-01-08 09:56 | 2022-01-08 16:24 | 6:28 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-01-08 09:32 | 2022-01-08 16:44 | 7:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | 230/132 kV transformer T-1 | 2022-01-09 08:44 | 2022-01-09 18:41 | 9:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer T-1 | 2022-01-09 08:50 | 2022-01-09 16:52 | 8:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-4 | 2022-01-09 09:56 | 2022-01-09 17:35 | 7:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-1 | 2022-01-09 09:40 | 2022-01-09 17:02 | 7:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | 230/132 kV transformer T-2 | 2022-01-10 10:26 | 2022-01-10 12:30 | 2:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer T-1 | 2022-01-10 08:48 | 2022-01-10 16:29 | 7:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-4 | 2022-01-10 10:03 | 2022-01-10 16:56 | 6:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | 132/33 kV transformer T-2 | 2022-01-10 09:03 | 2022-01-10 16:02 | 6:59 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2022-01-10 08:57 | 2022-01-10 15:59 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Kadda | 132/33 kV transformer T-2 | 2022-01-10 12:02 | 2022-01-10 12:02 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 |  | 2022-01-10 11:43 |  |  | After.maint work | 0 | 0 | No interruption
Aminbazar | 400/230 kV transformer T03 | 2022-01-10 13:13 | 2022-01-10 15:08 | 1:55 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirpur | 132 kV reserve Bus | 2022-01-10 10:28 | 2022-01-10 16:33 | 6:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer T-1 | 2022-01-11 08:24 | 2022-01-11 22:34 | 14:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-1 | 2022-01-11 08:55 | 2022-01-11 16:36 | 7:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV transformer T-1 | 2022-01-11 13:51 | 2022-01-11 15:06 | 1:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhaluka | 132/33 kV transformer T-1 | 2022-01-12 09:05 | 2022-01-12 17:31 | 8:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer T-1 | 2022-01-12 10:22 | 2022-01-12 17:17 | 6:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | 132 kV reserve Bus-2 | 2022-01-12 10:17 | 2022-01-12 14:53 | 4:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformers T-1 & T3 | 2022-01-12 08:44 | 2022-01-12 10:30 | 1:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132 kV reserve Bus | 2022-01-12 09:09 | 2022-01-12 13:45 | 4:36 | S/O | Due to D/W work | 0 | 0 | No interruption
Netrakona | 132/33 kV transformer T-1 | 2022-01-12 11:02 | 2022-01-12 13:36 | 2:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Satmosjid | 132/33 kV transformer T-2 | 2022-01-12 09:02 | 2022-01-12 17:01 | 7:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV transformer T-1 | 2022-01-13 07:53 | 2022-01-13 07:53 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhaluka | 132/33 kV transformer T-1 | 2022-01-13 09:02 | 2022-01-13 17:43 | 8:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer T-1 | 2022-01-13 08:17 | 2022-01-13 17:00 | 8:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132 kV main Bus | 2022-01-13 08:30 | 2022-01-13 09:29 | 0:59 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132 kV reserve Bus | 2022-01-13 09:49 | 2022-01-13 23:37 | 13:48 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2022-01-13 08:40 | 2022-01-13 23:39 | 14:59 | S/O | Due to D/W work | 0 | 0 | No interruption
Netrakona | 132/33 kV transformer T-3 with 33 kV Bus | 2022-01-14 07:45 | 2022-01-14 18:45 | 11:00 | S/O | Due to C/M work by PBS | 0 | 0 | No interruption
Mirpur | 132 kV reserve Bus | 2022-01-14 08:59 | 2022-01-14 14:18 | 5:19 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2022-01-15 07:13 | 2022-01-15 07:13 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | 132/33 kV transformer T-1 | 2022-01-15 07:41 | 2022-01-15 07:41 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Bhaluka | 132/33 kV transformer T-2 with 33 kV Bus | 2022-01-15 08:56 | 2022-01-15 18:03 | 9:07 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirpur | 132 kV main Bus | 2022-01-15 09:02 | 2022-01-15 20:20 | 11:18 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi (N) | 132/33 kV transformer T-1 | 2022-01-15 08:55 | 2022-01-15 12:35 | 3:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-1 | 2022-01-15 08:50 | 2022-01-15 16:38 | 7:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi (N) | 132/33 kV transformer T-2 | 2022-01-15 12:48 | 2022-01-15 15:45 | 2:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | 132 kV main Bus | 2022-01-15 08:40 | 2022-01-15 15:00 | 6:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 132 kV main Bus-2 | 2022-01-15 11:26 | 2022-01-15 14:46 | 3:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer T-2 | 2022-01-16 08:19 | 2022-01-16 17:16 | 8:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV transformer T-2 | 2022-01-16 09:20 | 2022-01-16 17:05 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer T01 | 2022-01-16 10:07 | 2022-01-16 22:38 | 12:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer T-2 | 2022-01-17 08:14 | 2022-01-17 17:12 | 8:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-2 | 2022-01-17 09:28 | 2022-01-17 16:37 | 7:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 230/132 kV transformer T01 | 2022-01-17 09:40 | 2022-01-17 15:10 | 5:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV transformer T-2 | 2022-01-17 09:20 | 2022-01-17 17:05 | 7:45 | S/O | Due to A/M work | 0 | 0
| 132/33 kV transformer T-3 | 2022-01-17 09:13 | 2022-01-17 15:35 | 6:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer T03 | 2022-01-18 10:05 | 2022-01-18 17:48 | 7:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer T-2 | 2022-01-18 08:35 | 2022-01-18 16:19 | 7:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-3 | 2022-01-18 08:42 | 2022-01-18 16:13 | 7:31 | S/O | Due to C/M work | 0 | 0
Jamalpur | 132/33 kV transformer T-2 | 2022-01-18 15:03 | 2022-01-18 16:13 | 1:10 | S/O | Due to replacement work at 33 kV feeder | 10 | 11.6667 | Power interruption
Bhaluka | 132/33 kV transformer T-2 | 2022-01-18 10:40 | 2022-01-18 10:50 | 0:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-1 | 2022-01-18 16:25 | 2022-01-18 16:42 | 0:17 | S/O | Due to protection test | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer T-2 | 2022-01-19 08:20 | 2022-01-19 16:51 | 8:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhaluka | 132/33 kV transformer T-2 | 2022-01-19 09:12 | 2022-01-19 17:13 | 8:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-2 | 2022-01-19 08:59 | 2022-01-19 16:28 | 7:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-2 | 2022-01-19 11:47 | 2022-01-19 12:25 | 0:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV transformer T-2 |  | 2022-01-19 14:28 |  |  | After.maint work | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer T-2 | 2022-01-19 10:54 | 2022-01-19 18:10 | 7:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer T02 | 2022-01-20 09:54 | 2022-01-20 10:37 | 0:43 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer T03 | 2022-01-20 11:21 | 2022-01-20 14:29 | 3:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Manikganj | 132/33 kV transformer T-1 | 2022-01-21 12:05 | 2022-01-21 12:05 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-A | 2022-01-22 08:44 | 2022-01-22 17:22 | 8:38 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-01-22 09:29 | 2022-01-22 17:12 | 7:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhaluka | 132/33 kV transformer T-1 | 2022-01-22 09:24 | 2022-01-22 14:00 | 4:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-3 | 2022-01-22 09:24 | 2022-01-22 09:24 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | 132/33 kV transformer T-2 | 2022-01-22 09:21 | 2022-01-22 13:10 | 3:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhaluka | 132/33 kV transformer T-1 | 2022-01-22 14:34 | 2022-01-22 17:21 | 2:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhaluka | 132 kV Bus-A |  | 2022-01-22 17:17 |  |  | new connection | 0 | 0 | No interruption
Savar | 33 kV Bus-B | 2022-01-23 10:44 | 2022-01-23 21:13 | 10:29 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi(N) | 132/33 kV transformer T-1 | 2022-01-24 09:10 | 2022-01-24 14:33 | 5:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV transformer T-1 | 2022-01-24 09:42 | 2022-01-24 14:47 | 5:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132 kV main Bus | 2022-01-25 07:45 | 2022-01-25 07:45 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi(N) | 132/33 kV transformer T-2 | 2022-01-25 09:08 | 2022-01-25 13:41 | 4:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-3 | 2022-01-25 09:10 | 2022-01-25 16:43 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-1 | 2022-01-25 09:15 | 2022-01-25 18:55 | 9:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV transformer T-3 | 2022-01-25 09:36 | 2022-01-25 17:45 | 8:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-1 | 2022-01-25 09:15 | 2022-01-25 18:55 | 9:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV transformer T-1 | 2022-01-25 09:36 | 2022-01-25 17:45 | 8:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132 kV main Bus | 2022-01-26 08:14 | 2022-01-26 21:06 | 12:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-1 | 2022-01-26 08:55 | 2022-01-26 18:40 | 9:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Keraniganj | 230/132 kV transformer T02 | 2022-01-26 10:14 | 2022-01-26 18:30 | 8:16 | S/O | Due to D/W work | 0 | 0 | No interruption
Kazla | 132/33 kV transformer T-1 | 2022-01-26 09:35 | 2022-01-26 13:26 | 3:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV transformer T-1 | 2022-01-26 09:17 | 2022-01-26 18:37 | 9:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV transformer T-1 | 2022-01-27 08:53 | 2022-01-27 17:39 | 8:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-1 | 2022-01-27 08:54 | 2022-01-27 18:42 | 9:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Satmosjid | 132/33 kV transformer T-1 | 2022-01-28 11:32 | 2022-01-28 13:19 | 1:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi(N) | 132 kV bus coupler | 2022-01-29 09:28 | 2022-01-29 14:25 | 4:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | 132/33 kV transformer T-3 with 33 kV Bus | 2022-01-29 09:20 | 2022-01-29 12:25 | 3:05 | S/O | Due to A/M work | 10 | 30.8333 | Power interruption
Savar | 33 kV Bus-A | 2022-01-29 11:02 | 2022-01-29 16:23 | 5:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-B | 2022-01-29 10:38 | 2022-01-29 17:33 | 6:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-1 | 2022-01-29 11:04 | 2022-01-29 12:10 | 1:06 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-01-29 12:15 | 2022-01-29 13:25 | 1:10 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2022-01-29 13:32 | 2022-01-29 16:15 | 2:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | 132/33 kV transformer T-4 | 2022-01-30 08:29 | 2022-01-30 08:29 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer T03 | 2022-01-30 09:59 | 2022-01-30 09:59 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-B & Bus coupler | 2022-01-30 09:34 | 2022-01-30 18:08 | 8:34 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2022-01-30 09:29 | 2022-01-30 18:05 | 8:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-3 | 2022-01-30 15:03 | 2022-01-30 16:05 | 1:02 | S/O | Due to maintenance work | 0 | 0 | No interruption
Cantonment | 132/33 kV transformer T-1 | 2022-01-31 08:16 | 2022-01-31 16:18 | 8:02 | S/O | Due to D/W work | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-2 | 2022-01-31 09:52 | 2022-01-31 09:52 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 230/132 kV transformer ATR-1 | 2022-01-31 11:03 | 2022-01-31 15:38 | 4:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-2 | 2022-01-31 11:08 | 2022-01-31 17:01 | 5:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi(N) | 132/33 kV transformer T-2 | 2022-01-31 11:29 | 2022-01-31 15:30 | 4:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Kazla | 132/33 kV transformer T-2 | 2022-01-31 11:29 | 2022-01-31 11:51 | 0:22 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 218:23 |  | Unserved Energy: |  | 1112.0833
Dhaka (South) Grid Circle :
Maniknagar | 132/33 kV transformer GT-1 | 2022-01-01 09:43 | 2022-01-01 09:43 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | 230/132 kV transformer T02 | 2022-01-01 08:05 | 2022-01-01 15:21 | 7:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | 230/132 kV transformer AT01 | 2022-01-02 07:16 | 2022-01-02 07:16 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | 230/132 kV transformer T02 | 2022-01-03 08:04 | 2022-01-03 08:04 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal | 230/132 kV transformer OAT02 | 2022-01-04 07:35 | 2022-01-04 12:15 | 4:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Sreenagar | 132/33 kV transformer T-2 | 2022-01-04 11:07 | 2022-01-04 12:50 | 1:43 | S/O | Due to SAS work | 0 | 0 | No interruption
Postogola | 132/33 kV transformers T-1 |  | 2022-01-04 13:04 |  |  | new connection | 0 | 0 | No interruption
| 132/33 kV transformers T-2 |  | 2022-01-04 13:15 |  |  |  | 0 | 0 | No interruption
Shyampur | 230/132 kV transformer T01 | 2022-01-06 07:04 | 2022-01-06 16:14 | 9:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Munshiganj | 132/33 kV transformers T-1 | 2022-01-06 08:47 | 2022-01-06 13:32 | 4:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur | 230/132 kV transformer T01 | 2022-01-06 07:04 | 2022-01-06 16:14 | 9:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Sonargaon | 132/33 kV transformers T-1 | 2022-01-07 08:42 | 2022-01-07 15:19 | 6:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | 230/132 kV transformer T03 | 2022-01-07 08:52 | 2022-01-07 18:01 | 9:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur | 230/132 kV transformer T02 | 2022-01-08 07:33 | 2022-01-08 15:33 | 8:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Narsingdi | 33 kV full Bus | 2022-01-08 07:40 | 2022-01-08 13:40 | 6:00 | S/O | Due to C/M work by PBS | 70 | 420 | Power interruption
Shyampur | 230/132 kV transformer T02 | 2022-01-08 07:33 | 2022-01-08 15:43 | 8:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Munshiganj | 132/33 kV transformers T-1 & T2 & full Bus | 2022-01-08 07:56 | 2022-01-08 14:40 | 6:44 | S/O | Due to A/M work | 44 | 296.2667 | Power interruption
Nawabganj | 132/33 kV transformer T-1 & 33 kV Bus | 2022-01-13 07:35 | 2022-01-13 07:35 | 7:44 | S/O | Due to C/M work by PBS | 0 | 0 | No interruption
Ullon | 132/33 kV transformer T-1 | 2022-01-13 09:12 | 2022-01-13 17:25 | 8:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Sonargaon | 132/33 kV transformer T-2 | 2022-01-14 08:55 | 2022-01-14 16:33 | 7:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Sitalakyha | 230/132 kV transformer T01 | 2022-01-16 09:06 | 2022-01-16 16:16 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Ullon | 132/33 kV transformer GT-2 | 2022-01-16 08:49 | 2022-01-16 16:30 | 7:41 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer GT-3 | 2022-01-17 09:10 | 2022-01-17 18:15 | 9:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Sitalakyha | 230/132 kV transformer T01 | 2022-01-17 09:06 | 2022-01-17 16:16 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | 230/132 kV transformer ATR1 | 2022-01-19 11:07 | 2022-01-19 17:15 | 6:08 | S/O | Due to D/W work | 0 | 0 | No interruption
Bhulta | 132/33 kV transformer T-2 | 2022-01-19 11:34 | 2022-01-19 15:50 | 4:16 | S/O | Due to PBS work | 0 | 0 | No interruption
Keraniganj | 230/132 kV transformer T01 | 2022-01-20 09:15 | 2022-01-20 17:52 | 8:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Kamrangirchar | 132/33 kV transformer GT-3 | 2022-01-21 09:09 | 2022-01-21 14:45 | 5:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | 230/132 kV transformer T01 | 2022-01-21 08:28 | 2022-01-21 16:38 | 8:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | 230/132 kV transformer T01 | 2022-01-21 10:18 | 2022-01-21 17:49 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | 230/132 kV transformer T01 | 2022-01-22 09:51 | 2022-01-22 17:52 | 8:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | 230/132 kV transformer T01 | 2022-01-22 10:56 | 2022-01-22 16:44 | 5:48 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | 230 kV Bus-1 | 2022-01-23 10:38 | 2022-01-23 21:11 | 10:33 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV transformer T01 | 2022-01-23 09:47 | 2022-01-23 11:25 | 1:38 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV Bus-1 | 2022-01-23 10:15 | 2022-01-23 11:19 | 1:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreenagar | 132/33 kV transformer T-1 | 2022-01-24 09:10 | 2022-01-24 17:11 | 8:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | 230/132 kV transformer T01 | 2022-01-24 11:32 | 2022-01-24 13:41 | 2:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | 230/132 kV transformer T02 | 2022-01-25 08:24 | 2022-01-25 10:47 | 2:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreenagar | 132/33 kV transformer T-2 | 2022-01-25 10:41 | 2022-01-25 17:22 | 6:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | 132/33 kV transformer GT-1 | 2022-01-26 09:15 | 2022-01-26 14:18 | 5:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Kamrangirchar | 132/33 kV transformer T-1 | 2022-01-27 09:01 | 2022-01-27 14:26 | 5:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | 230/132 kV transformer T02 | 2022-01-27 10:39 | 2022-01-27 16:55 | 6:16 | S/O | Due to D/W work | 0 | 0 | No interruption
Munshiganj | 132/33 kV transformer T-1 | 2022-01-27 09:31 | 2022-01-27 12:09 | 2:38 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-01-27 12:12 | 2022-01-27 14:09 | 1:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Sonargaon | 132/33 kV transformer T-1 | 2022-01-28 09:30 | 2022-01-28 11:43 | 2:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Matuail | 132/33 kV transformer T-2 | 2022-01-28 10:12 | 2022-01-28 16:37 | 6:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Sonargaon | 132/33 kV transformer T-2 | 2022-01-28 11:49 | 2022-01-28 14:08 | 2:19 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-01-28 14:11 | 2022-01-28 14:56 | 0:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhulta | 400/132 kV transformer T-02 | 2022-01-29 07:32 | 2022-01-29 07:32 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Keraniganj | 230/132 kV transformer T03 | 2022-01-29 15:31 | 2022-01-29 16:48 | 1:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Kamrangirchar | 132/33 kV transformer T2 | 2022-01-30 09:01 | 2022-01-30 20:00 | 10:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | 230 kV Bus | 2022-01-30 09:48 | 2022-01-30 17:03 | 7:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Kamrangirchar | 132/33 kV transformer GT1 | 2022-01-31 09:38 | 2022-01-31 19:47 | 10:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | 132/33 kV transformer T1 | 2022-01-31 13:16 | 2022-01-31 18:29 | 5:13 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 290:35 |  | Unserved Energy: |  | 716.2667
Chattogram Grid Circle :
Cox'sbazar | 132 kV Bus | 2022-01-01 06:25 | 2022-01-01 07:14 | 0:49 | S/O | Due to A/M work | 20 | 16.3333 | No interruption
| 132 kV Bus | 2022-01-02 07:33 | 2022-01-02 07:33 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirsorai | 230/33/11 kV transformer T01 | 2022-01-02 10:14 | 2022-01-02 15:27 | 5:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | 132 kV main bus | 2022-01-03 06:12 | 2022-01-03 11:49 | 5:37 | S/O | Due to D/W work | 40 | 224.6667 | Power interruption
Madunaghat | 132/33 kV transformer T-2 with 33 kV Bus | 2022-01-04 07:32 | 2022-01-04 10:09 | 2:37 | S/O | Due to D/W work | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV transformer T1 | 2022-01-04 06:45 | 2022-01-04 12:24 | 5:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Agrabad | 132/33 kV transformer T1 | 2022-01-05 12:28 | 2022-01-05 20:20 | 7:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV transformer T2 | 2022-01-06 08:13 | 2022-01-06 13:24 | 5:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | 132 kV bus-1 | 2022-01-07 07:33 | 2022-01-07 15:43 | 8:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Halishahar | 132 kV bus | 2022-01-07 10:25 | 2022-01-07 12:30 | 2:05 | S/O | Due to A/M work | 17 | 35.4167 | Power interruption
GPH | 230/132 kV transformers T01 & T02 | 2022-01-08 10:12 | 2022-01-08 15:18 | 5:06 | S/O | Due to C/M work | 0 | 0 | No interruption
T.K chemical | 132/33 kV transformer T2 | 2022-01-08 09:17 | 2022-01-08 14:23 | 5:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | 132/33 kV transformer T1 | 2022-01-14 08:12 | 2022-01-14 14:14 | 6:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahmirpur | 132/33 kV transformer T2 | 2022-01-14 08:53 | 2022-01-14 19:00 | 10:07 | S/O | Due to C/M work | 20 | 202.3333 | Power interruption
Juldah | 132 kV main bus | 2022-01-15 09:45 | 2022-01-15 14:45 | 5:00 | S/O | Due to A/M work | 8 | 40 | Power interruption
Cox'sbazar | 132/33 kV transformer T1 | 2022-01-16 08:09 | 2022-01-16 08:09 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | 230/132 kV transformer T02 | 2022-01-17 09:03 | 2022-01-17 14:06 | 5:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | 132 kV main bus-A | 2022-01-18 10:13 | 2022-01-18 14:46 | 4:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | 132 kV main bus-2 | 2022-01-19 07:45 | 2022-01-19 07:54 | 0:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | 132 kV bus-B | 2022-01-19 09:30 | 2022-01-19 13:39 | 4:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahmirpur | 132 kV main Bus | 2022-01-21 09:40 | 2022-01-21 13:48 | 4:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Halishahar | 132/33 kV transformer T3 | 2022-01-21 15:10 | 2022-01-21 19:48 | 4:38 | S/O | Due to D/W work | 0 | 0 | No interruption
GPH | 230/132 kV transformer T01 | 2022-01-22 12:30 | 2022-01-22 15:20 | 2:50 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV transformer T02 | 2022-01-22 19:06 | 2022-01-22 20:41 | 1:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | 132/33 kV transformer T1 | 2022-01-25 07:25 | 2022-01-25 09:43 | 2:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Khagrachari | 132/33 kV transformer T2 | 2022-01-27 09:20 | 2022-01-27 17:20 | 8:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | 132 kV bus-1 | 2022-01-28 08:41 | 2022-01-28 10:18 | 1:37 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230/132 kV transformer T02 | 2022-01-28 08:41 | 2022-01-28 10:15 | 1:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Khagrachari | 132/33 kV transformer T2 | 2022-01-28 09:03 | 2022-01-28 17:50 | 8:47 | S/O | Due to protection test | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-01-29 09:12 | 2022-01-29 10:18 | 1:06 | S/O | Due to D/W work | 12 | 13.2 | Power interruption
| 132/33 kV transformer T2 | 2022-01-29 09:12 | 2022-01-29 13:40 | 4:28 | S/O | Due to D/W work | 0 | 0
| 132 kV main Bus-2 | 2022-01-31 10:35 | 2022-01-31 15:40 | 5:05 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 134:34 |  | Unserved Energy : |  | 531.95
Cumilla Grid Circle :
Chowmuhani | 132/33 kV transformer T3 | 2022-01-01 10:18 | 2022-01-01 11:50 | 1:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Sunamganj | 132/33 kV transformer T-1 | 2022-01-01 09:39 | 2022-01-01 09:39 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV transformer T-2 | 2022-01-02 11:14 | 2022-01-02 17:47 | 6:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Comilla(S) | 132/33 kV transformer T1 |  | 2022-01-15 11:17 |  |  | After maint.work | 0 | 0 | No interruption
Daudkandi | 132/33 kV transformer T1 | 2022-01-15 08:03 | 2022-01-15 14:22 | 6:19 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-01-15 14:24 | 2022-01-15 16:26 | 2:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Comilla(S) | 132/33 kV transformer T4 | 2022-01-16 09:50 | 2022-01-16 09:50 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Comilla(N) | 230/132 kV transformer T02 | 2022-01-17 09:35 | 2022-01-17 13:13 | 3:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV transformer T4 | 2022-01-21 11:04 | 2022-01-21 16:33 | 5:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Comilla(S) | 132/33 kV transformer T2 | 2022-01-22 08:51 | 2022-01-22 11:19 | 2:28 | S/O | Due to C/M work by PDB | 0 | 0 | No interruption
Sreemongal | 132/33 kV transformer T-1 |  | 2022-01-22 08:51 |  |  | After maint.work | 0 | 0 | No interruption
Kachua | 132/33 kV transformer T-1 | 2022-01-25 09:02 | 2022-01-25 15:14 | 6:12 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-01-25 15:18 | 2022-01-25 18:26 | 3:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Kulaura | 132/33 kV transformer T-1 with 33 kV Bus | 2022-01-29 08:58 | 2022-01-29 12:50 | 3:52 | S/O | Due to A/M work | 4 | 15.4667 | Power interruption
Fenchuganj | 132 kV Bus-2 | 2022-01-29 09:37 | 2022-01-29 14:13 | 4:36 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-01-29 09:31 | 2022-01-29 14:14 | 4:43 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer T02 | 2022-01-31 09:19 | 2022-01-31 10:08 | 0:49 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 51:21 |  | Unserved Energy : |  | 15.4667
Khulna Grid Circle :
Barisal | 132/33 kV transformer T4 | 2022-01-01 09:39 | 2022-01-01 12:21 | 2:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Payra | 400 kV Bus-2 | 2022-01-03 08:20 | 2022-01-03 08:20 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal | 132/33 kV transformer T4 | 2022-01-04 09:12 | 2022-01-04 16:44 | 7:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | 132 kV Bus-B |  | 2022-01-04 09:15 |  | S/O | After maint.work | 0 | 0 | No interruption
Barisal | 132/33 kV transformer T4 | 2022-01-04 09:44 | 2022-01-04 17:35 | 7:51 | S/O | Due to D/W work | 0 | 0 | No interruption
Madaripur | 132 kV Bus-B | 2022-01-05 12:20 | 2022-01-05 16:50 | 4:30 | S/O | Due to D/W work | 0 | 0 | No interruption
Payra | 132 kV Bus-1 & 2 | 2022-01-07 09:31 | 2022-01-07 21:14 | 11:43 | S/O | Due to D/W work | 0 | 0 | No interruption
Satkhira | 132 kV Bus-B | 2022-01-10 07:28 | 2022-01-10 07:28 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132 kV CB | 2022-01-10 07:30 | 2022-01-10 07:30 | 0:00 |  |  | 0 | 0 | No interruption
Rampur | 132/33 kV transformer T1 |  | 2022-01-12 16:16 |  |  | new connection | 0 | 0 | No interruption
Khulna (S) | 132/33 kV transformer T3 with 33 kV Bus | 2022-01-15 09:52 | 2022-01-15 11:09 | 1:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | 132 kV Bus-B | 2022-01-16 10:55 | 2022-01-16 10:55 |  | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | 132/33 kV transformer T5 | 2022-01-18 10:40 | 2022-01-18 18:52 | 8:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Barisal(O) | 132 kV Bus-A | 2022-01-22 07:35 | 2022-01-22 21:56 | 14:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampur | 132/33 kV transformer T1 |  | 2022-01-22 15:13 |  |  | After maint.work | 0 | 0 | No interruption
Bhandaria | 132 kV Bus | 2022-01-23 07:37 | 2022-01-23 07:37 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Matarbari | 132/33 kV transformer T2 | 2022-01-23 08:59 | 2022-01-23 13:36 | 4:37 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-01-23 14:05 | 2022-01-23 14:31 | 0:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal(O) | 132/33 kV transformer T4 | 2022-01-24 11:18 | 2022-01-24 17:31 | 6:13 | S/O | Due to D/W work | 0 | 0 | No interruption
Golapara | 132/33 kV transformer T6 | 2022-01-25 11:43 | 2022-01-25 16:51 | 5:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Narail | 132/33 kV transformer T1 | 2022-01-26 10:45 | 2022-01-26 18:19 | 7:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Bhandaria | 132/33 kV transformer T2 | 2022-01-27 07:44 | 2022-01-27 14:34 | 6:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Narail | 132/33 kV transformer T2 | 2022-01-27 10:13 | 2022-01-27 17:14 | 7:01 | S/O | Due to D/W work | 0 | 0 | No interruption
Payra | 400/132 kV transformer T01 | 2022-01-28 05:54 | 2022-01-28 05:54 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| 400/132 kV transformer T02 | 2022-01-28 07:52 | 2022-01-28 07:52 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Narail | 132/33 kV transformer T2 | 2022-01-29 11:11 | 2022-01-29 16:00 | 4:49 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-01-29 16:06 | 2022-01-29 17:39 | 1:33 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-01-30 09:40 | 2022-01-30 11:00 | 1:20 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulna© | 132/33 kV transformer T2 | 2022-01-30 13:01 | 2022-01-30 13:44 | 0:43 | S/O | Due to Oil sample collection | 0 | 0 | No interruption
| 132/33 kV transformer T3 | 2022-01-30 13:44 | 2022-01-30 15:38 | 1:54 | S/O |  | 0 | 0 | No interruption
Madaripur | 132/33 kV transformer T3 | 2022-01-31 12:09 | 2022-01-31 13:49 | 1:40 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 107:56 |  | Unserved Energy : |  | 0
HVDC Grid Circle
Jashore | 132/33 kV transformer T1 | 2022-01-03 08:16 | 2022-01-03 13:35 | 5:19 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-01-04 08:04 | 2022-01-04 13:12 | 5:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | 230/132 kV transformer T-02 | 2022-01-08 08:26 | 2022-01-08 15:33 | 7:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenaidah | 132 kV Bus-1 & 2 | 2022-01-08 08:59 | 2022-01-08 17:01 | 8:02 | S/O | Due to D/W work | 0 | 0 | No interruption
Bheramara | 132/33 kV transformer T4 | 2022-01-11 09:03 | 2022-01-11 16:46 | 7:43 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bheramara HVDC 400 kV filer bus-2 | 2022-01-11 10:14 | 2022-01-11 16:16 | 6:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Pabna | 132/33 kV transformer T3 | 2022-01-11 12:02 | 2022-01-11 15:03 | 3:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Jashore | 132/33 kV transformer T1With 33 kV Bus | 2022-01-12 08:49 | 2022-01-12 09:29 | 0:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Bottail | 132 kV full Bus | 2022-01-15 11:13 | 2022-01-15 17:51 | 6:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Ishurdi | 230/132 kV transformer T-03 | 2022-01-20 09:20 | 2022-01-20 10:54 | 1:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Bottail | 132 kV Bus-A | 2022-01-22 08:10 | 2022-01-22 15:53 | 7:43 | S/O | Due to C/M work | 50 | 385.8333 | No interruption
Ishurdi | 230 kV Bus-1 | 2022-01-22 09:42 | 2022-01-22 17:05 | 7:23 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer T-03 |  | 2022-01-22 19:19 |  |  | After maint.work | 0 | 0 | No interruption
Baghabari | 230/132 kV transformer T-01 | 2022-01-24 08:12 | 2022-01-24 08:12 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenaidah(N) | 230/132 kV transformer T-01 | 2022-01-26 10:24 | 2022-01-26 19:29 | 9:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Baghabari | 230/132 kV transformer T-02 | 2022-01-27 08:33 | 2022-01-27 17:45 | 9:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenaidah(N) | 230/132 kV transformer T-02 | 2022-01-27 09:34 | 2022-01-27 17:52 | 8:18 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230 kV Bus-2 | 2022-01-27 15:49 | 2022-01-27 15:49 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Bottail | 132/33 kV transformer T2 | 2022-01-27 16:03 | 2022-01-27 17:30 | 1:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Pabna | 132 kV Bus | 2022-01-28 08:32 | 2022-01-28 14:41 | 6:09 | S/O | Due to A/M work | 30 | 184.5 | Power interruption
|  |  | Total : | 100:31 |  | Unserved Energy : |  | 570.3333
Bogura Grid Circle:
Thakurgaon | 132/33 kV transformer T3 | 2022-01-02 08:45 | 2022-01-02 19:05 | 10:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhangura | 132/33 kV transformer T1 | 2022-01-05 12:27 | 2022-01-05 13:30 | 1:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T2 | 2022-01-08 09:25 | 2022-01-08 16:47 | 7:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | 132/33 kV transformer T2 | 2022-01-09 11:49 | 2022-01-09 17:26 | 5:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T2 |  | 2022-01-12 14:58 |  | S/O | After maint.work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV transformer T1 with 33 kV Bus | 2022-01-15 07:48 | 2022-01-15 13:59 | 6:11 |  |  | 0 | 0 | No interruption
Naogaon | 33 kV Bus-2 | 2022-01-15 09:15 | 2022-01-15 13:25 | 4:10 | S/O | Due to C/M work | 5 | 20.8333 | Power interruption
Bhangura | 132/33 kV transformer T1 | 2022-01-16 08:45 | 2022-01-16 11:26 | 2:41 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-01-16 12:07 | 2022-01-16 12:42 | 0:35 | S/O | Due to replacement work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-01-17 09:02 | 2022-01-17 12:07 | 3:05 | S/O | Due to A/M work | 0 | 0 | Power interruption
| 132/33 kV transformer T2 | 2022-01-19 08:55 | 2022-01-19 12:46 | 3:51 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-01-20 09:06 | 2022-01-20 12:13 | 3:07 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-01-20 12:18 | 2022-01-20 13:01 | 0:43 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-01-20 08:55 | 2022-01-20 12:46 | 3:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV transformer T2 | 2022-01-20 13:46 | 2022-01-20 15:20 | 1:34 | S/O | Due to C/M work | 15 | 23.5 | Power interruption
Niyamatpur | 132/33 kV transformer T1 | 2022-01-20 14:41 | 2022-01-20 18:10 | 3:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Barapukuria | 132/33 kV transformer T4 | 2022-01-22 16:10 | 2022-01-22 17:48 | 1:38 | S/O | Due to 33 kV feeder maint.work | 25 | 40.8333 | Power interruption
Naogaon | 132/33 kV transformers T1,T2 T3 with 33 kV Bus | 2022-01-29 09:17 | 2022-01-29 14:35 | 5:18 | S/O |  | 85 | 450.5 | Power interruption
|  |  | Total : | 64:35 |  | Unserved Energy : |  | 535.6667
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 967:55 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/5 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | Tongi-Tongi Milgate 132 kV Ckt-1 | 2022-01-01 15:58 | 2022-01-01 16:14 | 0:16 | S/O | Due to A/M work | 0 | 0 | No interruption
| Tongi-Tongi Milgate 132 kV Ckt-2 | 2022-01-01 16:17 | 2022-01-01 17:02 | 0:45 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV Ckt-2 | 2022-01-02 10:21 | 2022-01-02 16:41 | 6:20 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Meghnaghat 230 kV Ckt-2 | 2022-01-03 09:57 | 2022-01-03 16:16 | 6:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh -Mymensingh Solar P.P 132 kV Ckt | 2022-01-04 07:11 | 2022-01-04 07:11 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV Ckt-1 | 2022-01-04 08:58 | 2022-01-04 17:20 | 8:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-1 | 2022-01-04 09:27 | 2022-01-04 13:56 | 4:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Saver | Saver-Manikganj P/S 132 kV Ckt-2 | 2022-01-04 09:07 | 2022-01-04 16:40 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV Ckt-1 | 2022-01-05 09:30 | 2022-01-05 13:40 | 4:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Tongi (N) 132 kV Ckt-1 | 2022-01-05 09:11 | 2022-01-05 10:33 | 1:22 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV Ckt-2 | 2022-01-05 13:44 | 2022-01-05 17:17 | 3:33 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh -Netrakona 132 kV Ckt-1 | 2022-01-06 09:16 | 2022-01-06 13:36 | 4:20 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh -Mymensingh Solar P.P 132 kV Ckt | 2022-01-06 08:43 | 2022-01-06 22:27 | 13:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Saver | Saver-Manikganj P/S 162 MW 132 kV Ckt-2 | 2022-01-06 10:11 | 2022-01-06 16:28 | 6:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh -Netrakona 132 kV Ckt-2 | 2022-01-06 13:45 | 2022-01-06 19:30 | 5:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-1 | 2022-01-08 07:47 | 2022-01-08 18:38 | 10:51 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Agargaon 230 kV Ckt-2 | 2022-01-08 11:22 | 2022-01-08 16:57 | 5:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh -Bhaluka 132 kV Ckt-2 | 2022-01-08 09:26 | 2022-01-08 17:28 | 8:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-1 | 2022-01-09 07:02 | 2022-01-09 18:07 | 11:05 | S/O | Due to D/W work | 0 | 0 | No interruption
| Aminbazar-Kaliakoir 230 kV Ckt-2 | 2022-01-09 09:55 | 2022-01-09 16:53 | 6:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakoir 132 kV Ckt-1 | 2022-01-09 08:27 | 2022-01-09 18:00 | 9:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh -Bhaluka 132 kV Ckt-2 | 2022-01-09 09:19 | 2022-01-09 16:51 | 7:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV Ckt-2 | 2022-01-10 09:25 | 2022-01-10 17:19 | 7:54 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Mirpur 132 kV Ckt-1 | 2022-01-10 09:53 | 2022-01-10 16:35 | 6:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakoir 132 kV Ckt-1 | 2022-01-10 08:28 | 2022-01-10 17:03 | 8:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydepur | Joydepur-Kodda 132 kV Ckt-1 & 2 | 2022-01-10 09:33 | 2022-01-10 16:08 | 6:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh -Bhaluka 132 kV Ckt-2 | 2022-01-10 09:29 | 2022-01-10 16:37 | 7:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-2 | 2022-01-11 06:59 | 2022-01-11 17:13 | 10:14 | S/O | Due to D/W work | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakoir 132 kV Ckt-1 | 2022-01-11 07:45 | 2022-01-11 19:56 | 12:11 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Agargaon 230 kV Ckt-2 | 2022-01-11 08:55 | 2022-01-11 11:19 | 2:24 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Kaliakoir 230 kV Ckt-2 | 2022-01-11 09:08 | 2022-01-11 17:01 | 7:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh -Bhaluka 132 kV Ckt-2 | 2022-01-11 09:13 | 2022-01-11 16:18 | 7:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Agargaon 230 kV Ckt-2 | 2022-01-11 11:30 | 2022-01-11 15:26 | 3:56 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Kaliyanpur 132 kV Ckt-1 | 2022-01-12 09:21 | 2022-01-12 11:59 | 2:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamrai 132 V Ckt-1 | 2022-01-12 08:40 | 2022-01-12 17:55 | 9:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV Ckt-1 | 2022-01-12 09:41 | 2022-01-12 17:26 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kallyanpur-Lalbagh 132 kV Ckt-2 | 2022-01-12 08:27 | 2022-01-12 09:32 | 1:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-2 | 2022-01-12 08:16 | 2022-01-12 20:32 | 12:16 | S/O | Due to D/W work | 0 | 0 | No interruption
| Aminbazar-Kaliyanpur 132 kV Ckt-2 | 2022-01-12 12:18 | 2022-01-12 14:50 | 2:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV Ckt-1 | 2022-01-13 07:32 | 2022-01-13 07:32 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-2 | 2022-01-13 07:33 | 2022-01-13 07:33 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakoir 132 kV Ckt-1 | 2022-01-13 07:21 | 2022-01-13 07:21 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamrai 132 V Ckt-1 | 2022-01-13 08:40 | 2022-01-13 17:55 | 9:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-2 | 2022-01-14 08:08 | 2022-01-14 16:36 | 8:28 | S/O | Due to D/W work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV Ckt-2 | 2022-01-14 09:27 | 2022-01-14 13:16 | 3:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-1 | 2022-01-15 07:00 | 2022-01-15 20:29 | 13:29 | S/O | Due to D/W work | 0 | 0 | No interruption
Tangail | Tangail -Kaliakoir 132 kV Ckt-1 & 2 | 2022-01-15 08:40 | 2022-01-15 15:00 | 6:20 | S/O | Due to A/M work | 0 | 0 | No interruption
| Tangail-Mymensingh RPCL 132 kV Ckt-1 | 2022-01-15 07:48 | 2022-01-15 15:30 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
| Tangail-Mymensingh RPCL 132 kV Ckt-2 | 2022-01-15 08:16 | 2022-01-15 15:33 | 7:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakoir 132 kV Ckt-2 | 2022-01-16 07:07 | 2022-01-16 17:16 | 10:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Lalbagh | Lalbagh-Kallyanpur 132 kV Ckt-2 | 2022-01-16 07:13 | 2022-01-16 19:30 | 12:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV Ckt-1 | 2022-01-17 07:14 | 2022-01-17 09:28 | 2:14 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Manikganj 132 kV Ckt-1 | 2022-01-17 07:33 | 2022-01-17 07:33 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV Ckt-1 | 2022-01-17 07:44 | 2022-01-17 15:57 | 8:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV Ckt-2 | 2022-01-17 09:32 | 2022-01-17 10:59 | 1:27 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Manikganj P.P kV Ckt-2 | 2022-01-17 10:12 | 2022-01-17 11:14 | 1:02 | S/O | Due to C/M work | 0 | 0 | No interruption
| Aminbazar-Meghnaghat 230 kV Ckt-2 | 2022-01-17 09:36 | 2022-01-17 12:54 | 3:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-2 | 2022-01-18 10:05 | 2022-01-18 16:01 | 5:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV Ckt-2 | 2022-01-18 09:28 | 2022-01-18 11:25 | 1:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV Ckt | 2022-01-18 10:13 | 2022-01-18 10:51 | 0:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Kaliakoir 230 kV Ckt-2 | 2022-01-18 11:15 | 2022-01-18 17:41 | 6:26 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-2 | 2022-01-18 12:52 | 2022-01-18 14:52 | 2:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Keraniganj 230 kV Ckt-2 | 2022-01-18 15:02 | 2022-01-18 16:08 | 1:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakoir 132 kV Ckt-2 | 2022-01-19 06:55 | 2022-01-19 06:55 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV Ckt-2 | 2022-01-19 10:26 | 2022-01-19 20:05 | 9:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 3rd phase 132 kV Ckt | 2022-01-19 10:10 | 2022-01-19 12:09 | 1:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Kodda Summit 230 kV Ckt | 2022-01-19 10:35 | 2022-01-19 14:55 | 4:20 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-1 | 2022-01-19 13:44 | 2022-01-19 14:25 | 0:41 | S/O | Due to protection test | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamrai 132 V Ckt-2 | 2022-01-20 07:18 | 2022-01-20 07:18 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV Ckt-2 | 2022-01-20 10:44 | 2022-01-20 13:28 | 2:44 | S/O | Due to relay test | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV Ckt-2 | 2022-01-20 10:44 | 2022-01-20 10:44 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh -Sutiakhali 50 MW 132 kV Ckt | 2022-01-22 07:03 | 2022-01-22 19:55 | 12:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Aminbazar 230 kV Ckt-2 | 2022-01-22 09:35 | 2022-01-22 19:18 | 9:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh -Bhaluka 132 kV Ckt-2 | 2022-01-22 14:36 | 2022-01-22 17:30 | 2:54 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh S/S-Mymensingh Solar 132 kV Ckt | 2022-01-23 07:01 | 2022-01-23 07:01 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Aminbazar 230 kV Ckt-2 | 2022-01-23 09:12 | 2022-01-23 17:35 | 8:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh -RPCL 132 kV Ckt-1 | 2022-01-23 09:48 | 2022-01-23 13:48 | 4:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh -RPCL 132 kV Ckt-2 | 2022-01-23 14:12 | 2022-01-23 16:50 | 2:38 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh S/S-Mymensingh Solar 132 kV Ckt | 2022-01-24 07:10 | 2022-01-24 07:10 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV Ckt-2 | 2022-01-24 09:32 | 2022-01-24 14:17 | 4:45 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kaliakoir-Aminbazar 230 kV Ckt-2 | 2022-01-24 09:35 | 2022-01-24 16:28 | 6:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh S/S-Mymensingh Solar 132 kV Ckt | 2022-01-25 06:55 | 2022-01-25 06:55 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Aminbazar 230 kV Ckt-1 | 2022-01-25 08:19 | 2022-01-25 13:00 | 4:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV Ckt-2 | 2022-01-25 08:34 | 2022-01-25 15:18 | 6:44 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kaliakoir-Aminbazar 230 kV Ckt-2 | 2022-01-25 09:33 | 2022-01-25 20:01 | 10:28 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kaliakoir-Kodda 300 MW P/P 230 kV Ckt | 2022-01-25 09:48 | 2022-01-25 20:14 | 10:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-1 | 2022-01-25 09:53 | 2022-01-25 16:03 | 6:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Aminbazar 230 kV Ckt-2 | 2022-01-25 13:01 | 2022-01-25 16:36 | 3:35 | S/O | Due to C/M work | 0 | 0 | No interruption
| Kallyanpur-Lalbagh 132 kV Ckt-1 | 2022-01-26 08:18 | 2022-01-26 21:10 | 12:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Ghorashal 230 kV Ckt-2 | 2022-01-26 09:08 | 2022-01-26 16:37 | 7:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV Ckt-1 | 2022-01-26 09:23 | 2022-01-26 17:40 | 8:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Nawabganj 132 kV Ckt-1 | 2022-01-26 16:28 | 2022-01-26 17:13 | 0:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Aminbazar 230 kV Ckt-1 | 2022-01-27 09:13 | 2022-01-27 18:17 | 9:04 | S/O | Due to C/M work | 0 | 0 | No interruption
| Kabirpur-Tongi 230 kV Ckt-2 | 2022-01-27 08:41 | 2022-01-27 18:14 | 9:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-RPCL P.P 132 KV Ckt-2 | 2022-01-29 09:39 | 2022-01-29 17:25 | 7:46 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh -Bhaluka 132 kV Ckt-1 | 2022-01-29 09:54 | 2022-01-29 18:16 | 8:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tongi 230 kV Ckt-2 | 2022-01-29 10:27 | 2022-01-29 16:37 | 6:10 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kaliakoir-Aminbazar 230 kV Ckt-1 | 2022-01-29 09:50 | 2022-01-29 16:47 | 6:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | Kodda-Rajendrapur 132 kV Ckt-1 | 2022-01-29 09:23 | 2022-01-29 17:27 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV Ckt | 2022-01-29 10:00 | 2022-01-29 13:25 | 3:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV Ckt-1 | 2022-01-29 10:58 | 2022-01-29 17:34 | 6:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Aminbazar 230 kV Ckt-1 | 2022-01-30 09:29 | 2022-01-30 16:42 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kaliakoir-Tongi 230 kV Ckt-2 | 2022-01-30 09:35 | 2022-01-30 16:44 | 7:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | Kodda-Rajendrapur 132 kV Ckt-1 | 2022-01-30 09:31 | 2022-01-30 16:02 | 6:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh -Jamalpur 132 kV Ckt-2 | 2022-01-31 11:10 | 2022-01-31 16:55 | 5:45 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh -Kishoreganjn 132 kV Ckt-2 | 2022-01-31 11:30 | 2022-01-31 16:56 | 5:26 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 603:01 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Haripur | Haripur S/S -Haripur P/S 132 kV Ckt | 2022-01-01 10:03 | 2022-01-01 17:06 | 7:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Keraniganj 230 kV Ckt | 2022-01-01 09:08 | 2022-01-01 16:02 | 6:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Sonargaon 132 kV Ckt-1 | 2022-01-02 10:40 | 2022-01-02 13:42 | 3:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Sreenagar 132 kV Ckt-1 | 2022-01-03 12:18 | 2022-01-03 13:30 | 1:12 | S/O | Due to SAS Work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Joydevpur 132 kV Ckt-2 | 2022-01-04 06:56 | 2022-01-04 06:56 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Siddhirganj 335 MW 230 kV Ckt |  | 2022-01-04 11:57 |  | S/O | After maint.work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 230 kV Ckt-2 | 2022-01-06 03:42 | 2022-01-06 03:42 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | Bhulta-Haripur 132 kV Ckt | 2022-01-06 09:01 | 2022-01-06 15:47 | 6:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Ullon | Ullon-Siddhirganj 132 kV Ckt-1 | 2022-01-07 09:58 | 2022-01-07 18:21 | 8:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Narsinghdi | Narsinghdi-Bhulta 132 kV Ckt-1 | 2022-01-08 09:27 | 2022-01-08 13:40 | 4:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Haripur 132 kV Ckt-1 | 2022-01-10 09:07 | 2022-01-10 17:17 | 8:10 | S/O | Due to A/M work | 0 | 0 | No interruption
| Siddhirganj-Haripur 132 kV Ckt-1 | 2022-01-11 09:48 | 2022-01-11 14:39 | 4:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Aftabnagar | Aftabnagar-Rumpura 12 kV Ckt-2 | 2022-01-11 12:25 | 2022-01-12 16:41 | 28:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Rumpura | Rumpura-Ullon 132 kV Ckt-2 | 2022-01-12 07:56 | 2022-01-12 16:54 | 8:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Haripur 132 kV Ckt-2 | 2022-01-12 09:13 | 2022-01-12 16:55 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Shitalakyha 132 kV Ckt |  | 2022-01-12 16:45 |  | S/O | After maint.work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV Ckt-1 | 2022-01-12 14:31 | 2022-01-12 16:18 | 1:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Madanganj 132 kV Ckt | 2022-01-15 09:56 | 2022-01-15 15:36 | 5:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj 132 kV Ckt-2 | 2022-01-16 08:29 | 2022-01-16 19:33 | 11:04 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ghorashal GIS-Ghorashal AIS 230 kV Ckt-2 | 2022-01-17 15:52 | 2022-01-17 15:52 | 0:00 |  | After maint.work |  | 0 | No interruption
Rampura | Rampura-Moghbazar 132 kV Ckt-1 | 2022-01-18 07:34 | 2022-01-18 07:34 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Fatullah 132 kV Ckt | 2022-01-18 10:35 | 2022-01-18 15:22 | 4:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Sreenagar 132 kV Ckt-2 | 2022-01-18 10:41 | 2022-01-18 17:51 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Mothered 132 kV Ckt-1 | 2022-01-19 09:00 | 2022-01-19 20:40 | 11:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Ullon | Ullon-Haripur 132 kV Ckt | 2022-01-19 09:25 | 2022-01-19 16:53 | 7:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Mothered 132 kV Ckt-1 | 2022-01-20 08:26 | 2022-01-20 19:46 | 11:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Ullon | Ullon-Siddhirganj 132 kV Ckt-1 | 2022-01-20 09:16 | 2022-01-20 17:44 | 8:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 230 kV Ckt-2 | 2022-01-21 10:25 | 2022-01-21 12:00 | 1:35 | S/O | Due to A/M work | 0 | 0 | No interruption
| Haripur-Madanganj 132 kV Ckt | 2022-01-21 12:28 | 2022-01-21 15:00 | 2:32 | S/O | Due to C/M work | 0 | 0 | No interruption
| Haripur-Narsingdi 132 kV Ckt | 2022-01-21 15:48 | 2022-01-21 17:01 | 1:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Tongi 230 kV Ckt-2 | 2022-01-22 08:32 | 2022-01-22 17:44 | 9:12 | S/O | Due to D/W work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Haripur 230 kV Ckt-2 | 2022-01-23 07:18 | 2022-01-23 21:07 | 13:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Tongi 230 kV Ckt-2 | 2022-01-23 08:29 | 2022-01-23 16:47 | 8:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Ullon | Ullon-Rampura 132 kV Ckt-1 | 2022-01-23 09:30 | 2022-01-23 17:31 | 8:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Nawabganj 132 kV Ckt-2 | 2022-01-23 16:22 | 2022-01-23 16:36 | 0:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 230 kV Ckt-2 | 2022-01-23 19:47 | 2022-01-23 20:42 | 0:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj 230 kV Ckt-1 | 2022-01-24 07:21 | 2022-01-24 07:21 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ghorashal-Tongi 230 kV Ckt-2 | 2022-01-24 08:30 | 2022-01-24 15:48 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Haripur 230 kV Ckt-2 | 2022-01-24 10:11 | 2022-01-24 19:36 | 9:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Ullon 132 kV Ckt |  | 2022-01-24 08:48 |  | S/O | After maint.work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Tongi 230 kV Ckt-2 | 2022-01-25 08:44 | 2022-01-25 15:39 | 6:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Mothered 132 kV Ckt-2 | 2022-01-25 08:51 | 2022-01-25 20:32 | 11:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Haripur 230 kV Ckt-2 | 2022-01-25 09:53 | 2022-01-25 19:07 | 9:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Keraniganj 230 kV Ckt-1 | 2022-01-25 15:08 | 2022-01-25 15:21 | 0:13 | S/O | Due to D/W work | 0 | 0 | No interruption
| Hasnabad-Keraniganj 230 kV Ckt-2 | 2022-01-25 15:26 | 2022-01-25 15:41 | 0:15 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi-Kaliakoir 230 kV Ckt-2 | 2022-01-26 10:09 | 2022-01-26 17:05 | 6:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Meghnaghat-Meghnaghat 230 kV Ckt-2 | 2022-01-26 12:52 | 2022-01-26 19:44 | 6:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Madanganj | Madanganj-Munshiganj 132 kV Ckt-2 | 2022-01-27 12:14 | 2022-01-27 17:25 | 5:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Mothertek 132 kV Ckt-1 | 2022-01-27 10:59 | 2022-01-27 14:52 | 3:53 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 132 kV Ckt- | 2022-01-27 10:01 | 2022-01-27 15:54 | 5:53 | S/O | Due to D/W work | 0 | 0 | No interruption
Madanganj | Madanganj-Munshiganj 132 kV Ckt-1 | 2022-01-27 15:28 | 2022-01-27 17:29 | 2:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Ullon 132 kV Ckt-1 |  | 2022-01-27 19:01 |  |  | After maint.work | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV Ckt-1 | 2022-01-30 10:33 | 2022-01-30 19:30 | 8:57 | S/O | Due to C/M work | 0 | 0 | No interruption
| Tongi-Tongi P/S 132 kV Ckt | 2022-01-30 10:41 | 2022-01-30 15:31 | 4:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur-Meghnaghat 230 kV Ckt-2 | 2022-01-30 11:13 | 2022-01-30 17:39 | 6:26 | S/O | Due to relay test | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV Ckt-1 | 2022-01-30 17:40 | 2022-01-30 17:51 | 0:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Aminmbazar 230 kV Ckt-2 | 2022-01-31 09:34 | 2022-01-31 15:53 | 6:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV Ckt-1 | 2022-01-31 11:45 | 2022-01-31 20:07 | 8:22 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 321:35 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-2 | 2022-01-01 06:25 | 2022-01-01 07:14 | 0:49 | S/O | Due to A/M work | 0 | 0 | No interruption
| Dohazari-Cox'sbazar 132 kV Ckt-2 | 2022-01-01 11:56 | 2022-01-01 16:43 | 4:47 | S/O | Due to D/W work | 32 | 153.0667 | Power interruption
Hathazari | Hathazari-Barierhat 132 kV Ckt-2 | 2022-01-01 09:32 | 2022-01-01 16:12 | 6:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV Ckt-1 | 2022-01-02 08:15 | 2022-01-02 14:52 | 6:37 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-1 | 2022-01-02 11:27 | 2022-01-02 12:19 | 0:52 | S/O | Due to D/W work | 0 | 0 | No interruption
| Dohazari-Matarbari-Cox'sbazar 132 kV Ckt | 2022-01-03 06:01 | 2022-01-03 07:10 | 1:09 | S/O | Due to D/W work | 80 | 92 | Power interruption
| Dohazari-Sikalbaha 132 kV Ckt-2 | 2022-01-03 06:07 | 2022-01-03 06:58 | 0:51 | S/O | Due to D/W work | 0 | 0 | No interruption
Bakulia | Bakulia-Khulshi 132 kV Ckt-1 | 2022-01-03 08:32 | 2022-01-03 14:40 | 6:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroaulia 132 kV Ckt-1 | 2022-01-03 09:51 | 2022-01-03 14:43 | 4:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Khulshi 132 kV Ckt-1 | 2022-01-04 08:36 | 2022-01-04 14:59 | 6:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroaulia 132 kV Ckt-1 | 2022-01-04 08:25 | 2022-01-04 15:40 | 7:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Khulshi 132 kV Ckt-1 | 2022-01-05 08:32 | 2022-01-05 15:04 | 6:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Kaptai 132 kV Ckt-1 | 2022-01-05 09:17 | 2022-01-05 15:47 | 6:30 | S/O | Due to A/M work | 0 | 0 | No interruption
| Hathazari-Kaptai 132 kV Ckt-2 | 2022-01-06 09:19 | 2022-01-06 15:54 | 6:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Raozan | Raozan-Hathazari 230 kV Ckt-1 | 2022-01-08 09:22 | 2022-01-08 16:16 | 6:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Modern 132 kV Ckt | 2022-01-09 08:42 | 2022-01-09 14:03 | 5:21 | S/O | Due to protection test | 0 | 0 | No interruption
Raozan | Raozan-Hathazari 230 kV Ckt-2 | 2022-01-09 10:03 | 2022-01-09 17:25 | 7:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Modern 132 kV Ckt | 2022-01-10 09:36 | 2022-01-10 15:19 | 5:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-AKSML 230 kV Ckt | 2022-01-10 09:17 | 2022-01-10 16:50 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Modern 132 kV Ckt | 2022-01-10 08:34 | 2022-01-10 15:04 | 6:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Madunaghat 132 kV Ckt-1 | 2022-01-11 09:30 | 2022-01-11 13:58 | 4:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Modern 132 kV Ckt | 2022-01-12 08:57 | 2022-01-12 16:30 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Madunaghat 132 kV Ckt-2 | 2022-01-12 09:38 | 2022-01-12 17:19 | 7:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV Ckt-1 | 2022-01-12 08:32 | 2022-01-12 15:58 | 7:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV Ckt-2 | 2022-01-13 09:29 | 2022-01-13 16:03 | 6:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV Ckt-3 | 2022-01-13 09:54 | 2022-01-13 16:20 | 6:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV Ckt-2 | 2022-01-13 09:01 | 2022-01-13 15:05 | 6:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV Ckt-3 | 2022-01-14 09:54 | 2022-01-14 11:50 | 1:56 | S/O | Due to C/M work | 0 | 0 | No interruption
| Halishahar-Juldah 132 kV Ckt | 2022-01-15 09:45 | 2022-01-15 15:35 | 5:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahmirpur | Shahmirpur-Juldah 132 kV Ckt-1 | 2022-01-15 08:42 | 2022-01-15 15:32 | 6:50 | S/O | Due to A/M work | 0 | 0 | No interruption
| Shahmirpur-Juldah 132 kV Ckt-2 | 2022-01-15 09:05 | 2022-01-15 15:35 | 6:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Juldah 132 kV Ckt | 2022-01-15 09:26 | 2022-01-15 14:45 | 5:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Juldah | Juldah-Halishahar 132 kV Ckt | 2022-01-16 08:17 | 2022-01-16 14:46 | 6:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV Ckt-3 | 2022-01-16 10:29 | 2022-01-16 17:57 | 7:28 | S/O | Due to project work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Juldah 132 kV Ckt | 2022-01-18 09:44 | 2022-01-18 11:44 | 2:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Baraulia 132 kV Ckt-2 | 2022-01-18 08:30 | 2022-01-18 14:56 | 6:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Shahmirpur 132 kV Ckt-1 | 2022-01-18 13:13 | 2022-01-18 14:03 | 0:50 | S/O | Due to C/M work | 0 | 0 | No interruption
| Sikalbaha-Shahmirpur 132 kV Ckt-2 | 2022-01-18 12:06 | 2022-01-18 13:06 | 1:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Sikalbaha-Madunaghat 132 kV Ckt-1 | 2022-01-18 14:59 | 2022-01-18 16:16 | 1:17 | S/O | Due to A/M work | 0 | 0 | No interruption
| Sikalbaha-Juldah 132 kV Ckt | 2022-01-19 08:10 | 2022-01-19 14:50 | 6:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| Sikalbaha-Juldah 132 kV Ckt | 2022-01-20 08:35 | 2022-01-20 15:57 | 7:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Barierhat 132 kV Ckt-1 |  | 2022-01-21 10:06 |  |  | After maint.work | 0 | 0 | No interruption
Juldah | Juldah-Shahmirpur 132 kV Ckt-1 | 2022-01-20 08:49 | 2022-01-20 14:08 | 5:19 | S/O | Due to A/M work | 0 | 0 | No interruption
| Juldah-Shahmirpur 132 kV Ckt-2 | 2022-01-24 08:36 | 2022-01-24 15:36 | 7:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV Ckt-2 | 2022-01-25 22:18 |  |  | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Hathazari 132 kV Ckt-2 | 2022-01-25 09:39 | 2022-01-25 17:01 | 7:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahmirpur | Shahmirpur-Sikalbaha 132 kV Ckt-1 | 2022-01-25 09:26 | 2022-01-25 15:58 | 6:32 | S/O | Due to A/M work | 0 | 0 | No interruption
| Shahmirpur-Sikalbaha 132 kV Ckt-1 | 2022-01-25 09:26 | 2022-01-25 15:58 | 6:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV Ckt-1 | 2022-01-26 08:34 | 2022-01-26 14:34 | 6:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Hathazari 132 kV Ckt-2 | 2022-01-26 09:28 | 2022-01-26 17:21 | 7:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahmirpur | Shahmirpur-Sikalbaha 132 kV Ckt-1 | 2022-01-26 09:03 | 2022-01-26 16:49 | 7:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Shahmirpur 132 kV Ckt-1 | 2022-01-27 09:41 | 2022-01-27 17:28 | 7:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-1 | 2022-01-28 06:25 | 2022-01-28 10:30 | 4:05 | S/O | Due to D/W work | 80 | 326.6667 | Power interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt-2 | 2022-01-28 08:36 | 2022-01-28 08:36 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-1 | 2022-01-29 06:14 | 2022-01-29 09:48 | 3:34 | S/O | Due to D/W work | 74 | 263.9333 | Power interruption
Khagrachari | Khagrachari-Rangamati 132 kV Ckt-1 | 2022-01-29 08:25 | 2022-01-29 17:02 | 8:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Shahmirpur 132 kV Ckt-2 | 2022-01-29 09:45 | 2022-01-29 16:56 | 7:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Kagrachari 132 kV Ckt-2 | 2022-01-30 09:08 | 2022-01-30 16:24 | 7:16 | S/O | Due to D/W work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Kaptai 132 kV Ckt-2 | 2022-01-31 08:50 | 2022-01-31 17:04 | 8:14 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 318:40 |  | Unserved Energy: |  | 835.6667
Cumilla Grid Circle :
B.Baria | B.Baria-Shahjibazar 132 kV Ckt-1 | 2021-01-01 09:02 | 2022-01-01 16:31 | 8767:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-1 | 2022-01-01 08:36 | 2022-01-01 16:17 | 7:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Chaddagram 132 kV Ckt-1 | 2022-01-01 10:19 | 2022-01-01 17:27 | 7:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Kushiara 132 kV Ckt-2 | 2022-01-01 09:11 | 2022-01-01 16:37 | 7:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-2 | 2022-01-02 09:04 | 2022-01-02 17:23 | 8:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Baroierhat | Baroierhat-PHP 132 kV Ckt | 2022-01-02 08:20 | 2022-01-02 14:44 | 6:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Chaddagram 132 kV Ckt-1 | 2022-01-02 08:34 | 2022-01-02 15:52 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Kulaura 132 kV Ckt-2 | 2022-01-02 09:15 | 2022-01-02 16:43 | 7:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-2 | 2022-01-03 08:26 | 2022-01-03 14:45 | 6:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Chaddagram 132 kV Ckt-2 | 2022-01-03 09:40 | 2022-01-03 15:28 | 5:48 | S/O | Due to A/M work | 0 | 0 | No interruption
| Cumilla(N)-Chaddagram 132 kV Ckt-1 | 2022-01-03 15:38 | 2022-01-03 15:38 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Cumilla(N)-Chaddagram 132 kV Ckt-1 | 2022-01-03 16:46 | 2022-01-03 19:40 | 2:54 | S/O | Due to L/A bypass work | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV Ckt-1 | 2022-01-04 09:12 | 2022-01-04 16:38 | 7:26 | S/O | Due to A/M work | 0 | 0 | No interruption
| Cumilla(N)-Chaddagram 132 kV Ckt-1 | 2022-01-04 10:51 | 2022-01-04 12:34 | 1:43 | S/O | Due to replacement work | 0 | 0 | No interruption
| Cumilla(N)-Kachua 132 kV Ckt-2 | 2022-01-04 09:37 | 2022-01-04 15:04 | 5:27 | S/O | Due to A/M work | 0 | 0 | No interruption
| Cumilla(N)-Ashuganj 230 kV Ckt-1 | 2022-01-05 08:58 | 2022-01-05 22:42 | 13:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj(S) | Ashuganj(S)-Ashuganj(N) 230 kV Ckt-2 | 2022-01-06 09:29 | 2022-01-06 09:29 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV Ckt-1 | 2022-01-06 10:09 | 2022-01-06 16:46 | 6:37 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ashuganj(S)-Ghorashal 230 kV Ckt-2 | 2022-01-06 07:25 | 2022-01-06 17:26 | 10:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani S/S-Chowmuhani MW P/S 132 kV Ckt | 2022-01-07 09:25 | 2022-01-07 19:48 | 10:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV Ckt-2 | 2022-01-08 09:13 | 2022-01-08 18:59 | 9:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV Ckt-1 | 2022-01-08 08:58 | 2022-01-08 17:00 | 8:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV Ckt-2 | 2022-01-08 08:36 | 2022-01-08 17:00 | 8:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV Ckt-2 | 2022-01-09 08:54 | 2022-01-09 16:00 | 7:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV Ckt-1 | 2022-01-09 08:49 | 2022-01-09 17:27 | 8:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV Ckt-2 | 2022-01-09 08:19 | 2022-01-09 14:54 | 6:35 | S/O | Due to A/M work | 0 | 0 | No interruption
| Sylhet-Chatak 132 kV Ckt-2 | 2022-01-10 07:42 | 2022-01-10 07:42 | 0:00 |  |  | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV Ckt-1 | 2022-01-10 08:34 | 2022-01-10 16:43 | 8:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-kaliakoir 400 kV Ckt-1 | 2022-01-11 08:33 | 2022-01-11 18:01 | 9:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Daudkandi | Daudkandi-Cumilla(N) 132 kV Ckt-1 | 2022-01-11 08:28 | 2022-01-11 15:29 | 7:01 | S/O | Due to A/M work | 0 | 0 | No interruption
| Daudkandi-Cumilla(N) 132 kV Ckt-1 | 2022-01-12 08:43 | 2022-01-12 16:33 | 7:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-kaliakoir 400 kV Ckt-1 | 2022-01-12 09:22 | 2022-01-12 18:07 | 8:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj(Net) | Ashuganj(Net)-Modular 230 kV Ckt | 2022-01-13 09:47 | 2022-01-13 14:02 | 4:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-kaliakoir 400 kV Ckt | 2022-01-13 08:57 | 2022-01-13 18:15 | 9:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Daudkandi | Daudkandi-Cumilla(N) 132 kV Ckt-1 | 2022-01-13 08:28 | 2022-01-13 16:30 | 8:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj(Net) | Ashuganj(Net)-Ashuganj(S) 230 kV Ckt-2 | 2022-01-13 12:14 | 2022-01-15 12:13 | 47:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-kaliakoir 400 kV Ckt-2 | 2022-01-15 09:00 | 2022-01-15 17:27 | 8:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur | Chandpur-Chandpur CCPP 132 kV Ckt | 2022-01-15 09:18 | 2022-01-15 09:18 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV Ckt-2 | 2022-01-15 08:25 | 2022-01-15 15:16 | 6:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Fenchuganj P.S 132 kV Ckt-2 | 2022-01-15 09:03 | 2022-01-15 16:45 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur | Chandpur-Chandpur Desh 132 kV Ckt-2 | 2022-01-15 11:19 | 2022-01-15 16:22 | 5:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-kaliakoir 400 kV Ckt-2 | 2022-01-16 08:48 | 2022-01-16 17:33 | 8:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV Ckt-2 | 2022-01-16 08:26 | 2022-01-16 15:26 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Tripura 132 kV Ckt-2 | 2022-01-16 10:04 | 2022-01-16 17:18 | 7:14 | S/O | Due to D/W work | 0 | 0 | No interruption
Bibiyana | Bibiyana-kaliakoir 400 kV Ckt-2 | 2022-01-17 08:50 | 2022-01-17 17:34 | 8:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV Ckt-2 | 2022-01-17 08:58 | 2022-01-17 16:00 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Bhulta 400 kV Ckt-1 | 2022-01-17 10:26 | 2022-01-17 11:07 | 0:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Rampura 132 kV Ckt | 2022-01-17 12:08 | 2022-01-17 15:08 | 3:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sylhet 132 kV Ckt-2 | 2022-01-17 09:17 | 2022-01-17 16:58 | 7:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Feni 132 kV Ckt-1 | 2022-01-18 09:22 | 2022-01-18 16:57 | 7:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sylhet 132 kV Ckt-2 | 2022-01-18 09:46 | 2022-01-18 15:50 | 6:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-kaliakoir 400 kV Ckt-2 | 2022-01-18 08:38 | 2022-01-18 20:07 | 11:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Feni 132 kV Ckt-1 | 2022-01-19 08:55 | 2022-01-19 17:26 | 8:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.Baria 132 kV Ckt-2 | 2022-01-19 09:44 | 2022-01-19 17:01 | 7:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sylhet 132 kV Ckt-1 | 2022-01-19 09:31 | 2022-01-19 12:54 | 3:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Feni 132 kV Ckt-1 | 2022-01-20 08:48 | 2022-01-20 12:25 | 3:37 | S/O | Due to A/M work | 0 | 0 | No interruption
B,Baria | B,Baria-Ashuganj 132 kV Ckt-1 | 2022-01-20 08:54 | 2022-01-20 17:00 | 8:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Kachua 132 kV Ckt-2 | 2022-01-20 09:49 | 2022-01-20 19:36 | 9:47 | S/O | Due to D/W work | 0 | 0 | No interruption
Ashuganj(S) | Ashuganj(S)-Ghorashal 230 kV Ckt-2 | 2022-01-22 08:02 | 2022-01-22 13:30 | 5:28 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ashuganj(S)-Kishoreganj 132 kV Ckt-2 | 2022-01-22 09:44 | 2022-01-22 15:48 | 6:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Feni 132 kV Ckt-2 | 2022-01-22 09:38 | 2022-01-22 16:54 | 7:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.Baria 132 kV Ckt-2 | 2022-01-23 09:00 | 2022-01-23 16:27 | 7:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Feni 132 kV Ckt-2 | 2022-01-23 09:09 | 2022-01-23 16:35 | 7:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Tripura 132 kV Ckt-1 | 2022-01-23 10:22 | 2022-01-23 17:01 | 6:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj P/P 132 kV Ckt | 2022-01-25 08:38 | 2022-01-25 15:08 | 6:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Feni 132 kV Ckt-2 | 2022-01-25 09:08 | 2022-01-25 14:48 | 5:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.Baria 132 kV Ckt-2 | 2022-01-25 10:51 | 2022-01-25 16:52 | 6:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur S/S | Chandpur S/S-Chandpur 115 MW P/P 132 kV Ckt | 2022-01-25 10:40 | 2022-01-25 17:15 | 6:35 | S/O | Due to D/W work | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj P/S 132 kV Ckt | 2022-01-26 08:47 | 2022-01-26 15:46 | 6:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | Sreemongal-Shahjibazar 132 kV Ckt-2 | 2022-01-26 08:52 | 2022-01-26 15:06 | 6:14 | S/O | Due to A/M work | 0 | 0 | No interruption
| Sreemongal-Shahjibazar 132 kV Ckt-2 | 2022-01-27 08:19 | 2022-01-27 15:50 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-2 | 2022-01-28 09:06 | 2022-01-28 14:37 | 5:31 | S/O | Due to D/W work | 0 | 0 | No interruption
Sreemongal | Sreemongal-Shahjibazar 132 kV Ckt-2 | 2022-01-29 08:28 | 2022-01-29 17:15 | 8:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Fenchuganj P.P 132 kV Ckt-1 | 2022-01-29 09:47 | 2022-01-29 11:24 | 1:37 | S/O | Due to A/M work | 0 | 0 | No interruption
| Fenchuganj-Fenchuganj P.P 132 kV Ckt-2 | 2022-01-29 11:26 | 2022-01-29 13:22 | 1:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | Sreemongal-Shahjibazar 132 kV Ckt-2 | 2022-01-30 08:16 | 2022-01-30 16:32 | 8:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.Baria 132 kV Ckt-2 | 2022-01-31 09:09 | 2022-01-31 16:13 | 7:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV Ckt-1 | 2022-01-31 10:10 | 2022-01-31 10:49 | 0:39 | S/O | Due to C/M work | 0 | 0 | No interruption
| Fenchuganj-Sreemongal 132 kV Ckt-2 | 2022-01-31 10:51 | 2022-01-31 16:16 | 5:25 | S/O | Due to C/M work | 0 | 0 | No interruption
| Fenchuganj-Kulaura 132 kV Ckt-2 | 2022-01-31 11:48 | 2022-01-31 12:22 | 0:34 | S/O | Due to A/M work | 0 | 0 | No interruption
| Fenchuganj-Kulaura 132 kV Ckt-1 | 2022-01-31 12:23 | 2022-01-31 13:02 | 0:39 | S/O | Due to A/M work | 0 | 0 | No interruption
| Fenchuganj-Fenchuganj P.P 132 kV Ckt-3 | 2022-01-31 13:29 | 2022-01-31 13:53 | 0:24 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 9319:34 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Goaplaganj | Goaplaganj-Madaripur 132 kV Ckt-3 | 2022-01-01 07:48 | 2022-01-01 07:48 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaia 132 kV Ckt | 2022-01-01 08:20 | 2022-01-01 17:41 | 9:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Faridpur P/S 132 kV Ckt | 2022-01-01 08:20 | 2022-01-01 15:48 | 7:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | Goalpara-Bagerhat 132 kV Ckt-1 | 2022-01-02 08:36 | 2022-01-02 16:19 | 7:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Bhola 230 kV Ckt-2 | 2022-01-02 08:55 | 2022-01-02 17:22 | 8:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj(N)-Madaripur 132 kV Ckt-3 | 2022-01-02 08:00 | 2022-01-02 18:03 | 10:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Goalpara 132 kV Ckt | 2022-01-03 08:50 | 2022-01-03 16:15 | 7:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Bhola 230 kV Ckt-2 | 2022-01-03 08:39 | 2022-01-03 16:53 | 8:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Goaplaganj(N) | Goaplaganj-Madaripur 132 kV Ckt-4 | 2022-01-03 08:25 | 2022-01-03 18:07 | 9:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Shariatpur 132 kV Ckt-2 | 2022-01-03 08:45 | 2022-01-03 17:35 | 8:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Magura | Magura-Narail 132 kV Ckt-2 | 2022-01-04 09:52 | 2022-01-04 09:52 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Bhola 230 kV Ckt-2 | 2022-01-04 08:17 | 2022-01-04 17:22 | 9:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | Goalpara-Orion Rupsha 132 kV Ckt | 2022-01-04 09:30 | 2022-01-04 17:12 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Goaplaganj(N) | Goaplaganj-Madaripur 132 kV Ckt-4 | 2022-01-04 08:14 | 2022-01-04 17:25 | 9:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Orion Rupsha P/P 132 kV Ckt | 2022-01-05 08:29 | 2022-01-05 16:34 | 8:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Bhola 230 kV Ckt-2 | 2022-01-05 09:10 | 2022-01-05 17:23 | 8:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Goaplaganj(N) | Goaplaganj-Madaripur 132 kV Ckt-3 | 2022-01-05 08:15 | 2022-01-05 16:15 | 8:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Bhola 230 kV Ckt-2 | 2022-01-06 09:02 | 2022-01-06 17:13 | 8:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj | Gopalganj(N)-Faridpur 132 kV Ckt-2 | 2022-01-06 10:01 | 2022-01-06 16:31 | 6:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Goaplaganj(N) | Goaplaganj(N)-Payra 400 kV Ckt-2 | 2022-01-06 10:18 | 2022-01-07 08:08 | 21:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Magura | Magura-Narail 132 kV Ckt-2 | 2022-01-06 09:52 | 2022-01-06 13:48 | 3:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Bhola 230 kV Ckt-2 | 2022-01-07 09:08 | 2022-01-07 16:37 | 7:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Payra | Payra-Gopalganj 400 kV Ckt-2 |  | 2022-01-07 08:33 |  | S/O | After maint.work | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Bhola 230 kV Ckt-1 | 2022-01-07 08:27 | 2022-01-07 08:27 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Gopalganj (N) 132 kV Ckt-3 | 2022-01-08 08:39 | 2022-01-08 17:03 | 8:24 | S/O | Due to D/W work | 0 | 0 | No interruption
| Madaripur-Gopalganj (N) 132 kV Ckt-4 | 2022-01-08 08:39 | 2022-01-08 17:03 | 8:24 | S/O |  | 0 | 0 | No interruption
Magura | Magura-Narail 132 kV Ckt-2 | 2022-01-08 18:10 | 2022-01-08 21:29 | 3:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Gopalganj (N) 132 kV Ckt-3 | 2022-01-09 09:36 | 2022-01-09 17:19 | 7:43 | S/O | Due to D/W work | 0 | 0 | No interruption
| Madaripur-Gopalganj (N) 132 kV Ckt-4 | 2022-01-09 09:41 | 2022-01-09 17:00 | 7:19 | S/O | Due to D/W work | 0 | 0 | No interruption
Magura | Magura-Narail 132 kV Ckt-2 | 2022-01-10 08:40 | 2022-01-10 17:15 | 8:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Goaplaganj(N) | Goaplaganj(N)-Gopalganj (O) 132 kV Ckt-2 | 2022-01-11 07:35 | 2022-01-11 07:35 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Magura | Magura-Narail 132 kV Ckt-2 | 2022-01-11 08:28 | 2022-01-11 15:46 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Goaplaganj(N) | Goaplaganj(N)-Gopalganj (O) 132 kV Ckt-2 | 2022-01-12 08:39 | 2022-01-12 17:18 | 8:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Bhola 230 kV Ckt-1 | 2022-01-13 09:47 | 2022-01-13 14:02 | 4:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Shariatpur 132 kV Ckt-1 | 2022-01-15 10:12 | 2022-01-15 17:02 | 6:50 | S/O | Due to A/M work | 0 | 0 | No interruption
| Madaripur-Shariatpur 132 kV Ckt-1 | 2022-01-16 08:55 | 2022-01-16 17:12 | 8:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Mongla | Mongla-Orion Solar 132 kV Ckt | 2022-01-16 11:42 | 2022-01-16 15:12 | 3:30 | S/O | Due to D/W work | 0 | 0 | No interruption
Payra | Payra-Payra P/S 132 kV Ckt-4 | 2022-01-16 11:03 | 2022-01-16 11:03 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Madaripur | Madaripur-Shariatpur 132 kV Ckt-2 | 2022-01-17 09:12 | 2022-01-17 16:27 | 7:15 | S/O | Due to A/M work | 0 | 0 | No interruption
| Madaripur-Shariatpur 132 kV Ckt-2 | 2022-01-18 09:10 | 2022-01-18 16:41 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | Goalpara-Khulna© 132 kV Ckt-1 | 2022-01-18 14:10 | 2022-01-18 17:23 | 3:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal | Barisal-Bhandaria 132 kV Ckt | 2022-01-19 08:03 | 2022-01-19 17:12 | 9:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Goaplaganj(N) | Goaplaganj(N)-Madhumati P/P 132 kV Ckt | 2022-01-20 12:12 | 2022-01-20 14:24 | 2:12 | S/O | Due to SPMD work | 0 | 0 | No interruption
Barisal | Barisal-Bhandaria 132 kV Ckt | 2022-01-20 08:37 | 2022-01-20 16:42 | 8:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Goaplaganj S/S | Goaplaganj S/S-Gopalganj P/P 132 kV Ckt | 2022-01-20 08:10 | 2022-01-20 17:48 | 9:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Shariatpur 132 kV Ckt-2 | 2022-01-20 08:16 | 2022-01-20 12:48 | 4:32 | S/O | Due to A/M work | 0 | 0 | No interruption
| Madaripur-Shariatpur 132 kV Ckt-1 | 2022-01-20 12:52 | 2022-01-20 17:29 | 4:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Mongla | Mongla-Bagerhat 132 kV Ckt-2 | 2022-01-21 09:09 | 2022-01-21 13:11 | 4:02 | S/O | Due to D/W work | 0 | 0 | No interruption
Payra P/S | Payra P/S-Payra 400 kV Ckt-4 | 2022-01-21 08:41 | 2022-01-21 08:41 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Orion Rupsha P/S 132 kV Ckt | 2022-01-21 10:09 | 2022-01-21 13:21 |  | S/O | Due to D/W work | 0 | 0 | No interruption
| Bagerhat-Goalpara 132 kV Ckt | 2022-01-22 08:57 | 2022-01-22 11:58 | 3:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna © | Khulna ©-Noapara 132 kV Ckt-1 | 2022-01-22 08:34 | 2022-01-22 16:36 | 8:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Barisal 132 kV Ckt-1 | 2022-01-22 09:05 | 2022-01-22 16:17 | 7:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna © | Khulna ©-Noapara 132 kV Ckt-1 | 2022-01-23 08:30 | 2022-01-23 14:40 | 6:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Barisal 132 kV Ckt-1 | 2022-01-24 09:05 | 2022-01-24 16:10 | 7:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna © | Khulna ©-Noapara 132 kV Ckt-2 | 2022-01-25 08:19 | 2022-01-25 14:26 | 6:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Barisal 132 kV Ckt-1 | 2022-01-25 08:28 | 2022-01-25 16:44 | 8:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna © | Khulna ©-Noapara 132 kV Ckt-2 | 2022-01-25 08:19 | 2022-01-25 14:26 | 6:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Barisal 132 kV Ckt-1 | 2022-01-25 08:28 | 2022-01-25 16:44 | 8:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | Khulna (S)-Satkhira 132 kV Ckt-2 |  | 2022-01-25 10:31 |  |  | After maint.work | 0 | 0 | No interruption
Patuakhali | Patuakhali-Payra 132 kV Ckt-1 | 2022-01-25 11:04 | 2022-01-25 11:05 | 0:01 | S/O | Due to D/W work | 0 | 0 | No interruption
Magura | Magura-Narail 132 kV Ckt-1 | 2022-01-26 10:25 | 2022-01-26 18:18 | 7:53 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulna © | Khulna ©-Noapara 132 kV Ckt-2 | 2022-01-26 08:15 | 2022-01-26 14:02 | 5:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Barisal 132 kV Ckt-1 | 2022-01-26 09:23 | 2022-01-26 16:58 | 7:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal | Barishal-Bhandaria 132 kV Ckt-1 | 2022-01-26 07:48 | 2022-01-26 09:15 | 1:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Barapukuria | Barapukuria-Bogura 230 kV Ckt-1 | 2022-01-26 12:13 | 2022-01-26 14:08 | 1:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Barisal 132 kV Ckt-1 | 2022-01-27 09:53 | 2022-01-27 14:34 | 4:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Magura | Magura-Narail 132 kV Ckt-2 | 2022-01-27 09:49 | 2022-01-27 17:12 | 7:23 | S/O | Due to D/W work | 0 | 0 | No interruption
Payra P.P | Payra P.P-Payra S/S 400 kV Ckt-3 | 2022-01-28 05:34 | 2022-01-28 05:34 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Barisal 132 kV Ckt-2 | 2022-01-29 08:40 | 2022-01-29 16:56 | 8:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Magura | Magura-Narail 132 kV Ckt-2 | 2022-01-29 11:07 | 2022-01-29 15:59 | 4:52 | S/O | Due to D/W work | 0 | 0 | No interruption
Madaripur | Madaripur-Barisal (N)132 kV Ckt-2 | 2022-01-30 08:36 | 2022-01-30 16:49 | 8:13 | S/O | Due to A/M work | 0 | 0 | No interruption
| Madaripur-Gopalganj (N) 132 kV Ckt-2 | 2022-01-30 14:23 | 2022-01-30 15:15 | 0:52 | S/O | Due to C/M work | 0 | 0 | No interruption
| Madaripur-Gopalganj (N) 132 kV Ckt-2 | 2022-01-31 09:28 | 2022-01-31 10:18 | 0:50 | S/O | Due to C/M work | 0 | 0 | No interruption
| Madaripur-Gopalganj (N) 132 kV Ckt-4 | 2022-01-31 10:29 | 2022-01-31 11:49 | 1:20 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 439:33 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Bheramara | Bheramara-Ishurdi 132 kV Ckt-1 | 2022-01-01 08:51 | 2022-01-01 15:45 | 6:54 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bheramara -Bottail 132 kV Ckt-1 | 2022-01-01 08:20 | 2022-01-01 16:03 | 7:43 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bheramara -Bottail 132 kV Ckt-1 | 2022-01-02 08:17 | 2022-01-02 14:45 | 6:28 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bheramara -Kustia 132 kV Ckt-2 | 2022-01-05 08:48 | 2022-01-05 15:52 | 7:04 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bheramara -Kustia 132 kV Ckt-2 | 2022-01-06 08:51 | 2022-01-06 15:10 | 6:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenaidah(O) | Jhenaidah(O)-Jhenaidah (N) 132 kV Ckt-2 | 2022-01-09 08:22 | 2022-01-09 17:05 | 8:43 | S/O | Due to A/M work | 0 | 0 | No interruption
| Jhenaidah(O)-Kustia (N) 132 kV Ckt-1 | 2022-01-09 08:16 | 2022-01-09 17:02 | 8:46 | S/O | Due to A/M work | 0 | 0 | No interruption
| Jhenaidah(O)-Jhenaidah (N) 132 kV Ckt-2 | 2022-01-10 08:29 | 2022-01-10 17:35 | 9:06 | S/O | Due to A/M work | 0 | 0 | No interruption
| Jhenaidah(O)-Kustia (N) 132 kV Ckt-1 & 2 | 2022-01-10 08:25 | 2022-01-10 17:34 | 9:09 | S/O | Due to A/M work | 0 | 0 | No interruption
| Jhenaidah(O)-Jhenaidah (N) 132 kV Ckt-2 | 2022-01-11 10:48 | 2022-01-11 12:56 | 2:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenaidah(N) | Jhenaidah(N)-Jashore 132 kV Ckt-1 | 2022-01-11 08:44 | 2022-01-11 10:31 | 1:47 | S/O | Due to D/W work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ruppur 132 kV Ckt-1 | 2022-01-12 09:17 | 2022-01-12 14:22 | 5:05 | S/O | Due to C/M work | 0 | 0 | No interruption
| Jhenaidah-Bottai 132 kV Ckt-2 |  | 2022-01-13 23:10 |  |  | After maint.work | 0 | 0 | No interruption
Bottail | Bottail-Jhenaidah 132 kV Ckt-1 | 2022-01-16 11:13 |  |  | S/O | Due to C/M work | 0 | 0 | No interruption
Kustia | Kustia-Jhenaidah 132 kV Ckt-2 | 2022-01-16 08:07 | 2022-01-16 17:00 | 8:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenaidah(O) | Jhenaidah(O)-Jhenaidah (N) 132 kV Ckt-1 | 2022-01-16 11:19 | 2022-01-16 12:14 | 0:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Bottail | Bottail-Jhenaidah 132 kV Ckt-2 | 2022-01-17 08:24 | 2022-01-17 16:58 | 8:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Kustia | Kustia-Jhenaidah 132 kV Ckt-2 | 2022-01-18 08:43 | 2022-01-18 14:37 | 5:54 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kustia-Jhenaidah 132 kV Ckt-1 |  | 2022-01-18 22:20 |  |  | After maint.work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Bheramara 132 kV Ckt-2 | 2022-01-19 08:19 | 2022-01-19 16:11 | 7:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenaidah(O) | Jhenaidah(O)-Jhenaidah (N) 132 kV Ckt-1 | 2022-01-19 08:53 | 2022-01-19 14:25 | 5:32 | S/O | Due to A/M work | 0 | 0 | No interruption
| Jhenaidah(O)-Jhenaidah (N) 132 kV Ckt-2 | 2022-01-20 09:04 | 2022-01-20 15:17 | 6:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-HVDC 230 kV Ckt-1 | 2022-01-24 10:19 | 2022-01-24 11:31 | 1:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenaidah (N) | Jhenaidah-Jashore 132 kV Ckt-2 | 2022-01-25 08:44 | 2022-01-25 14:08 | 5:24 | S/O | Due to A/M work | 0 | 0 | No interruption
| Jhenaidah-Khulna(S) 230 kV Ckt-1 | 2022-01-26 09:28 | 2022-01-26 20:09 | 10:41 | S/O | Due to D/W work | 0 | 0 | No interruption
| Jhenaidah (N)-HVDC 230 kV Ckt-1 | 2022-01-26 09:51 | 2022-01-26 20:07 | 10:16 | S/O | Due to D/W work | 0 | 0 | No interruption
| Jhenaidah-Jashore 132 kV Ckt-2 | 2022-01-26 08:09 | 2022-01-26 15:16 | 7:07 | S/O | Due to A/M work | 0 | 0 | No interruption
HVDC | HVDC -Jhenaidah(N) 230 kV Ckt-1 | 2022-01-27 09:13 | 2022-01-27 18:34 | 9:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Jhenaidah (N) | Jhenaidah (N)-Jashore 132 kV Ckt-1 | 2022-01-27 08:15 | 2022-01-27 16:00 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
| Jhenaidah (N)-Khulna(S) 230 kV Ckt-1 | 2022-01-27 09:03 | 2022-01-27 18:19 | 9:16 | S/O | Due to D/W work | 0 | 0 | No interruption
| Jhenaidah (O)-Jhenaidah(N) 132 kV Ckt-3 | 2022-01-29 08:31 | 2022-01-29 16:47 | 8:16 | S/O | Due to A/M work | 0 | 0 | No interruption
| Jhenaidah (N)-Chuadanga 132 kV Ckt | 2022-01-29 08:16 | 2022-01-29 16:47 | 8:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Pabna | Pabna-Ishurdi 132 kV Ckt | 2022-01-30 09:09 | 2022-01-30 11:52 | 2:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenaidah (N) | Jhenaidah (N)-Jashore 132 kV Ckt-1 | 2022-01-30 08:19 | 2022-01-30 13:06 | 4:47 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 208:24 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Palashbari | Palashbari-Mohastanghor 132 kV Ckt-2 | 2022-01-01 09:05 | 2022-01-01 16:42 | 7:37 | S/O | Due to A/M work | 0 | 0 | No interruption
| Palashbari-Mohastanghor 132 kV Ckt-1 | 2022-01-02 09:10 | 2022-01-02 15:25 | 6:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura -Mohasthangarth 132 kV Ckt-1 | 2022-01-03 08:32 | 2022-01-03 16:45 | 8:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Thakurgaon | Thakurgaon-Energay Pac.P.P 132 kV Ckt | 2022-01-03 11:56 | 2022-01-03 13:42 | 1:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura -Mohasthangarth 132 kV Ckt-2 | 2022-01-06 09:18 | 2022-01-06 16:44 | 7:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura (N) | Bogura (N)-Sherpur(Bogura) 132 kV Ckt-1 | 2022-01-08 12:09 | 2022-01-08 16:43 | 4:34 | S/O | Due to protection test | 0 | 0 | No interruption
Bogura | Bogura -Mohasthangarth 132 kV Ckt-2 | 2022-01-08 10:24 | 2022-01-08 15:43 | 5:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Shahjadpur 132 kV Ckt | 2022-01-11 09:16 | 2022-01-11 13:49 | 4:33 | S/O | Due to A/M work | 0 | 0 | No interruption
| Sirajganj-Baghabari 132 kV Ckt | 2022-01-12 08:18 | 2022-01-12 16:16 | 7:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Kurigram 132 kV Ckt | 2022-01-14 08:35 | 2022-01-14 16:29 | 7:54 | S/O | Due to C/M work | 40 | 316 | Power interruption
Mithapukur | Mithapukur-Rangpur Confidence 132 kV Ckt | 2022-01-18 09:32 | 2022-01-18 16:46 | 7:14 | S/O | Due to D/W work | 0 | 0 | No interruption
| Mithapukur-Rangpur 132 kV Ckt-1 | 2022-01-18 14:32 | 2022-01-18 16:46 | 2:14 | S/O | Due to D/W work | 0 | 0 | No interruption
| Mithapukur-Palashbari 132 kV Ckt-1 | 2022-01-19 09:19 | 2022-01-19 13:49 | 4:30 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangpur | Rangpur-Lalmonirhat 132 kV Ckt | 2022-01-21 08:30 | 2022-01-21 16:45 | 8:15 | S/O | Due to A/M work | 18 | 148.5 | Power interruption
Barapukuria | Barapukuria-Bogura 230 kV Ckt-1 | 2022-01-22 08:13 | 2022-01-22 19:09 | 10:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | Natore-Rajlanka P.P 132 kV Ckt-2 | 2022-01-22 09:09 | 2022-01-22 17:30 | 8:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | Barapukuria-Bogura 230 kV Ckt-1 | 2022-01-23 07:48 | 2022-01-23 07:48 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV Ckt-1 | 2022-01-23 09:10 | 2022-01-23 12:30 | 3:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | Bogura -Barapukuria 230 kV Ckt-2 | 2022-01-24 07:48 | 2022-01-24 07:48 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bogura -Barapukuria 230 kV Ckt-2 | 2022-01-25 07:48 | 2022-01-25 07:48 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | Barapukuria-Bogura 230 kV Ckt-2 | 2022-01-26 07:41 | 2022-01-26 12:09 | 4:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Lalmonirhat 132 kV Ckt | 2022-01-28 08:19 | 2022-01-28 16:56 | 8:37 | S/O | Due to C/M work | 35 | 301.5833 | Power interruption
|  |  | Total : | 119:30 |  | Unserved Energy: |  | 766.0833
Others :
Ullon | Ullon-Dhanmondi 132 kV cable line |  | 2022-01-19 16:58 | 0:00 | S/O | After maint.work | 0 | 0 | No interruption
Haripur | Haripur-Ullon 132 kV Ckt |  | 2022-01-24 08:48 |  |  |  | 0 | 0 | No interruption
Dhanmondi | Dhanmondi-Ullon 132 kV Ckt |  | 2022-01-24 09:04 |  |  |  | 0 | 0 | No interruption
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 11330:17 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:January 2022
| Area | Previous Month (December' 2021) |  |  |  | Current Month (January '2022)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 8 | - | 163 | 171 | 7 | 5 | 248 | 260
2 | Dhaka (South) Grid Circle. | 15 | - | 110 | 125 | 9 | 4 | 110 | 123
3 | Chattogram Grid Circle. | 11 | 1 | 78 | 90 | 4 | 3 | 91 | 98
4 | Cumilla Grid Circle. | 13 | 4 | 96 | 113 | 21 | 4 | 99 | 124
5 | Khulna Grid Circle. | 7 | 3 | 90 | 100 | 3 | 5 | 106 | 114
6 | HVDC Grid Circle | 2 | 1 | 43 | 46 | 3 | - | 53 | 56
7 | Bogura Grid Circle. |  | 3 | 119 | 122 | 10 | 2 | 41 | 53
8 | Others |  |  | 3 | 3 |  |  | 3 | 3
9 | Total | 56 | 12 | 702 | 770 | 57 | 23 | 751 | 831
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:January 2022
| Area | Previous Month (December' 2021) |  |  |  | Current Month (January '2022)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | - | - | 1028.58 | 1028.58 | - | 82.97 | 1112.0833 | 1195.0533
2 | Dhaka (South) Grid Circle. | 34.93 |  | 109.67 | 144.6 | - | 50 | 716.27 | 766.27
3 | Chattogram Grid Circle. | 223.06 | 122.67 | 95.8 | 441.53 | 18.37 | 14.25 | 1367.61 | 1400.23
4 | Cumilla Grid Circle. | 16.97 | - | - | 16.97 | 483.4 |  | 15.47 | 498.87
5 | Khulna Grid Circle. | 3.6 |  | 353.25 | 356.85 | - | 3.33 |  | 3.33
6 | HVDC Grid Circle | 12.67 | 5.67 | 423.37 | 441.71 |  |  | 570.33 | 570.33
7 | Bogura Grid Circle. |  | 522.33 | 462.83 | 985.16 | 110.85 |  | 1301.75 | 1412.6
8 | Others | 0 | 0 | 0 | 0 |  |  |  | 0
9 | Total | 291.23 | 650.67 | 2473.5 | 3415.4 | 612.62 | 150.55 | 5083.5133 | 5846.6833
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:January 2022
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 3 | 5 | 8 | 2 | 1 | 5 | 1195.05
2 | Dhaka (South) | 5031.6 | 2 | 2 | 4 | 1 | 1 | 2 | 766.27
3 | Chattogram | 2042 | 3 | 6 | 9 |  | 3 | 6 | 564.57
4 | Khulna | 2434 | 1 | - | 1 | - | 1 | - | 3.33
5 | HVDC | 5954.3 | 1 | 2 | 3 | - | 1 | 2 | 570.33
6 | Bogura | 3145.6 | 3 | 4 | 7 | 1 | 2 | 4 | 553.32
7 | Cumilla | 2981 | 2 | 1 | 3 | 1 |  | 2 | 290.8
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 3943.67
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.79%
4 | Khulna | 99.99%
5 | HVDC | 99.98% | [6 empty] | Executive Engineer
6 | Bogura | 99.97% | [6 empty] | Information Management Division
7 | Cumilla | 99.93% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:January 2022
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | - | - | - | - | - | - | -
2 | Dhaka (South) | 990.29 |  | - | - | - | - | - | - | -
3 | Chattogram | 917 | - |  | 4 | 4 | 2 |  | 4 | 835.6667
4 | Khulna | 1238.4 | - | - | - | - | - | - | - | - | -
5 | HVDC | 1325 | - | - | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - | 1 | 2 | 3 |  |  | 1 | 859.28
7 | Cumilla | 1648.16 | - | 3 |  | 3 | 2 |  | 1 | 208.07
8 | Others | - |  | - | - | - | - | - | - | -
| Total | 10176.6215 | [7 empty] | 1903.0167
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 99.97%
4 | Khulna | 99.98%
5 | Bheramara (HVDC) | 100% | [7 empty] | Executive Engineer
6 | Bogura | 99.51% | [7 empty] | Information Management Division
7 | Cumilla | 99.91% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:January 2022
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2022-01-01 | 5 | - | 3 | 2hr'46 min | - | - | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:January 2022
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Kishoreganj | 2 | 0:29 | 94 | 45.4333 | Due to 33 kV feeder fault
|  | 0:31 | 32 | 16.5333
Kabirpur | 1 | 0:14 | 90 | 21 | Due to 33 kV feeder fault
|  | 1:15 | 60 | 75 | Due to S/D of 132/33 kV Transformer T2
Jamalpur | 1 | 1:10 | 10 | 11.6667 | Due to S/D of 132/33 kV Transformer T2
Kadda | 2 | 9:21 | 75 | 701.25 | Due to S/D of 132/33 kV Transformer T4
|  | 5:52 | 50 | 293.3333 | Due to S/D of 132/33 kV Transformers T1 & T2
Tangail | 1 | 3:05 | 10 | 30.8333 | Due to S/D of 132/33 kV Transformer T3
Hasnabad | 2 | 0:25 | 40 | 16.6667 | Due to 33 kV feeder fault
|  | 0:33 | 40 | 33.3333
Narsingdi |  | 6:00 | 70 | 420 | Due to S/D of 33 kV main Bus
Munshiganj | 1 | 6:44 | 44 | 296.2667 | Due to S/D of 132/33 kV Transformers T1 & T2
Khulshi | 1 | 0:31 | 22 | 11.3667 | Due to 33 kV feeder fault
Hathazari | 2 | 0:42 | 10 | 7 | Due to tripping of 132/33 kV transformer T-1
|  | 4:53 | 15 | 14.25 | Due to Oil leakage
Cox'sbazar |  | 0:49 | 20 | 16.3333 | Due to S/D of 132 kV main Bus
Dohazari |  | 5:37 | 40 | 224.6667 | Due to S/D of 132 kV main Bus
Halishahar |  | 2:05 | 17 | 35.4167 | Due to S/D of 132 main Bus
Shahmirpur | 1 | 10:07 | 20 | 202.3333 | Due to S/D of 132/33 kV TransformerT2
Juldah | 1 | 5:00 | 8 | 40 | Due to S/D of 132 main Bus
Khagrachari |  | 1:06 | 12 | 13.2 | Due to S/D of 132/33 kV TransformerT1
Dohazari |  | 4:47 | 32 | 153.0667 | Due to S/D of Dohazari-Cox'sbazar 132 kV Ckt-2
| 3 | 1:09 | 80 | 92 | Due to S/D of Dohazari-Matarbari 132 kV Ckt
|  | 4:05 | 80 | 326.6667 | Due to S/D of Dohazari-Cox'sbazar 132 kV Ckt-1
|  | 3:34 | 74 | 263.9333
Fenchuganj | 1 | 0:22 | 10 | 3.6667 | Due to tripping of 132/33 kV transformer T2
B.Baria | 1 | 5:26 | 50 | 271.6667 | Due to 33 kV feeder fault
Chattak | 1 | 0:12 | 15 | 3 | Due to tripping of Chattak-Sunamganj 132 kV Ckt
Fenchuganj | 1 | 6:59 | 28 | 195.5333 | Due to tripping of Fenchuganj S/S-Sylhet 132 kV Ckt
Sylhet | 1 | 0:26 | 22 | 9.5333 | Due to tripping of Sylhet-Biyanibazar -Fenchuganj 132 kV Ckt
Kulaura | 1 | 3:52 | 4 | 15.4667 | Due to S/D of 132/33 kV TransformerT1
Khulna© | 1 | 0:50 | 4 | 3.3333 | Due to red-hot maint of 33 kV Bus
Bottail | 1 | 7:43 | 50 | 385.8333 | Due to S/D of 132 kV main Bus
Pabna | 1 | 6:09 | 30 | 184.5
Rajshahi | 1 | 0:25 | 5 | 2.0833 | Due to tripping of 132/33 kV transformer T3
Char-Saidpur | 1 | 0:58 | 10 | 9.6667 | Due to tripping of 132/33 kV transformer T-2
Naogaon | 1 | 0:59 | 6 | 5.9
Rangpur | 1 | 3:53 | 24 | 93.2 | Due to tripping of Rangpur-Kurigram 132 kV Ckt
Naogaon |  | 4:10 | 5 | 20.8333 | Due to S/D of 33 kV Bus-2
Purbasadipur | 1 | 1:34 | 15 | 23.5 | Due to S/D of 132/33 kV TransformerT2
Barapukuria | 1 | 1:38 | 25 | 40.8333 | Due to S/D of 132/33 kV TransformerT4
Naogaon | 1 | 5:18 | 85 | 450.5 | Due to S/D of 132/33 kV TransformersT1,T2 & T3
Rangpur | 4 | 7:54 | 40 | 316 | Due to S/D of Rangpur-Kurigram 132 kV Ckt
| 1 | 8:15 | 18 | 148.5 | Due to S/D of Rangpur-Lalmonirhat 132 kV Ckt
| 1 | 8:37 | 35 | 301.5833
| Total Unserved energy : |  |  | 5846.6833 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: January '2022
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 106 | 13 | 2022-01-01 | 12:00
2 | Munsiganj | 66 | 6 | 2022-01-01 | 19:30
3 | Sonargaon | 78 | 26 | 2022-01-01 | 19:30
4 | Shyampur | 190 | 12 | 2022-01-01 | 11:00
5 | Bhulta | 222 | 24 | 2022-01-01 | 0:00
6 | Madanganj | 41 | 7 | 2022-01-01 | 15:00
7 | Shitalakhya | 97 | 11 | 2022-01-01 | 12:00
8 | Rahim steel | 30 | 6 | 2022-01-01 | 15:00
9 | Matuail | 74 | 11 | 2022-01-01 | 1:00
10 | Ghorasal | 88 | 8 | 2022-01-01 | 16:00
11 | Narsingdi | 138 | 30 | 2022-01-01 | 19:00
12 | Haripur (SBU) | 122 | 20 | 2022-01-01 | 19:00
13 | Sreenagar | 36 | 13 | 2022-01-01 | 21:00
14 | Ullon | 62 | 24 | 2022-01-01 | 5:00
15 | Hasnabad | 78 | 8 | 2022-01-01 | 11:00
16 | Magbazar | 90 | 24 | 2022-01-01 | 2:00
17 | Maniknagar | 84 | 19 | 2022-01-01 | 19:00
18 | Bangabhaban | 9 | 10 | 2022-01-01 | 11:00
19 | Motijheel | 23 | 10 | 2022-01-01 | 13:00
20 | Narinda | 52 | 7 | 2022-01-01 | 13:00
21 | Kazla | 71 | 24 | 2022-01-01 | 12:00
22 | Dhanmondi | 129 | 23 | 2022-01-01 | 13:00
23 | Lalbag | 96 | 10 | 2022-01-01 | 18:30
24 | Madartek | 66 | 12 | 2022-01-01 | 20:00
25 | Dhaka University | 24 | 7 | 2022-01-01 | 12:00
26 | Aftabnagar | 18.32 | 25 | 2022-01-01 | 11:00
27 | Fatullah | 54 | 26 | 2022-01-01 | 10:00
28 | Nawabganj | 34 | 8 | 2022-01-01 | 18:00
29 | Keraniganj | 56 | 13 | 2022-01-01 | 18:30
30 | Banani | 45 | 7 | 2022-01-01 | 17:00
31 | Mirpur | 85 | 3 | 2022-01-01 | 18:30
32 | Kalyanpur | 72 | 15 | 2022-01-01 | 18:00
33 | Gulshan | 78 | 6 | 2022-01-01 | 5:00
34 | Uttara | 59 | 7 | 2022-01-01 | 18:00
35 | Uttara(new) | 48 | 10 | 2022-01-01 | 13:00
36 | Kamrangirchar | 79 | 7 | 2022-01-01 | 13:00
37 | Savar | 155 | 11 | 2022-01-01 | 18:00
38 | Bhasantec | 88 | 17 | 2022-01-01 | 13:00
39 | Agargaon | 57 | 7 | 2022-01-01 | 13:00
40 | Satmosjid | 84 | 30 | 2022-01-01 | 9:00
41 | Tongi | 106 | 13 | 2022-01-01 | 12:00
42 | Kabirpur | 228 | 19 | 2022-01-01 | 15:00
43 | Basundhara | 137 | 3 | 2022-01-01 | 21:00
44 | Purbachal | 150 | 23 | 2022-01-01 | 12:00
45 | Manikganj | 143 | 18 | 2022-01-01 | 18:30
46 | Joydevpur | 150 | 23 | 2022-01-01 | 12:00
47 | New Tongi | 129 | 25 | 2022-01-01 | 12:00
48 | Kodda | 94 | 6 | 2022-01-01 | 18:00
49 | Dhamrai | 102 | 10 | 2022-01-01 | 12:00
50 | Rajendrapur | 57.1 | 10 | 2022-01-01 | 22:00
51 | Tongi Millgate | 56 | 13 | 2022-01-01 | 12:00
52 | Valuka | 112 | 10 | 2022-01-01 | 18:00
53 | Tangail | 182 | 15 | 2022-01-01 | 18:30
54 | Mymensing | 194 | 28 | 2022-01-01 | 13:00
55 | Kishorganj | 108 | 15 | 2022-01-01 | 20:00
56 | Netrokona | 129 | 28 | 2022-01-01 | 10:00
57 | Jamalpur | 128 | 25 | 2022-01-01 | 8:00
58 | Sherpur | 132 | 21 | 2022-01-01 | 18:30
59 | Srimongal | 44 | 7 | 2022-01-01 | 18:00
60 | Shahjibazar | 86 | 21 | 2022-01-01 | 19:00
61 | Fenchuganj | 32 | 15 | 2022-01-01 | 17:00
62 | Kulawara | 30 | 4 | 2022-01-01 | 19:00
63 | Sylhet | 99 | 11 | 2022-01-01 | 18:00
64 | Chatak | 19 | 9 | 2022-01-01 | 20:00
65 | Sunamganj | 33 | 8 | 2022-01-01 | 18:00
66 | Bianibazar | 44 | 8 | 2022-01-01 | 19:30
67 | Cumilla (S) | 122 | 31 | 2022-01-01 | 18:00
68 | Cumilla(N) | 115 | 23 | 2022-01-01 | 18:00
69 | Chandpur | 52 | 3 | 2022-01-01 | 19:00
70 | Feni | 98 | 25 | 2022-01-01 | 20:00
71 | Chowmuhani | 135 | 15 | 2022-01-01 | 19:00
72 | Ashuganj | 30 | 14 | 2022-01-01 | 7:00
73 | Daudkandi | 102 | 25 | 2022-01-01 | 18:00
74 | B.Baria | 103 | 24 | 2022-01-01 | 20:00
75 | Ramganj | 62 | 12 | 2022-01-01 | 21:00
76 | Chaddagram | 36 | 7 | 2022-01-01 | 18:00
77 | PHP | 11 | 10 | 2022-01-01 | 2:00
78 | Kochua | 40 | 15 | 2022-01-01 | 18:00
79 | Madanhat | 50 | 7 | 2022-01-01 | 18:30
80 | Hathazari | 75 | 7 | 2022-01-01 | 18:00
81 | Khulshi | 175 | 25 | 2022-01-01 | 13:00
82 | Halishahar | 72 | 12 | 2022-01-01 | 20:00
83 | Baraulia | 160 | 11 | 2022-01-01 | 10:00
84 | Sikalbaha | 31 | 8 | 2022-01-01 | 17:00
85 | Dohazari | 78 | 9 | 2022-01-01 | 18:00
86 | Cox'sbazar | 96 | 29 | 2022-01-01 | 18:00
87 | Chandraghona | 30 | 2 | 2022-01-01 | 13:00
88 | Kaptai | 3.5 | 1 | 2022-01-01 | 18:00
89 | A. Khaer Stl. | 18 | 11 | 2022-01-01 | 7:00
90 | Bakulia | 90 | 7 | 2022-01-01 | 18:00
91 | Julda | 25 | 2 | 2022-01-01 | 12:00
92 | TK chemical | 27 | 3 | 2022-01-01 | 13:00
93 | Modern Steel | 0 | 1 | 2022-01-01 | 1:00
94 | Shahmirpur | 40 | 27 | 2022-01-01 | 18:00
95 | Khagrachhari | 26 | 22 | 2022-01-01 | 9:00
96 | Matarbari | 35 | 22 | 2022-01-01 | 19:00
97 | Baroiar Hat | 42 | 5 | 2022-01-01 | 17:00
98 | Rangamati | 10 | 1 | 2022-01-01 | 18:00
99 | Abul Khair 230 | 168.9 | 22 | 2022-01-01 | 13:00
100 | BSRM | 166 | 30 | 2022-01-01 | 1:00
101 | GPH Ispat | 99 | 27 | 2022-01-01 | 2:00
102 | Agrabad | 65 | 7 | 2022-01-01 | 18:00
103 | Goalpara | 26 | 4 | 2022-01-01 | 13:00
104 | Central s/s | 81 | 29 | 2022-01-01 | 18:30
105 | Noapara | 47 | 27 | 2022-01-01 | 20:00
106 | Jashore | 94 | 31 | 2022-01-01 | 13:00
107 | Benapol | 80 | 11 | 2022-01-01 | 18:30
108 | Jhenidah | 95 | 8 | 2022-01-01 | 18:00
109 | Bottail | 104 | 31 | 2022-01-01 | 13:00
110 | G.K Project | 47 | 1 | 2022-01-01 | 19:00
111 | Faridpur | 104 | 2 | 2022-01-01 | 19:30
112 | Rajbari | 44 | 8 | 2022-01-01 | 18:00
113 | Madaripur | 71 | 30 | 2022-01-01 | 21:00
114 | Sariatpur | 42 | 1 | 2022-01-01 | 20:00
115 | Gopalganj | 71 | 31 | 2022-01-01 | 18:30
116 | Bagerhat | 80 | 9 | 2022-01-01 | 18:30
117 | Mongla | 48 | 13 | 2022-01-01 | 12:00
118 | Satkhira | 78 | 10 | 2022-01-01 | 18:30
119 | Gallamari | 48 | 3 | 2022-01-01 | 13:00
120 | Magura | 56 | 8 | 2022-01-01 | 18:30
121 | Norail | 38 | 16 | 2022-01-01 | 18:30
122 | Chuadanga | 74 | 29 | 2022-01-01 | 19:00
123 | Barsal(N) | 30 | 7 | 2022-01-01 | 19:00
124 | Barsal(S) | 78 | 9 | 2022-01-01 | 19:30
125 | Patuakhali | 80 | 17 | 2022-01-01 | 20:00
126 | Bhandaria | 40 | 24 | 2022-01-01 | 20:00
127 | Borguna | 12 | 1 | 2022-01-01 | 19:30
128 | Borhan Uddin | 32 | 18 | 2022-01-01 | 22:00
129 | Ishurdi | 52 | 10 | 2022-01-01 | 18:30
130 | Ruppur Paromanobik | 4 | 7 | 2022-01-01 | 15:00
131 | Natore | 100 | 22 | 2022-01-01 | 20:00
132 | Bogura | 117 | 30 | 2022-01-01 | 13:00
133 | Naogaon | 102 | 30 | 2022-01-01 | 13:00
134 | Rajshahi | 100 | 3 | 2022-01-01 | 21:00
135 | Rajshahi New | 39 | 24 | 2022-01-01 | 20:00
136 | C.Nawabganj | 55 | 31 | 2022-01-01 | 12:00
137 | Amnura | 48 | 16 | 2022-01-01 | 19:00
138 | Pabna | 92 | 4 | 2022-01-01 | 18:30
139 | Shahjadpur | 79 | 6 | 2022-01-01 | 19:00
140 | Serajganj | 83 | 31 | 2022-01-01 | 19:00
141 | Niyamatpur | 96 | 29 | 2022-01-01 | 12:00
142 | Joypurhat | 53 | 29 | 2022-01-01 | 18:30
143 | Sherpur(Bogura) | 54 | 26 | 2022-01-01 | 18:30
144 | Mohastangar | 50 | 9 | 2022-01-01 | 18:00
145 | Bangura | 23 | 11 | 2022-01-01 | 18:00
146 | Rangpur | 116 | 31 | 2022-01-01 | 18:30
147 | Lalmonirhat | 43 | 29 | 2022-01-01 | 18:30
148 | Saidpur | 96 | 29 | 2022-01-01 | 18:30
149 | Purbasadipur | 98 | 13 | 2022-01-01 | 19:00
150 | Thakurgaon | 68 | 4 | 2022-01-01 | 18:30
151 | Palshbari | 102 | 26 | 2022-01-01 | 12:00
152 | Barapukuria | 57 | 26 | 2022-01-01 | 13:00
153 | Panchugar | 48 | 26 | 2022-01-01 | 19:00
154 | Joldhaka | 58 | 29 | 2022-01-01 | 18:30
155 | Kurigram | 58 | 22 | 2022-01-01 | 18:00
156 | Mitha Pukur | 48 | 8 | 2022-01-01 | 18:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:January 2022
Area | MW | Date | Hour | Remarks
Dhaka | 45577.875 | 21.01.2022 | 21:00
Chattogram | 1233 | 25.01.2022 | 18:00
Khulna | 1148 | 08.01.2022 | 18:30
Rajshahi | 1027 | 29.01.2022 | 19:00
Cumilla | 837 | 22.01.2022 | 18:30
Mymensingh | 899 | 29.01.2022 | 18:30
Sylhet | 358 | 11.01.2022 | 18:30
Barisal | 283 | 01.01.2022 | 21:00
Rangpur | 747 | 29.01.2022 | 18:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: January '2022
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 428 | 23 | 2022-01-01 | 20:00 | 407 | 1 | 2022-01-01 | 12:00
2 | Bheramara | 400 | 417 | 10 | 2022-01-01 | 20:00 | 393 | 1 | 2022-01-01 | 18:30
3 | Ashuganj(N) | 400 | 424 | 30 | 2022-01-01 | 6:00 | 386 | 11 | 2022-01-01 | 12:00
4 | Payra | 400 | 423 | 6 | 2022-01-01 | 21:00 | 404 | 8 | 2022-01-01 | 1:00
5 | Kaliakoir | 400 | 423 | 0 | 2022-01-01 | 24:00 | 396 | 11 | 2022-01-01 | 12:00
6 | Bhulta | 400 | 425 | 30 | 2022-01-01 | 6:00 | 384 | 9 | 2022-01-01 | 15:00
7 | Gopalganj | 400 | 421 | 6 | 2022-01-01 | 15:00 | 369 | 7 | 2022-01-01 | 8:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 244 | 25 | 2022-01-01 | 20:00 | 227 | 2 | 2022-01-01 | 10:00
2 | Ishurdi | 230 | 248 | 13 | 2022-01-01 | 24:00 | 224 | 27 | 2022-01-01 | 9:00
3 | Ashuganj | 230 | 253 | 17 | 2022-01-01 | 5:00 | 242 | 20 | 2022-01-01 | 16:00
4 | Serajganj | 230 | 245 | 1 | 2022-01-01 | 1:00 | 234 | 9 | 2022-01-01 | 12:00
5 | Baghabari | 230 | 245 | 13 | 2022-01-01 | 24:00 | 226 | 27 | 2022-01-01 | 8:00
6 | Barapukuria | 230 | 239 | 12 | 2022-01-01 | 23:00 | 225 | 25 | 2022-01-01 | 18:30
7 | Bogura | 230 | 244 | 7 | 2022-01-01 | 1:00 | 226 | 30 | 2022-01-01 | 9:00
8 | Rajshahi | 230 | 247 | 13 | 2022-01-01 | 24:00 | 220 | 27 | 2022-01-01 | 9:00
9 | Khulna South | 230 | 250 | 4 | 2022-01-01 | 5:00 | 220 | 26 | 2022-01-01 | 19:00
10 | Rampura | 230 | 245 | 28 | 2022-01-01 | 23:00 | 230 | 9 | 2022-01-01 | 12:00
11 | Haripur | 230 | 244 | 17 | 2022-01-01 | 4:00 | 231 | 11 | 2022-01-01 | 12:00
12 | Hasnabad | 230 | 247 | 12 | 2022-01-01 | 22:00 | 231 | 20 | 2022-01-01 | 16:00
13 | Shyampur | 230 | 245 | 12 | 2022-01-01 | 21:00 | 230 | 20 | 2022-01-01 | 16:00
14 | Aminbazar | 230 | 247 | 6 | 2022-01-01 | 1:00 | 234 | 9 | 2022-01-01 | 2:00
15 | Tongi | 230 | 246 | 12 | 2022-01-01 | 20:00 | 136 | 28 | 2022-01-01 | 8:00
16 | Comilla (N) | 230 | 245 | 12 | 2022-01-01 | 23:00 | 231 | 20 | 2022-01-01 | 16:00
17 | Hathazari | 230 | 248 | 14 | 2022-01-01 | 7:00 | 228 | 8 | 2022-01-01 | 10:00
18 | Megnaghat | 230 | 252 | 18 | 2022-01-01 | 3:00 | 239 | 23 | 2022-01-01 | 11:00
19 | Fenchuganj | 230 | 249 | 9 | 2022-01-01 | 4:00 | 237 | 20 | 2022-01-01 | 11:00
20 | Siddhirganj | 230 | 245 | 7 | 2022-01-01 | 9:00 | 231 | 20 | 2022-01-01 | 16:00
21 | Maniknagar | 230 | 243 | 7 | 2022-01-01 | 9:00 | 230 | 20 | 2022-01-01 | 16:00
22 | Old Airport | 230 | 247 | 30 | 2022-01-01 | 3:00 | 232 | 11 | 2022-01-01 | 12:00
23 | Barisal | 230 | 248 | 1 | 2022-01-01 | 9:00 | 234 | 8 | 2022-01-01 | 18:30
24 | Bhola 225 MW | 230 | 250 | 2 | 2022-01-01 | 4:00 | 239 | 30 | 2022-01-01 | 7:00
25 | AKSML | 230 | 246 | 5 | 2022-01-01 | 17:00 | 220 | 20 | 2022-01-01 | 16:00
26 | BSRM | 230 | 246 | 4 | 2022-01-01 | 24:00 | 224 | 20 | 2022-01-01 | 16:00
27 | Bibiyana | 230 | 251 | 29 | 2022-01-01 | 24:00 | 233 | 20 | 2022-01-01 | 16:00
28 | Bhulta | 230 | 246 | 7 | 2022-01-01 | 13:00 | 232 | 11 | 2022-01-01 | 12:00
29 | Ashuganj (S) | 230 | 251 | 30 | 2022-01-01 | 6:00 | 238 | 11 | 2022-01-01 | 12:00
30 | Kaliakoir | 230 | 246 | 14 | 2022-01-01 | 6:00 | 232 | 9 | 2022-01-01 | 12:00
31 | GPH | 230 | 246 | 3 | 2022-01-01 | 6:00 | 219 | 20 | 2022-01-01 | 16:00
132 kV Substation
1 | Siddhirganj | 132 | 144 | 21 | 2022-01-01 | 0.041667 | 131 | 11 | 2022-01-01 | 0.5
2 | Munsiganj | 132 | 143 | 2 | 2022-01-01 | 0.8125 | 133 | 6 | 2022-01-01 | 0.70833
3 | Sonargaon | 132 | 143 | 21 | 2022-01-01 | 0.16667 | 132 | 8 | 2022-01-01 | 0.66667
4 | Shyampur | 132 | 141 | 21 | 2022-01-01 | 0.33333 | 127 | 20 | 2022-01-01 | 0.66667
5 | Bhulta | 132 | 142 | 21 | 2022-01-01 | 0.041667 | 122 | 6 | 2022-01-01 | 0.625
6 | Madanganj | 132 | 143 | 21 | 2022-01-01 | 0.58333 | 131 | 8 | 2022-01-01 | 0.66667
7 | Shitalakhya | 132 | 144 | 21 | 2022-01-01 | 0.77083 | 132 | 20 | 2022-01-01 | 0.66667
8 | Rahim Steal | 132 | 141 | 21 | 2022-01-01 | 0.77083 | 131 | 21 | 2022-01-01 | 0.5
9 | Matuail | 132 | 141 | 2 | 2022-01-01 | 0.79167 | 121 | 21 | 2022-01-01 | 0.5
10 | Ghorasal | 132 | 146 | 6 | 2022-01-01 | 0.875 | 136 | 21 | 2022-01-01 | 0.5
11 | Narsinghdi | 132 | 142 | 21 | 2022-01-01 | 0.041667 | 126 | 25 | 2022-01-01 | 0
12 | Haripur (SBU) | 132 | 141 | 1 | 2022-01-01 | 0.20833 | 131 | 27 | 2022-01-01 | 0.625
13 | Sreenagar | 132 | 142 | 21 | 2022-01-01 | 0.041667 | 130 | 11 | 2022-01-01 | 0.5
14 | Ullon | 132 | 143 | 10 | 2022-01-01 | 0.375 | 129 | 30 | 2022-01-01 | 0.5
15 | Hasnabad | 132 | 143 | 1 | 2022-01-01 | 0.083333 | 132 | 9 | 2022-01-01 | 0.625
16 | Magbazar | 132 | 142 | 10 | 2022-01-01 | 0.79167 | 128 | 24 | 2022-01-01 | 0.91667
17 | Maniknagar | 132 | 143 | 6 | 2022-01-01 | 0.25 | 129 | 10 | 2022-01-01 | 0.5
18 | Bangabhaban | 132 | 143 | 6 | 2022-01-01 | 0.25 | 130 | 9 | 2022-01-01 | 0.5
19 | Motijheel | 132 | 143 | 6 | 2022-01-01 | 0.25 | 126 | 21 | 2022-01-01 | 0.66667
20 | Narinda | 132 | 143 | 6 | 2022-01-01 | 0.25 | 129 | 31 | 2022-01-01 | 12:00
21 | Kazla | 132 | 143 | 6 | 2022-01-01 | 0.25 | 129 | 9 | 2022-01-01 | 0.54167
22 | Dhanmondi | 132 | 143 | 24 | 2022-01-01 | 0.79167 | 130 | 18 | 2022-01-01 | 0.66667
23 | Lalbag | 132 | 142 | 21 | 2022-01-01 | 0.16667 | 120 | 22 | 2022-01-01 | 0.77083
24 | Madartek | 132 | 143 | 10 | 2022-01-01 | 0.20833 | 127 | 27 | 2022-01-01 | 0.66667
25 | Dhaka University | 132 | 144 | 18 | 2022-01-01 | 0.75 | 130 | 9 | 2022-01-01 | 0.5
26 | Aftabnagar | 132 | 139 | 14 | 2022-01-01 | 0.125 | 128 | 27 | 2022-01-01 | 0.625
27 | Fatullah | 132 | 143 | 31 | 2022-01-01 | 18:30 | 129 | 27 | 2022-01-01 | 0.66667
28 | Nawabganj | 132 | 140 | 12 | 2022-01-01 | 0.95833 | 130 | 22 | 2022-01-01 | 0.5
29 | Keraniganj | 132 | 140 | 12 | 2022-01-01 | 0.91667 | 130 | 9 | 2022-01-01 | 0.5
30 | Banani | 132 | 140 | 21 | 2022-01-01 | 0.041667 | 128 | 27 | 2022-01-01 | 0.66667
31 | Mirpur | 132 | 141 | 1 | 2022-01-01 | 0.125 | 127 | 11 | 2022-01-01 | 0.5
32 | Kalyanpur | 132 | 141 | 1 | 2022-01-01 | 0.91667 | 129 | 11 | 2022-01-01 | 0.5
33 | Gulshan | 132 | 144 | 21 | 2022-01-01 | 0.25 | 127 | 27 | 2022-01-01 | 0.66667
34 | Uttara | 132 | 144 | 21 | 2022-01-01 | 0.16667 | 130 | 11 | 2022-01-01 | 0.5
35 | Uttara(New) | 132 | 143 | 21 | 2022-01-01 | 0.625 | 128 | 17 | 2022-01-01 | 0.66667
36 | Kamrangirchar | 132 | 140 | 16 | 2022-01-01 | 0.83333 | 130 | 27 | 2022-01-01 | 0.66667
37 | Savar | 132 | 141 | 1 | 2022-01-01 | 0.041667 | 128 | 11 | 2022-01-01 | 0.5
38 | Bhasantec | 132 | 142 | 7 | 2022-01-01 | 0.16667 | 126 | 9 | 2022-01-01 | 0.625
39 | Agargaon | 132 | 142 | 7 | 2022-01-01 | 0.16667 | 127 | 9 | 2022-01-01 | 0.625
40 | Satmosjid | 132 | 141 | 7 | 2022-01-01 | 0.16667 | 127 | 9 | 2022-01-01 | 0.5
41 | Tongi | 132 | 143 | 4 | 2022-01-01 | 0.95833 | 131 | 21 | 2022-01-01 | 0.77083
42 | Kabirpur | 132 | 147 | 31 | 2022-01-01 | 0.20833 | 128 | 19 | 2022-01-01 | 0.66667
43 | Basundhara | 132 | 144 | 21 | 2022-01-01 | 0.083333 | 130 | 23 | 2022-01-01 | 0.45833
44 | Purbachal | 132 | 145 | 24 | 2022-01-01 | 22:00 | 126 | 19 | 2022-01-01 | 0.625
45 | Manikganj | 132 | 145 | 13 | 2022-01-01 | 5:00 | 132 | 31 | 2022-01-01 | 0.5
46 | Joydevpur | 132 | 144 | 21 | 2022-01-01 | 0.20833 | 126 | 13 | 2022-01-01 | 17:00
47 | New Tongi | 132 | 144 | 21 | 2022-01-01 | 0.625 | 122 | 10 | 2022-01-01 | 0.625
48 | Kodda | 132 | 140 | 11 | 2022-01-01 | 0.95833 | 130 | 18 | 2022-01-01 | 0.66667
49 | Dhamrai | 132 | 141 | 21 | 2022-01-01 | 0.16667 | 124 | 10 | 2022-01-01 | 0.66667
50 | Rajendrapur | 132 | 140 | 17 | 2022-01-01 | 0.25 | 115 | 22 | 2022-01-01 | 0.77083
51 | Tongi Millgate | 132 | 141 | 1 | 2022-01-01 | 0.25 | 129 | 22 | 2022-01-01 | 0.45833
52 | Valuka | 132 | 142 | 21 | 2022-01-01 | 0.25 | 112 | 29 | 2022-01-01 | 0.54167
53 | Tangail | 132 | 138 | 1 | 2022-01-01 | 0.041667 | 125 | 25 | 2022-01-01 | 0.54167
54 | Mymensing | 132 | 139 | 21 | 2022-01-01 | 0.041667 | 118 | 18 | 2022-01-01 | 0.75
55 | Kishorganj | 132 | 138 | 21 | 2022-01-01 | 0.041667 | 123 | 19 | 2022-01-01 | 0.77083
56 | Netrokona | 132 | 137 | 21 | 2022-01-01 | 0.125 | 114 | 18 | 2022-01-01 | 0.75
57 | Jamalpur | 132 | 142 | 13 | 2022-01-01 | 0.91667 | 123 | 24 | 2022-01-01 | 0.20833
58 | Sherpur | 132 | 141 | 21 | 2022-01-01 | 0.16667 | 121 | 24 | 2022-01-01 | 0.20833
59 | Srimongal | 132 | 145 | 21 | 2022-01-01 | 0.20833 | 135 | 20 | 2022-01-01 | 0.5
60 | Shahjibazar | 132 | 140 | 21 | 2022-01-01 | 0.041667 | 133 | 16 | 2022-01-01 | 0.77083
61 | Fenchuganj | 132 | 142 | 29 | 2022-01-01 | 1899-12-31 | 129 | 21 | 2022-01-01 | 0.75
62 | Khulawara | 132 | 140 | 29 | 2022-01-01 | 0.95833 | 133 | 21 | 2022-01-01 | 0.33333
63 | Sylhet | 132 | 142 | 21 | 2022-01-01 | 0.125 | 131 | 15 | 2022-01-01 | 0.75
64 | Chattak | 132 | 140 | 21 | 2022-01-01 | 0.29167 | 131 | 15 | 2022-01-01 | 0.75
65 | Sunamganj | 132 | 143 | 21 | 2022-01-01 | 0.125 | 130 | 15 | 2022-01-01 | 0.75
66 | Biani Bazar | 132 | 137 | 24 | 2022-01-01 | 0.16667 | 131 | 29 | 2022-01-01 | 0.66667
67 | Comilla(South) | 132 | 139 | 23 | 2022-01-01 | 0.41667 | 123 | 16 | 2022-01-01 | 0.5
68 | Comilla (North) | 132 | 147 | 12 | 2022-01-01 | 0.041667 | 125 | 21 | 2022-01-01 | 0.77083
69 | Chandpur | 132 | 146 | 11 | 2022-01-01 | 0.20833 | 122 | 21 | 2022-01-01 | 0.77083
70 | Feni | 132 | 145 | 18 | 2022-01-01 | 0.95833 | 120 | 21 | 2022-01-01 | 0.75
71 | Chowmuhani | 132 | 144 | 23 | 2022-01-01 | 0.25 | 130 | 21 | 2022-01-01 | 0.77083
72 | Ashuganj | 132 | 142 | 5 | 2022-01-01 | 0.125 | 130 | 21 | 2022-01-01 | 0.83333
73 | Daudkandi | 132 | 144 | 10 | 2022-01-01 | 0.79167 | 122 | 21 | 2022-01-01 | 0.77083
74 | Brahminbaria | 132 | 138 | 1 | 2022-01-01 | 0.041667 | 122 | 21 | 2022-01-01 | 0.77083
75 | Ramganj | 132 | 143 | 9 | 2022-01-01 | 0.79167 | 125 | 21 | 2022-01-01 | 0.77083
76 | Chaddagram | 132 | 146 | 12 | 2022-01-01 | 0.75 | 132 | 21 | 2022-01-01 | 0.75
77 | PHP | 132 | 143 | 5 | 2022-01-01 | 0.25 | 132 | 7 | 2022-01-01 | 0.54167
78 | Kochua | 132 | 145 | 14 | 2022-01-01 | 0.16667 | 134 | 20 | 2022-01-01 | 0.5
79 | Madanhat | 132 | 145 | 23 | 2022-01-01 | 0.83333 | 133 | 21 | 2022-01-01 | 0.375
80 | Hathazari | 132 | 145 | 14 | 2022-01-01 | 0.375 | 124 | 27 | 2022-01-01 | 0.875
81 | Khulshi | 132 | 143 | 16 | 2022-01-01 | 0.79167 | 129 | 20 | 2022-01-01 | 0.66667
82 | Halishahar | 132 | 143 | 2 | 2022-01-01 | 0.29167 | 127 | 20 | 2022-01-01 | 0.66667
83 | Baraulia | 132 | 144 | 4 | 2022-01-01 | 0 | 129 | 20 | 2022-01-01 | 0.66667
84 | Sikalbaha | 132 | 144 | 21 | 2022-01-01 | 0.77083 | 130 | 20 | 2022-01-01 | 0.66667
85 | Dohazari | 132 | 142 | 28 | 2022-01-01 | 0.33333 | 130 | 6 | 2022-01-01 | 0.70833
86 | Cox'sbazar | 132 | 138 | 2 | 2022-01-01 | 0.375 | 114 | 20 | 2022-01-01 | 0.66667
87 | Chandraghona | 132 | 145 | 24 | 2022-01-01 | 0.91667 | 130 | 20 | 2022-01-01 | 0.66667
88 | Kaptai | 132 | 142 | 2 | 2022-01-01 | 0.91667 | 126 | 15 | 2022-01-01 | 0.375
89 | A. Khaer Stl. | 132 | 143 | 7 | 2022-01-01 | 0.54167 | 133 | 5 | 2022-01-01 | 0.45833
90 | Bakulia | 132 | 143 | 2 | 2022-01-01 | 0.95833 | 129 | 20 | 2022-01-01 | 0.66667
91 | Julda | 132 | 143 | 2 | 2022-01-01 | 0.16667 | 130 | 20 | 2022-01-01 | 0.66667
92 | TK Chemical | 132 | 149 | 22 | 2022-01-01 | 0.91667 | 131 | 20 | 2022-01-01 | 0.625
93 | Modern Steel | 132 | 143 | 5 | 2022-01-01 | 0.29167 | 131 | 20 | 2022-01-01 | 0.625
94 | Shahmirpur | 132 | 144 | 3 | 2022-01-01 | 0.25 | 130 | 20 | 2022-01-01 | 0.66667
95 | Khagrachhari | 132 | 143 | 3 | 2022-01-01 | 0.25 | 130 | 20 | 2022-01-01 | 0.66667
96 | Matarbari | 132 | 142 | 1 | 2022-01-01 | 0.33333 | 120 | 7 | 2022-01-01 | 0.95833
97 | Baroiar Hat | 132 | 144 | 5 | 2022-01-01 | 0.29167 | 132 | 28 | 2022-01-01 | 0.41667
98 | Rangamati | 132 | 144 | 14 | 2022-01-01 | 0.083333 | 129 | 20 | 2022-01-01 | 0.66667
99 | Agrabad | 132 | 144 | 3 | 2022-01-01 | 0.25 | 128 | 20 | 2022-01-01 | 0.66667
100 | Goalpara | 132 | 143 | 1 | 2022-01-01 | 0.125 | 127 | 27 | 2022-01-01 | 0.5
101 | Khulna Central | 132 | 141 | 6 | 2022-01-01 | 0.41667 | 127 | 26 | 2022-01-01 | 0.79167
102 | Noapara | 132 | 141 | 2 | 2022-01-01 | 0.083333 | 123 | 26 | 2022-01-01 | 0.54167
103 | Jessore | 132 | 140 | 4 | 2022-01-01 | 0.16667 | 124 | 22 | 2022-01-01 | 0.77083
104 | Benapol | 132 | 141 | 1 | 2022-01-01 | 0.083333 | 122 | 26 | 2022-01-01 | 0.54167
105 | Jhenida | 132 | 141 | 4 | 2022-01-01 | 0.041667 | 125 | 26 | 2022-01-01 | 0.54167
106 | Bottail | 132 | 141 | 7 | 2022-01-01 | 0.041667 | 127 | 27 | 2022-01-01 | 0.375
107 | G.K Project | 132 | 143 | 7 | 2022-01-01 | 0.20833 | 131 | 16 | 2022-01-01 | 0.45833
108 | Faridpur | 132 | 142 | 4 | 2022-01-01 | 0.33333 | 130 | 8 | 2022-01-01 | 0.79167
109 | Rajbari | 132 | 142 | 8 | 2022-01-01 | 0.375 | 128 | 27 | 2022-01-01 | 0.77083
110 | Madaripur | 132 | 145 | 4 | 2022-01-01 | 0.083333 | 132 | 24 | 2022-01-01 | 0.75
111 | Sariatpur | 132 | 145 | 30 | 2022-01-01 | 0.29167 | 133 | 8 | 2022-01-01 | 0.79167
112 | Gopalganj | 132 | 145 | 5 | 2022-01-01 | 0.29167 | 134 | 8 | 2022-01-01 | 0.75
113 | Bagerhat | 132 | 142 | 4 | 2022-01-01 | 0.375 | 125 | 26 | 2022-01-01 | 0.8125
114 | Mongla | 132 | 141 | 4 | 2022-01-01 | 0.375 | 125 | 26 | 2022-01-01 | 0.8125
115 | Satkhira | 132 | 142 | 19 | 2022-01-01 | 0.58333 | 124 | 26 | 2022-01-01 | 0.8125
116 | Gallamari | 132 | 144 | 19 | 2022-01-01 | 0.70833 | 130 | 4 | 2022-01-01 | 0.79167
117 | Magura | 132 | 142 | 4 | 2022-01-01 | 0.16667 | 123 | 8 | 2022-01-01 | 0.75
118 | Norail | 132 | 141 | 1 | 2022-01-01 | 0.083333 | 124 | 26 | 2022-01-01 | 0.5
119 | Chuadanga | 132 | 141 | 5 | 2022-01-01 | 0.083333 | 120 | 30 | 2022-01-01 | 0.5
120 | Barisal(N) | 132 | 146 | 5 | 2022-01-01 | 0.16667 | 134 | 8 | 2022-01-01 | 0.75
121 | Barisal(S) | 132 | 145 | 2 | 2022-01-01 | 0.16667 | 134 | 8 | 2022-01-01 | 0.77083
122 | Patuakhali | 132 | 143 | 1 | 2022-01-01 | 0.625 | 131 | 8 | 2022-01-01 | 0.77083
123 | Bhandaria | 132 | 145 | 15 | 2022-01-01 | 0.125 | 125 | 30 | 2022-01-01 | 0.375
124 | Borguna | 132 | 146 | 29 | 2022-01-01 | 0.20833 | 134 | 8 | 2022-01-01 | 0.75
125 | Jhenaidah(New) | 132 | 142 | 4 | 2022-01-01 | 0.16667 | 125 | 27 | 2022-01-01 | 0.375
126 | Ishurdi | 132 | 144 | 25 | 2022-01-01 | 0.125 | 130 | 27 | 2022-01-01 | 0.375
127 | Ruppur paromanobik | 132 | 142 | 3 | 2022-01-01 | 0.70833 | 130 | 23 | 2022-01-01 | 0.41667
128 | Natore | 132 | 143 | 5 | 2022-01-01 | 0.041667 | 131 | 23 | 2022-01-01 | 0.41667
129 | Bogra | 132 | 144 | 12 | 2022-01-01 | 0.95833 | 131 | 23 | 2022-01-01 | 0.41667
130 | Noagaon | 132 | 142 | 12 | 2022-01-01 | 0.95833 | 123 | 23 | 2022-01-01 | 0.41667
131 | Rajshahi | 132 | 141 | 5 | 2022-01-01 | 0.70833 | 125 | 27 | 2022-01-01 | 0.33333
132 | Rajshahi New | 132 | 142 | 3 | 2022-01-01 | 0.70833 | 125 | 27 | 2022-01-01 | 0.375
133 | C.Nawabganj | 132 | 141 | 12 | 2022-01-01 | 0.91667 | 126 | 23 | 2022-01-01 | 0.41667
134 | Amnura | 132 | 141 | 2 | 2022-01-01 | 0.8125 | 124 | 27 | 2022-01-01 | 0.33333
135 | Pabna | 132 | 144 | 7 | 2022-01-01 | 0.75 | 129 | 27 | 2022-01-01 | 0.375
136 | Shahjadpur | 132 | 148 | 4 | 2022-01-01 | 0.16667 | 134 | 30 | 2022-01-01 | 0.5
137 | Serajganj | 132 | 143 | 12 | 2022-01-01 | 1899-12-31 | 129 | 23 | 2022-01-01 | 0.41667
138 | Niyamatpur | 132 | 142 | 12 | 2022-01-01 | 0.95833 | 117 | 30 | 2022-01-01 | 0.375
139 | Joypurhat | 132 | 142 | 12 | 2022-01-01 | 0.95833 | 118 | 30 | 2022-01-01 | 0.5
140 | Sherpur(Bogura) | 132 | 143 | 5 | 2022-01-01 | 0.083333 | 130 | 30 | 2022-01-01 | 0.5
141 | Mohastangor | 132 | 142 | 12 | 2022-01-01 | 0.95833 | 128 | 30 | 2022-01-01 | 0.5
142 | Bangura | 132 | 145 | 7 | 2022-01-01 | 0.16667 | 132 | 27 | 2022-01-01 | 0.375
143 | Rangpur | 132 | 139 | 4 | 2022-01-01 | 0.25 | 121 | 29 | 2022-01-01 | 0.77083
144 | Lalmonirhat | 132 | 139 | 5 | 2022-01-01 | 0.25 | 118 | 27 | 2022-01-01 | 0.33333
145 | Saidpur | 132 | 137 | 6 | 2022-01-01 | 0.25 | 120 | 19 | 2022-01-01 | 18;30
146 | Purbasadipur | 132 | 136 | 12 | 2022-01-01 | 0.20833 | 115 | 22 | 2022-01-01 | 0.77083
147 | Thakurgaon | 132 | 134 | 1 | 2022-01-01 | 0.041667 | 112 | 22 | 2022-01-01 | 0.77083
148 | Palashbari | 132 | 140 | 5 | 2022-01-01 | 0.041667 | 124 | 30 | 2022-01-01 | 0.375
149 | Barapukuria | 132 | 139 | 12 | 2022-01-01 | 0.95833 | 122 | 4 | 2022-01-01 | 0.77083
150 | Panchagar | 132 | 137 | 30 | 2022-01-01 | 0.25 | 115 | 22 | 2022-01-01 | 0.77083
151 | Joldhaka | 132 | 137 | 12 | 2022-01-01 | 0.95833 | 116 | 22 | 2022-01-01 | 0.77083
152 | Kurigram | 132 | 140 | 12 | 2022-01-01 | 0.95833 | 118 | 29 | 2022-01-01 | 0.58333
153 | Mithapukur | 132 | 141 | 1 | 2022-01-01 | 0.041667 | 126 | 23 | 2022-01-01 | 0.375
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:January 2022
Name of the | Auto transformer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 42 | 140
Hasnabad | TR2 | 225 | 42 | 140 | 03/01/2022 | 23:00
| TR3 | 225 | 42 | 140
| TR1 | 225 | 140 | 360 | 10.01.2022 | 15:00
Tongi | TR2 | 225 | 140 | 360
| TR3 | 225 | 140 | 360
Haripur | TR1 | 225 | 85 | 215
| TR2 | 225 | 85 | 215 | 02.01.2022 | 12:00
| TR3 | 225 | 85 | 215
| TR1 | 225 | 128 | 305
Rampura | TR2 | 225 | 128 | 305 | 13.01.2022 | 13:00
| TR3 | 225 | 128 | 305
Keraniganj | ATR1 | 300 | 72 | 184
| ATR2 | 300 | 72 | 184 | 06.01.2022 | 13:00
| ATR3 | 300 | 72 | 184
| TR1 | 225 | 80 | 200
Aminbazar | TR2 | 225 | 80 | 200 | 17/01/2022 | 22:00
| TR3 | 225 | 73 | 180
Agargaon | TR1 | 300 | 103 |  |  |  | S/D
| TR2 | 300 | 103 | 514 | '26/1/2022 | 1:00
Maniknagar | TR1 | 300 | 92 | 240 | 25/01/2022 | 13:00
| TR2 | 300 | 92 | 240
Cumilla (N) | TR1 | 225 | 152 | 404 | '21/1/2022 | 1:00
| TR2 | 225 | 150 | 393
Fenchuganj | AT2 | 300 | 159 | 387 | 16/01/2022 | 19:00
| MT1 | 150 | 67 | 290
Hathazari | MT2 | 150 | 67 | 290 | 02/01/2022 | 11:00
| MT3 | 150 | 67 | 290
| MT4 | 150 | 67 | 290
| TR1 | 225 | 87 | 220
Ishurdi | TR2 | 225 | 87 | 220 | 06/01/2022 | 18:30
| TR3 | 225 | 87 | 220
Khulna(S) | TR1 | 225 | 70 | 170
| TR2 | 225 | 70 | 170 | 08/01/2022 | 20:00
| TR3 | 300 | 88 | 218
Bogura | TR1 | 225 | 86 | 398 | 30.01.22 | 8:00
| TR2 | 225 | 86 | 398
| TR3 | 225 | 114 | 518
Baghabari | TR1 | 300 | 110 | 300 | 30.01.22 | 10:00
| TR2 | 225 | 88 | 230
Rajshahi | ATR-01 | 300 | 81 | 202 | 25.01.2022 | 9:00
| ATR-02 | 300 | 81 | 202
Barapukuria | TR1 | 225 | 138 | 610 |  |  | Due to unavailability of 230 kV side meters
| TR2 | 225 | 140 | 660 | 30.01.2022 | 18:30 | 132 kV current is being provided
| TR6 | 300 | 183 | 864
Bheramara | Transformer-1 | 225 | 95 | 234 | 06.01.2022 | 19:00
| Transformer-2 | 225 | 95 | 234
Shyampur | ATR-01 | 300 | 134 | 321 | 13.01.2022 | 12:00
| ATR-02 | 300 | 134 | 321
Kaliakoir | TR1 | 300 | 98.5 | 263 | 26.01.2022 | 18:30
Sikalbaha | ATR-1 | 300 | 117 | 214 | 30.01.2022 | 19:00
| ATR-2 | 300 | 117 | 214
Jhenaidah | T1(230/132 kV) | 300 | 142 | 361 | 22.01.2022 | 13:00
| T2(230/132 kV) | 300 | 142 | 361
Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:January 2022
Name of the | Transformer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps (400 kV side) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 188.3 | 265.7 | 17.01.2022 | 4:00
| TR2(400/230 kV) | 520 | 189.9 | 269
| TR1(400/132 kV) | 325 | 265.5 | 398 | 19.01.2022 | 18:45
| TR2(400/132 kV) | 325 | 266.5 | 400
Bibiyana | ICT1(400/230 kV) | 520 | 127 | 194
| ICT2(400/230kV) | 520 | 124 | 189 | 15.01.2022 | 13:00
Bhulta | ATR1(400/230 kV) | 520 | 180 | 299 | 06.01.2022 | 12:30
| ATR2(400/230kV) | 520 | 180 | 299
Ashuganj(N) | GSUT1(400/230 kV) | 567 | 184 | 248 | 30.01.2022 | 5:57
Gopalganj | ATR1(400/138 kV) | 325 | 268 | 386 | 13.01.2022 | 20:00
| ATR2(400/138kV) | 325 | 268 | 386
Payra | GSUT1 | 270 | 185.72 | 792.3 | 13/01/2022 | 19:59
| GSUT2 | 270 | 180.34 | 771.13
| GSUT3 | 270 | 181.92 | 775.7
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.
594
423

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:January2022 | [6 empty] | (For Evening Peak) | [7 empty] | Month:January2022 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2022-01-01 | 8985 | 8985 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-01 | 7339 | 7339 | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-02 | 9156 | 9156 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-02 | 7659 | 7659 | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-03 | 9342 | 9342 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-03 | 6698 | 6698 | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-04 | 9406 | 9406 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-04 | 7954 | 7954 | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-05 | 9239 | 9239 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-05 | 7756 | 7756 | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-06 | 9338 | 9338 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-06 | 8136 | 8136 | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-07 | 8218 | 8218 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-07 | 6932 | 6932 | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-08 | 9513 | 9513 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-08 | 7280 | 7280 | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-09 | 9537 | 9537 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-09 | 8149 | 8149 | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-10 | 9612 | 9612 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-10 | 8242 | 8242 | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-11 | 9726 | 9726 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-11 | 8457 | 8457 | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-12 | 9583 | 9583 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-12 | 8347 | 8347 | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-13 | 9643 | 9643 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-13 | 8555 | 8555 | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-14 | 8349 | 8349 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-14 | 7236 | 7236 | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-15 | 9604 | 9604 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-15 | 7688 | 7688 | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-16 | 9676 | 9676 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-16 | 8286 | 8286 | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-17 | 9771 | 9771 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-17 | 8276 | 8276 | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-18 | 9829 | 9829 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-18 | 8453 | 8453 | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-19 | 9853 | 9853 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-19 | 8575 | 8575 | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-20 | 9783 | 9783 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-20 | 8645 | 8645 | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-21 | 8615 | 8615 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-21 | 7503 | 7503 | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-22 | 9673 | 9673 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-22 | 8154 | 8154 | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-23 | 9735 | 9735 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-23 | 8883 | 8883 | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-24 | 9894 | 9894 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-24 | 8804 | 8804 | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-25 | 10021 | 10021 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-25 | 8842 | 8842 | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-26 | 9699 | 9699 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-26 | 8795 | 8795 | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-27 | 9959 | 9959 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-27 | 8843 | 8843 | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-28 | 8683 | 8683 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-28 | 7718 | 7718 | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-29 | 9869 | 9869 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-29 | 8280 | 8280 | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-30 | 9867 | 9867 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-30 | 8945 | 8945 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
2022-01-31 | 9801 | 9801 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-31 | 8869 | 8869 | - | - | - | - | - | - | - | - | - | - | - | -
Evening Peak | Max. L/S | 0 | - | -
| Min. L/S | 0 | - | -
| No. of Days | - | [12 empty] | 0 | 0 | 1
[15 empty] | 0 | 0 | 2
| Max. L/S | - | - | - | [10 empty] | 0 | 0 | 3
Day Peak | Min. L/S | - | - | - | [10 empty] | 0 | 0 | 4
| No. of Days | - | - | - | [10 empty] | 0 | 0 | 5
[15 empty] | 0 | 0 | 6
| Max. L/S | - | - | - | [10 empty] | 0 | 0 | 7
Full Day | Min. L/S | - | - | - | [10 empty] | 0 | 0 | 8
| No. of Days | - | [12 empty] | 0 | 0 | 9
| Average L/S | #DIV/0! | [12 empty] | 0 | 0 | 10
[15 empty] | 0 | 0 | 11
[15 empty] | 0 | 0 | 12
[15 empty] | 0 | 0 | 13
[15 empty] | 0 | 0 | 14
[15 empty] | 0 | 0 | 15
[15 empty] | 0 | 0 | 16
[15 empty] | 0 | 0 | 17
[15 empty] | 0 | 0 | 18
[15 empty] | 0 | 0 | 19
[15 empty] | 0 | 0 | 20
[15 empty] | 0 | 0 | 21
[15 empty] | 0 | 0 | 22
[15 empty] | 0 | 0 | 23
[15 empty] | 0 | 0 | 24
[15 empty] | 0 | 0 | 25
[15 empty] | 0 | 0 | 26
[15 empty] | 0 | 0 | 27
[15 empty] | 0 | 0 | 28
[15 empty] | 0 | 0 | 29
[15 empty] | 0 | 0 | 30
[15 empty] | #REF! | #REF! | 31

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:January 2022
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 10021 | 2022-01-25 | 19:00
2 | Maximum Day Peak Genaration | MW | 8945 | 2022-01-30 | 12:00
3 | Maximum Evening Peak Demand | MW | 10021 | 2022-01-25 | 12:00
4 | Minimum Generation | MW | 5475 | 2022-01-08 | 6:00
5 | Average of the daily evening peak Genaration | MW | 9483.1935
6 | Average of the daily day peak Genaration | MW | 8138.6774
7 | Maximum load shed | MW | 0 | - | -
8 | Minimum load shed | MW | 0 | - | -
9 | Total nos. of load shed days | Day | 0
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 0
11 | Total Generation | MkWh | 5820.076
12 | Total Generation by BPDB | MkWh | 1181.174 | % of total Gen. | 20.29%
13 | Total Generation by IPP | MkWh | 2319.7869 | '' | 39.86%
14 | A) Total Generation by Generation Companies | MkWh | 1256.6407 | '' | 21.59%
| B) Total Generation by REB | MkWh | 117.4558 | " | 2.018%
| C) Total Generation by RENTAL | MkWh | 409.5082 | " | 7.036%
| D) Total Imported from India (BIPTC) | MkWh | 474.2931 | " | 8.149%
| E) Total Imported from Tripura, India (A.C) | MkWh | 61.2173 | " | 1.052%
15 | Fuel wise Generation.
| A) Gas | MkWh | 2951.4743 | % of total Gen. | 50.71%
| B) Oil | MkWh | 1827.5534 | '' | 31.4%
| C) Hydro | MkWh | 70.6636 | '' | 1.214%
| D) Solar | MkWh | 27.2583 | '' | 0.4683%
| E) Coal | MkWh | 407.6161 | '' | 7.004%
| F) BIPTC (Import from India) | MkWh | 474.2931 | '' | 8.149%
| G) A.C (Import from Tripura, India) | MkWh | 61.2173 | '' | 1.052%
16 | Maximun of the daily total Generation . | MkWh | 199.0372 | 2022-01-25
17 | Monthly Load factor | % | 78.0725
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 22040.614
| A) Gas | M.Taka | 2819.7046
| B) Liquid fuel | M.Taka | 14524.0602
| C) Coal | M.Taka | 1944.5149
| D) BIPTC (Import from India) | M.Taka | 2328.8268
| E) Tripura(Import from India) | M.Taka | 423.5074
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 780.6419 | 2022-01-05
| A) Gas | M.Taka | 98.4116 | 2022-01-01
| B) Liquid fuel | M.Taka | 629.8829 | 2022-01-05
| C) Coal | M.Taka | 67.6869 | 2022-01-06
| D) BIPTC (Import from India) | M.Taka | 89.1295 | 2022-01-23
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 5.3592
| B) Excluding Hydro & Solar | Taka/kWhR | 5.4502
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 97.2 | 31/01/2022 | 06:00
b) | Actual | FT (MSL) | 93.81 | 31/01/2022 | 06:00
22 | Peak Genaration of January 2021 | MW | 9380 | 19-01-2021 | 19:00
23 | Peak Demand of January 2021 | MW | 9380 | 19-01-2021 | 19:00
24 | Maximum peak Generation recorded upto 31/01/2022 | MW | 13792 | 27/04/21 | 20:00
25 | Maximum peak Demand recorded upto 31/01/2022 | MW | 14097 | 27/04/21 | 12:00
26 | Maximum load shed recorded upto 31/01/2022 | MW | 1459 | 04/05/2010 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.