## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-07-31 | Wednesday
|  | Date (day): | 2019-07-31 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12809 | MW |  |  | (b) At Evening Peak Hour : |  | 14643 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-07-30 | 2019-07-31 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 32 | 32 | 32 | 32 |  | 53 | #2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 219 | 220 | 220 | 220
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 220 | 200 | 220 | 220
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 73 | 50 | 50 | 50
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 90 | 22 | 100 | 100
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 340 | 340 | 370 | 370 |  |  | FGMO
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 283 | 252 | 250 | 250 |  |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 340 | 300 | 300 | 300 |  |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 24 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 230 | 230 | 280 | 280 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 15 | 32 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 70 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| Siddhirganj Desh |  | HSD | QRPP | 96*1.2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217 | 217 | 217 | 3 | 313 | 10 | 10 |  |  | Test
| Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 75 | 100 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 13 | 48 | 47 | 47
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 130 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 17 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 68 | 72 | 72 | 72 |  | 36 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 46 | 57 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 42 | 42 | 42 | 42 |  | 10 | Engine problem
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 14 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 103 | 112 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 102 | 100 | 100 | 100
| Dhaka area Total |  |  |  |  | 5929 | 5693 | 2360 | 2952 | 3455 | 4057 | 355 | 792
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 95 | 95 | 95 | 95 | 85 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 11 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 13 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 213 | 211 | 220 | 220
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 206 | 204 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 130 | 131 | 136 | 136
44 | Sikalbaha 51 MW PP(Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Contract expired
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 17 | 17 | 50 | 100
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 0 | 85
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 10 | 100 | 100
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 60 | 100 | 100 | 100
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 34 | 15 | 35
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 5 | 52 | 90 | 96 |  |  | Engine problem
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 1.83 | 0 | 4.4 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 182 | 213 | 230 | 260
| Jodiac Power |  | HFO | IPP | 54.36 | 0 | 0 | 11 | 0 | 0 | 0
| Karnaphuli Power Lid. |  | HFO | IPP | 110 | 0 | 0 | 0 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2113 | 2053 | 1076.83 | 1369 | 1492.4 | 1659 | 145 | 0
54 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 100 | 80 | 100 | 100
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
55 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 189 | 184 | 220 | 220 |  |  | FGMO
56 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 310 | 360 | 360
57 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 290 | 340 | 360 |  |  | FGMO
58 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 27 | 37 | 37 | 37 |  | 8 | Engine problem
59 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 49 | 52 | 51 | 50
60 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract expired
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 72 | 75 | 68 | 68 | 127 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 42 | 43 | 45 | 45 |  | 5 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 10 | 50 | 150 | 150
64 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 42
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 90 | 0 | 90
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 17 | 192 | 200 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 124 | 154 | 140 | 184
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 48 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 12 | 14 | 20 | 20 |  | 5 | Engine problem
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1412 | 1682 | 1849 | 2244 | 390 | 18
74 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 145 | 145 | 145 | 145 |  | 57 | GT-1 Under maint.
75 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
76 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 16 | 95 | 95 | 95
77 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
78 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 16 | 160 | 100 | 200
79 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 315 | 537 | 478.6 | 577 | 0 | 57
80 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 54 | 54 | 53 | 53
81 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 69 | 69 | 69 | 69
82 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 130 | 163 | 163
83 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 259 | 263 | 260 | 267
84 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
85 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 46 | 47 | 44 | 44
86 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
87 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 64 | 64 | 66 |  |  | FGMO
88 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 71 | 75 | 75 | 75
89 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 40 | 40 | 42 | 42 |  | 8 | Engine problem
90 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 111 | 112 | 120 | 125
91 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 17 | 17 |  | 3 | Engine problem
92 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 40 | 45 | 45 | 45
93 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 24 | 24
94 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 285 | 315 | 320 |  |  | FGMO
95 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285 MW | 285 | 285 | 234 | 232 | 300 | 300
96 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1879 | 1834 | 1531 | 1523 | 1663 | 1682 | 0 | 11
97 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 32 | 0 | 32
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 912 | 925 | 931 | 931
| Khulna 115 MW PP (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
98 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 115 | 115 | 115
99 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 27 | 0 | 35
100 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 150 | 150 |  | 80 | ST Under maint
101 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 68 | 0 | 70
102 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maint.
103 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 40 | 40 | 40
| Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
104 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 0 | 100
105 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 105 | 105 | 105
106 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 33 | 68 | 84 | 85 |  | 20 | Engine problem
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 986 | 1480 | 1425 | 1663 | 0 | 510
107 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 70 | 110
108 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
109 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 13 | 36 | 33 | 33
110 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 173 | 173 | 175 | 175
111 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 82 | 95 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 268 | 336 | 373 | 443 | 0 | 0
112 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 55 | 60 | 60 | 60
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
113 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
114 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 30
115 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 18 | 33 | 12 | 33 |  | 38 | Engine problem
116 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 8 | 42 | 42 | 42 |  | 8 | Engine problem
117 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 45 | 45 | 45
118 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 189 | 184 | 215 | 215 |  |  | FGMO
119 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 194 | 146 | 200 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 196 | 191 | 205 | 215 |  |  | FGMO
121 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 300 | 390 | 400 | 400
122 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 0 | 36
123 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
124 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 13 | 16 | 16 | 16
125 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
126 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 8 | 52 | 52 | 52
127 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 95 | 80 | 100
128 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
129 | Bagura 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 100 | 93 | 110 | 113
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 1111 | 1467 | 1720 | 1850 | 0 | 146
130 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 68 | 70 | 100 | 100
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
131 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 249 | 232 | 250 | 250
132 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
133 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 15 | 0 | 18
| Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 0 | 0 | 27 | 0 | 0 | 100
| Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 0 | 0 | 3 | 0 | 3 | 0
| Rangpur Area Total |  |  |  |  | 564 | 484 | 347 | 317 | 353 | 468 | 0 | 105
| Total |  |  |  |  | 18961 | 18438 | 9406.83 | 11663 | 12809 | 14643 | 890 | 1639
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8938.2226 | 11082 | 12170.9113 | 13913.5493
A. |  | 2019-07-30 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 11663 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 8421.22 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11663 | MW
3 | Day peak Generation : |  |  | 9406.83 | MW at | 11:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11082 | MW
4 | Evening peak Generation : |  |  | 11663 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 237.7747 | MKWHr | By Solar | 0.14977 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 153.8521 | MKWHr |  | By Oil: | 45.874 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 7.5969 | MKWHr |  | By Hydro: | 4.9387 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 890 | MW | Dhaka | 3994 | 3994 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1639 | MW | Chittagong | 1128 | 1128 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2529 | MW | Khulna | 1387 | 1387 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1404.89 | MMCFD |  |  | Rajshahi | 1228 | 1228 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 151583298.83 | ii) Oil : | Taka | 398851426 | Comilla | 938 | 938 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 34892650.64 | Total | Taka | 585327375.47 | Mymensingh | 957 | 957 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 1.2995 | MKWHr. | Sylhet | 464 | 464 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -290 | MW (E to W) at | 21:00 | hrs | Barisal | 305 | 305 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -330 | MW at | 20:00 | hrs | Rangpur | 681 | 681 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 31.6° C |  |  | Total | 11082 | 11082 |  | 0
B. |  | 2019-07-31 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 32.3° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12100 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14643 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9900 | MW
4 | Reserve(Generation end) |  |  |  | 2543 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 246.6838 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8557.5 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.0771 | MKWHr. | ii) HVDC Flow at Peak Time |  | 925 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.2861 | MKWHr. | iii) Maximum HVDC Flow : |  | 934 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 106 |  | (b) Today: | 105.85 |  | (c) Rule Curve: |  | 88.83
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-07-30
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Lid. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence) | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 30 | 219 | 220 | 0 | 0 | 101 | 74 | 340 | 303 |  | 0 | 370 | 265 | 30 | 25 | 0 | 9 | 0 | 0 | 0 | 0 | 7 | 62 | 0 | 72 | 0 | 11 | 53 | 17 | 17 | 22 | 25 | 31 | 25 | 33 | 41 | 0 | 123 | 90 | 95 | 120 | 8 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 10 | 50 | 22 | 40 | 100 | 0 | 0 | 310 | 310 | 186 | 68 | 90 | 30 | 51 | 0 | 43 | 0 | 0 | 25 | 19 | 11 | 33 | 20 | 160 | 147 | 95 | 22 | 0 | 54 | 69 | 50 | 50 | 100 | 265 | 63 | 73 | 43 | 109 | 17 | 44 | 10 | 295 | 24 | 11 | 0 | 0 | 0 | 0 | 150 | 0 | 69 | 0 | 100 | 199 | 10 | 233 | 115 | 102 | 17 | 0 | 233 | 0 | 0 |  | 934 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 23 | 20 | 40 | 173 | 34 | 32 | 0 | 0 | 55 | 0 | 21 | 93 | 6 | 42 | 45 | 52 | 36 | 22 | 16 | 8 | 71 | 0 | 250 | 0 | 0 | 188 | 0 | 186 | 0 | 97 | 50 | 189 | 0 | 300 | 105 | 0 | 80 | 85 | 0 | 0 | 0 |  | 7529 | 3269 | 10798 | 4447 | 934 | 2184 | 2239 | 321 | 213 | 300 | 160 | 0 | 0 | 106.05
2:00 | 30 | 219 | 220 | 0 | 0 | 101 | 74 | 340 | 303 |  | 0 | 370 | 272 | 0 | 15 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 72 | 0 | 10 | 53 | 17 | 0 | 22 | 25 | 31 | 25 | 33 | 41 | 0 | 124 | 90 | 95 | 120 | 0 | 206 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 5 | 42 | 22 | 40 | 100 | 0 | 0 | 315 | 315 | 217 | 68 | 90 | 30 | 52 | 0 | 43 | 0 | 0 | 25 | 19 | 11 | 33 | 20 | 158 | 148 | 95 | 22 | 0 | 54 | 69 | 50 | 50 | 130 | 262 | 63 | 73 | 43 | 109 | 17 | 44 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 60 | 160 | 10 | 236 | 115 | 102 | 17 | 0 | 180 | 0 | 0 |  | 929 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 23 | 16 | 40 | 173 | 33 | 16 | 0 | 0 | 55 | 0 | 0 | 93 | 6 | 42 | 45 | 25 | 36 | 22 | 16 | 8 | 71 | 0 | 250 | 0 | 0 | 185 | 0 | 189 | 0 | 95 | 10 | 192 | 0 | 300 | 70 | 0 | 90 | 84 | 0 | 0 | 0 |  | 7248 | 3130 | 10378 | 4494 | 929 | 2217 | 1800 | 321 | 214 | 245 | 158 | 0 | 0 | 106.04
3:00 | 30 | 219 | 220 | 0 | 0 | 101 | 74 | 340 | 303 |  | 0 | 370 | 272 | 0 | 15 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 72 | 0 | 13 | 53 | 17 | 0 | 19 | 25 | 31 | 25 | 33 | 25 | 0 | 124 | 90 | 95 | 120 | 0 | 205 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 5 | 25 | 22 | 40 | 100 | 0 | 0 | 310 | 305 | 219 | 68 | 90 | 30 | 51 | 0 | 43 | 0 | 0 | 25 | 19 | 11 | 33 | 20 | 156 | 148 | 95 | 22 | 0 | 54 | 69 | 50 | 50 | 130 | 263 | 57 | 73 | 43 | 109 | 17 | 44 | 10 | 285 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 60 | 130 | 10 | 233 | 115 | 102 | 17 | 0 | 142 | 0 | 0 |  | 920 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 23 | 12 | 40 | 173 | 30 | 0 | 0 | 0 | 60 | 0 | 0 | 93 | 6 | 42 | 0 | 17 | 36 | 22 | 16 | 8 | 71 | 0 | 250 | 0 | 0 | 183 | 0 | 187 | 0 | 96 | 10 | 190 | 0 | 300 | 70 | 0 | 108 | 86 | 0 | 0 | 0 |  | 7107 | 3065 | 10172 | 4468 | 920 | 2199 | 1698 | 321 | 214 | 196 | 156 | 0 | 0 | 106.03
4:00 | 30 | 219 | 220 | 0 | 0 | 101 | 74 | 340 | 303 |  | 0 | 340 | 265 | 0 | 15 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 72 | 0 | 13 | 53 | 17 | 0 | 19 | 25 | 31 | 25 | 33 | 25 | 0 | 126 | 90 | 95 | 120 | 0 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 5 | 25 | 22 | 40 | 100 | 0 | 0 | 310 | 305 | 218 | 68 | 90 | 30 | 49 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 150 | 148 | 95 | 22 | 0 | 54 | 69 | 50 | 50 | 100 | 263 | 64 | 73 | 43 | 110 | 17 | 44 | 10 | 275 | 24 | 11 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 60 | 105 | 10 | 232 | 115 | 102 | 17 | 0 | 106 | 0 | 0 |  | 920 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 12 | 40 | 173 | 31 | 0 | 0 | 0 | 60 | 0 | 0 | 93 | 6 | 8 | 0 | 25 | 17 | 22 | 16 | 8 | 72 | 0 | 250 | 0 | 0 | 181 | 0 | 185 | 0 | 97 | 10 | 187 | 0 | 300 | 70 | 0 | 109 | 87 | 0 | 0 | 0 |  | 6906 | 3013 | 9919 | 4466 | 920 | 2129 | 1544 | 322 | 216 | 172 | 150 | 0 | 0 | 106.02
5:00 | 30 | 219 | 222 | 0 | 0 | 101 | 74 | 345 | 303 |  | 0 | 340 | 255 | 0 | 15 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 13 | 53 | 17 | 0 | 19 | 25 | 31 | 25 | 33 | 0 | 0 | 126 | 90 | 95 | 120 | 0 | 205 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 5 | 24 | 22 | 40 | 100 | 0 | 0 | 310 | 305 | 219 | 68 | 90 | 30 | 51 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 13 | 144 | 148 | 95 | 22 | 0 | 54 | 69 | 50 | 50 | 100 | 264 | 56 | 73 | 43 | 110 | 17 | 44 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 20 | 60 | 10 | 233 | 115 | 102 | 17 | 0 | 107 | 0 | 0 |  | 920 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 12 | 12 | 8 | 173 | 30 | 0 | 0 | 0 | 60 | 0 | 0 | 40 | 6 | 8 | 0 | 8 | 0 | 22 | 16 | 8 | 72 | 0 | 250 | 0 | 0 | 189 | 0 | 193 | 0 | 97 | 10 | 196 | 0 | 300 | 17 | 0 | 110 | 51 | 0 | 0 | 0 |  | 6707 | 2824 | 9531 | 4487 | 920 | 2155 | 1223 | 322 | 216 | 64 | 144 | 0 | 0 | 106.01
6:00 | 30 | 219 | 221 | 0 | 0 | 22 | 50 | 340 | 252 |  | 0 | 340 | 230 | 0 | 15 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 13 | 35 | 17 | 0 | 19 | 25 | 31 | 25 | 32 | 0 | 0 | 126 | 90 | 95 | 120 | 0 | 202 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 5 | 20 | 22 | 40 | 100 | 0 | 0 | 270 | 270 | 182 | 68 | 90 | 30 | 51 | 0 | 10 | 0 | 0 | 8 | 19 | 11 | 33 | 14 | 134 | 148 | 67 | 22 | 0.1 | 54 | 69 | 11 | 10 | 100 | 262 | 51 | 30 | 10 | 110 | 17 | 10 | 10 | 265 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0.49 | 20 | 52 | 10 | 233 | 78 | 102 | 17 | 0.26 | 94 | 0 | 0 |  | 920 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 12 | 12 | 8 | 173 | 27 | 0 | 0 | 0 | 60 | 0 | 0 | 24 | 6 | 8 | 0 | 8 | 0 | 22 | 16 | 8 | 71 | 0 | 251 | 0 | 0 | 178 | 0 | 182 | 0 | 54 | 0 | 187 | 0 | 270 | 17 | 0 | 110 | 34 | 0 | 0 | 0 |  | 5977.85 | 2674 | 8651.85 | 4328 | 920 | 1668 | 1015 | 322 | 216 | 48 | 134 | 0.85 | 0 | 106
7:00 | 32 | 219 | 220 | 0 | 0 | 22 | 50 | 340 | 252 |  | 0 | 340 | 260 | 0 | 15 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 13 | 17 | 17 | 0 | 19 | 25 | 31 | 25 | 33 | 0 | 0 | 126 | 90 | 95 | 120 | 0 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 5 | 12 | 22 | 33 | 100 | 0 | 0 | 255 | 305 | 186 | 68 | 90 | 30 | 52 | 0 | 10 | 0 | 0 | 8 | 19 | 11 | 33 | 15 | 122 | 148 | 16 | 22 | 0.2 | 54 | 69 | 11 | 10 | 100 | 265 | 63 | 10 | 10 | 110 | 17 | 12 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 2.78 | 20 | 17 | 10 | 234 | 70 | 102 | 17 | 1 | 52 | 0 | 0 |  | 920 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 6 | 8 | 8 | 172 | 21 | 0 | 0 | 0 | 60 | 0 | 0 | 24 | 6 | 8 | 0 | 8 | 0 | 22 | 16 | 8 | 72 | 0 | 249 | 0 | 18 | 167 | 0 | 153 | 0 | 52 | 0 | 192 | 0 | 270 | 17 | 0 | 111 | 34 | 0 | 0 | 1.2 |  | 5874.98 | 2639.2 | 8514.18 | 4329 | 920 | 1661 | 884 | 321 | 216 | 56 | 122 | 5.18 | 0 | 105.99
8:00 | 32 | 220 | 220 | 0 | 0 | 22 | 50 | 339 | 252 |  | 0 | 340 | 272 | 0 | 15 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 13 | 17 | 17 | 0 | 0 | 25 | 21 | 25 | 32 | 3 | 0 | 126 | 90 | 95 | 120 | 0 | 205 | 0 | 136 | 0 |  | 0 | 0 | 0 | 10 | 5 | 12 | 0 | 10 | 100 | 0 | 0 | 260 | 310 | 189 | 68 | 90 | 30 | 51 | 0 | 10 | 0 | 0 | 8 | 19 | 11 | 33 | 0 | 122 | 145 | 16 | 22 | 0.5 | 54 | 69 | 11 | 10 | 100 | 263 | 63 | 10 | 10 | 122 | 17 | 12 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 1 | 20 | 17 | 10 | 249 | 70 | 102 | 17 | 2.72 | 52 | 0 | 0 |  | 919 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 173 | 20 | 0 | 0 | 0 | 60 | 0 | 0 | 24 | 6 | 8 | 0 | 8 | 0 | 22 | 16 | 8 | 71 | 0 | 250 | 0 | 18 | 163 | 0 | 164 | 0 | 52 | 0 | 189 | 0 | 270 | 17 | 0 | 55 | 34 | 0 | 0 | 1 |  | 5849.22 | 2572 | 8421.22 | 4317 | 919 | 1636 | 843 | 321 | 216 | 42 | 122 | 5.22 | 0 | 106.26
9:00 | 32 | 219 | 220 | 0 | 0 | 22 | 50 | 366 | 254 |  | 0 | 340 | 286 | 0 | 15 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 10 | 0 | 8 | 0 | 13 | 17 | 17 | 0 | 0 | 25 | 21 | 25 | 32 | 30 | 0 | 126 | 90 | 95 | 120 | 0 | 217 | 0 | 143 | 0 |  | 0 | 0 | 0 | 10 | 5 | 12 | 0 | 3 | 100 | 0 | 0 | 285 | 340 | 204 | 68 | 90 | 30 | 50 | 0 | 10 | 0 | 0 | 8 | 19 | 11 | 33 | 12 | 124 | 145 | 16 | 22 | 1.1 | 54 | 69 | 11 | 10 | 130 | 275 | 61 | 10 | 10 | 124 | 17 | 12 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 5 | 20 | 17 | 10 | 269 | 70 | 102 | 17 | 3.62 | 52 | 0 | 0 |  | 916 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 173 | 17 | 0 | 0 | 0 | 60 | 0 | 0 | 24 | 6 | 8 | 0 | 8 | 0 | 22 | 16 | 8 | 70 | 0 | 250 | 0 | 17 | 190 | 0 | 178 | 0 | 52 | 0 | 208 | 0 | 300 | 17 | 0 | 56 | 35 | 0 | 0 | 1 |  | 6119.72 | 2656 | 8775.72 | 4531 | 916 | 1717 | 890 | 320 | 216 | 51 | 124 | 10.72 | 0 | 106.25
10:00 | 32 | 219 | 220 | 0 | 0 | 85 | 50 | 370 | 283 |  | 0 | 340 | 283 | 0 | 15 | 0 | 3 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 31 | 0 | 13 | 17 | 17 | 17 | 0 | 25 | 21 | 25 | 32 | 42 | 0 | 124 | 90 | 95 | 120 | 0 | 227 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 5 | 12 | 0 | 2 | 100 | 0 | 0 | 365 | 315 | 194 | 68 | 90 | 27 | 51 | 0 | 20 | 0 | 0 | 8 | 19 | 11 | 33 | 12 | 118 | 145 | 16 | 22 | 0.4 | 54 | 69 | 44 | 36 | 163 | 272 | 61 | 50 | 40 | 112 | 17 | 42 | 10 | 320 | 16 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 40 | 2 | 20 | 17 | 10 | 247 | 94 | 102 | 17 | 2.12 | 52 | 0 | 0 |  | 910 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 173 | 12 | 0 | 0 | 0 | 55 | 0 | 0 | 21 | 6 | 8 | 0 | 8 | 0 | 22 | 13 | 8 | 71 | 0 | 250 | 0 | 0 | 203 | 0 | 204 | 0 | 64 | 0 | 209 | 0 | 300 | 17 | 0 | 56 | 34 | 12 | 0 | 5.9 |  | 6528.52 | 2685.9 | 9214.42 | 4563 | 910 | 2015 | 1026 | 321 | 214 | 37 | 118 | 10.42 | 0 | 106.25
11:00 | 32 | 219 | 220 | 0 | 0 | 90 | 73 | 340 | 283 |  | 0 | 340 | 230 | 0 | 15 | 0 | 3 | 0 | 0 | 0 | 0 | 24 | 16 | 0 | 68 | 0 | 13 | 17 | 17 | 17 | 0 | 25 | 21 | 25 | 25 | 42 | 0 | 123 | 90 | 95 | 120 | 0 | 206 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 5 | 13 | 0 | 2 | 100 | 0 | 0 | 310 | 310 | 189 | 72 | 90 | 27 | 49 | 0 | 42 | 0 | 0 | 8 | 19 | 0 | 33 | 12 | 124 | 145 | 16 | 22 | 1 | 54 | 69 | 50 | 46 | 130 | 259 | 63 | 71 | 40 | 111 | 17 | 40 | 10 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 103 | 11 | 60 | 17 | 10 | 234 | 115 | 102 | 17 | 1.83 | 182 | 11 | 0 |  | 912 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 173 | 13 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 18 | 8 | 0 | 8 | 0 | 22 | 13 | 8 | 68 | 0 | 249 | 0 | 0 | 189 | 0 | 194 | 0 | 82 | 0 | 196 | 0 | 300 | 17 | 0 | 100 | 33 | 27 | 0 | 3 |  | 6694.83 | 2712 | 9406.83 | 4367 | 912 | 2078 | 1363 | 317 | 213 | 16 | 124 | 16.83 | 0 | 106.25
12:00 | 32 | 219 | 220 | 0 | 0 | 97 | 73 | 340 | 283 |  | 0 | 340 | 230 | 0 | 15 | 0 | 3 | 0 | 0 | 0 | 0 | 24 | 16 | 0 | 67 | 0 | 13 | 17 | 17 | 17 | 19 | 25 | 0 | 0 | 32 | 42 | 0 | 115 | 90 | 95 | 120 | 0 | 205 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 5 | 25 | 0 | 4 | 100 | 0 | 0 | 310 | 310 | 182 | 68 | 90 | 27 | 49 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 12 | 134 | 145 | 16 | 22 | 2.4 | 54 | 69 | 53 | 46 | 100 | 261 | 63 | 73 | 40 | 110 | 16 | 41 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 100 | 13 | 100 | 17 | 10 | 232 | 115 | 102 | 17 | 4.02 | 194 | 0 | 0 |  | 911 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 173 | 11 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 18 | 8 | 0 | 8 | 0 | 22 | 15 | 8 | 68 | 0 | 250 | 0 | 0 | 182 | 0 | 187 | 0 | 88 | 0 | 190 | 0 | 270 | 17 | 0 | 112 | 34 | 27 | 0 | 5.9 |  | 6712.42 | 2683.9 | 9396.32 | 4336 | 911 | 2026 | 1425 | 318 | 205 | 16 | 134 | 25.32 | 0 | 106.25
13:00 | 32 | 219 | 220 | 0 | 0 | 100 | 72 | 340 | 283 |  | 0 | 340 | 230 | 0 | 15 | 0 | 58 | 0 | 0 | 0 | 0 | 24 | 16 | 5 | 72 | 0 | 13 | 17 | 17 | 17 | 19 | 25 | 0 | 20 | 32 | 42 | 0 | 122 | 90 | 95 | 120 | 0 | 205 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 5 | 39 | 0 | 11 | 100 | 0 | 0 | 310 | 310 | 182 | 72 | 87 | 27 | 48 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 12 | 136 | 143 | 16 | 22 | 2.4 | 54 | 69 | 53 | 50 | 100 | 263 | 64 | 70 | 40 | 110 | 17 | 42 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 100 | 9 | 100 | 17 | 10 | 232 | 111 | 102 | 17 | 0.74 | 194 | 0 | 0 |  | 914 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 172 | 15 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 42 | 0 | 8 | 0 | 21 | 15 | 8 | 68 | 0 | 250 | 0 | 0 | 190 | 0 | 192 | 0 | 91 | 0 | 198 | 0 | 240 | 17 | 0 | 112 | 36 | 21 | 0 | 7 |  | 6822.14 | 2708 | 9530.14 | 4430 | 914 | 2016 | 1469 | 318 | 212 | 16 | 136 | 19.14 | 0 | 106.24
14:00 | 32 | 219 | 221 | 0 | 0 | 101 | 72 | 300 | 252 |  | 0 | 300 | 230 | 0 | 0 | 0 | 77 | 0 | 0 | 0 | 0 | 24 | 16 | 61 | 72 | 0 | 13 | 17 | 35 | 17 | 0 | 25 | 21 | 25 | 32 | 42 | 0 | 120 | 90 | 95 | 120 | 0 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 5 | 48 | 10 | 6 | 100 | 0 | 0 | 260 | 260 | 182 | 68 | 91 | 37 | 51 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 12 | 132 | 143 | 16 | 22 | 0.5 | 53 | 69 | 11 | 50 | 100 | 267 | 64 | 40 | 40 | 120 | 17 | 12 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 100 | 9.5 | 100 | 17 | 10 | 232 | 115 | 102 | 17 | 1.6 | 196 | 0 | 0 |  | 915 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 173 | 15 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 42 | 0 | 8 | 0 | 22 | 15 | 5 | 68 | 0 | 250 | 0 | 0 | 185 | 0 | 164 | 0 | 91 | 0 | 157 | 0 | 220 | 17 | 0 | 112 | 33 | 0 | 0 | 5.4 |  | 6616.6 | 2593.4 | 9210 | 4274 | 915 | 1809 | 1519 | 318 | 210 | 16 | 132 | 17 | 0 | 105.92
15:00 | 32 | 219 | 221 | 0 | 0 | 101 | 72 | 300 | 253 |  | 0 | 300 | 230 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 24 | 16 | 100 | 72 | 0 | 13 | 35 | 35 | 17 | 0 | 25 | 21 | 25 | 33 | 42 | 0 | 120 | 90 | 95 | 120 | 0 | 217 | 0 | 133 | 0 |  | 0 | 0 | 0 | 10 | 5 | 50 | 22 | 4 | 100 | 0 | 0 | 285 | 285 | 203 | 68 | 90 | 37 | 53 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 12 | 120 | 145 | 16 | 22 | 2 | 54 | 69 | 11 | 50 | 100 | 267 | 67 | 40 | 42 | 123 | 17 | 12 | 10 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 100 | 9.1 | 100 | 17 | 10 | 249 | 115 | 102 | 17 | 1.9 | 196 | 0 | 0 |  | 915 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 7 | 8 | 172 | 7 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 42 | 0 | 8 | 0 | 21 | 15 | 5 | 68 | 0 | 249 | 0 | 0 | 183 | 0 | 171 | 0 | 54 | 0 | 174 | 0 | 250 | 17 | 0 | 113 | 32 | 8 | 0 | 4.2 |  | 7063 | 2611.2 | 9674.2 | 4670 | 915 | 1816 | 1586 | 317 | 210 | 23 | 120 | 17.2 | 0 | 106.24
16:00 | 32 | 219 | 220 | 0 | 0 | 100 | 71 | 300 | 252 |  | 0 | 300 | 230 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 24 | 16 | 100 | 72 | 0 | 13 | 35 | 35 | 17 | 19 | 25 | 21 | 25 | 33 | 42 | 0 | 118 | 90 | 95 | 120 | 0 | 205 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 9 | 50 | 22 | 5 | 100 | 0 | 0 | 260 | 260 | 184 | 68 | 87 | 37 | 52 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 8 | 108 | 144 | 16 | 22 | 0.4 | 54 | 69 | 11 | 50 | 130 | 263 | 65 | 40 | 42 | 98 | 17 | 12 | 10 | 315 | 16 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 100 | 3.6 | 100 | 17 | 10 | 232 | 115 | 102 | 17 | 2.1 | 196 | 0 | 0 |  | 915 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 40 | 8 | 172 | 9 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 42 | 0 | 8 | 0 | 21 | 15 | 5 | 68 | 0 | 249 | 0 | 0 | 203 | 0 | 122 | 0 | 54 | 0 | 171 | 0 | 320 | 17 | 0 | 113 | 33 | 27 | 0 | 3.2 |  | 6959.1 | 2703.2 | 9662.3 | 4519 | 915 | 1920 | 1610 | 317 | 208 | 56 | 108 | 9.3 | 0 | 106.23
17:00 | 32 | 160 | 120 | 0 | 0 | 52 | 50 | 300 | 283 |  | 0 | 330 | 230 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 24 | 16 | 100 | 40 | 0 | 13 | 35 | 35 | 17 | 19 | 25 | 21 | 25 | 33 | 42 | 0 | 118 | 90 | 95 | 120 | 0 | 214 | 0 | 90 | 0 |  | 0 | 0 | 0 | 10 | 10 | 50 | 22 | 8 | 100 | 0 | 0 | 270 | 265 | 197 | 68 | 90 | 37 | 51 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 8 | 120 | 145 | 16 | 22 | 0.2 | 54 | 69 | 11 | 10 | 163 | 264 | 62 | 40 | 10 | 98 | 17 | 12 | 10 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 100 | 0.97 | 100 | 17 | 10 | 239 | 115 | 102 | 17 | 0.7 | 207 | 0 | 0 |  | 925 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 3 | 45 | 8 | 173 | 16 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 42 | 0 | 8 | 0 | 21 | 15 | 5 | 69 | 0 | 249 | 0 | 0 | 202 | 0 | 143 | 0 | 23 | 0 | 169 | 0 | 280 | 17 | 0 | 55 | 33 | 13 | 0 | 1.5 |  | 6743.87 | 2603.5 | 9347.37 | 4385 | 925 | 1806 | 1518 | 318 | 208 | 64 | 120 | 3.37 | 0 | 105.91
18:00 | 32 | 160 | 120 | 0 | 0 | 22 | 50 | 270 | 252 |  | 0 | 300 | 230 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 0 | 24 | 16 | 100 | 40 | 0 | 13 | 35 | 35 | 17 | 19 | 25 | 25 | 25 | 33 | 42 | 0 | 120 | 90 | 95 | 120 | 25 | 204 | 0 | 90 | 0 |  | 0 | 0 | 0 | 10 | 9 | 48 | 22 | 9 | 80 | 0 | 0 | 260 | 260 | 189 | 68 | 91 | 37 | 52 | 0 | 10 | 0 | 0 | 8 | 19 | 0 | 33 | 8 | 136 | 145 | 16 | 22 | 0.1 | 54 | 69 | 11 | 10 | 100 | 262 | 63 | 10 | 10 | 75 | 17 | 12 | 0 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 100 | 0.17 | 100 | 17 | 10 | 233 | 115 | 102 | 17 | 0.1 | 196 | 0 | 0 |  | 925 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 53 | 8 | 173 | 22 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 42 | 0 | 8 | 0 | 22 | 15 | 5 | 69 | 0 | 250 | 0 | 0 | 184 | 0 | 145 | 0 | 23 | 0 | 158 | 0 | 250 | 17 | 0 | 55 | 33 | 0 | 0 | 0.3 |  | 6369.37 | 2563.3 | 8932.67 | 4201 | 925 | 1538 | 1516 | 319 | 210 | 87 | 136 | 0.67 | 0 | 106.22
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 32 | 159 | 200 | 0 | 0 | 22 | 50 | 270 | 252 |  | 0 | 300 | 230 | 7 | 10 | 12 | 308 | 0 | 0 | 0 | 5 | 40 | 60 | 100 | 72 | 0 | 13 | 53 | 35 | 17 | 19 | 25 | 20 | 25 | 33 | 42 | 0 | 120 | 90 | 95 | 120 | 25 | 210 | 0 | 135 | 0 |  | 0 | 0 | 78 | 10 | 32 | 50 | 22 | 21 | 80 | 0 | 0 | 335 | 295 | 203 | 68 | 90 | 37 | 52 | 0 | 10 | 0 | 0 | 8 | 19 | 0 | 33 | 14 | 154 | 145 | 42 | 22 | 0 | 54 | 69 | 52 | 23 | 100 | 267 | 62 | 75 | 10 | 123 | 17 | 43 | 10 | 305 | 0 | 11 | 0 | 11 | 0 | 0 | 16 | 0 | 100 | 0 | 100 | 34 | 22 | 260 | 115 | 102 | 17 | 0 | 199 | 0 | 0 |  | 925 | 10 | 0 | 0 | 60 | 0 | 0 | 0 | 30 | 85 | 40 | 173 | 25 | 48 | 0 | 0 | 55 | 50 | 0 | 60 | 33 | 42 | 28 | 16 | 21 | 22 | 15 | 11 | 68 | 0 | 249 | 0 | 17 | 190 | 0 | 145 | 0 | 97 | 8 | 175 | 0 | 300 | 87 | 0 | 70 | 60 | 0 | 0 | 0 |  | 7223 | 3215 | 10438 | 4558 | 925 | 1852 | 1983 | 317 | 210 | 439 | 154 | 0 | 0 | 106.22
19:30 | 32 | 159 | 200 | 0 | 0 | 22 | 50 | 340 | 253 |  | 0 | 300 | 230 | 56 | 30 | 15 | 308 | 0 | 0 | 0 | 10 | 60 | 100 | 100 | 72 | 0 | 20 | 30 | 55 | 35 | 19 | 25 | 29 | 25 | 33 | 42 | 0 | 120 | 90 | 95 | 120 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 85 | 10 | 70 | 50 | 22 | 27 | 80 | 0 | 0 | 310 | 290 | 182 | 68 | 91 | 37 | 52 | 0 | 35 | 0 | 0 | 10 | 19 | 0 | 33 | 14 | 156 | 145 | 95 | 22 | 0 | 54 | 69 | 53 | 47 | 100 | 262 | 63 | 75 | 40 | 109 | 17 | 44 | 10 | 310 | 16 | 11 | 0 | 30 | 0 | 0 | 31 | 0 | 120 | 0 | 100 | 125 | 50 | 232 | 115 | 102 | 17 | 0 | 213 | 0 | 0 |  | 924 | 32 | 0 | 0 | 115 | 0 | 0 | 0 | 29 | 80 | 40 | 173 | 28 | 64 | 0 | 0 | 55 | 43 | 0 | 95 | 33 | 42 | 46 | 42 | 38 | 22 | 15 | 11 | 68 | 0 | 249 | 0 | 15 | 195 | 0 | 144 | 0 | 98 | 78 | 201 | 0 | 330 | 105 | 0 | 113 | 68 | 0 | 0 | 0 |  | 7752 | 3591 | 11343 | 4576 | 924 | 1979 | 2618 | 317 | 210 | 563 | 156 | 0 | 0 | 0
20:00 | 32 | 220 | 201 | 0 | 0 | 21 | 50 | 342 | 254 |  | 0 | 300 | 230 | 56 | 45 | 15 | 233 | 0 | 0 | 0 | 40 | 75 | 127 | 100 | 72 | 0 | 30 | 35 | 55 | 35 | 19 | 25 | 32 | 25 | 33 | 42 | 0 | 120 | 90 | 95 | 120 | 25 | 203 | 0 | 130 | 0 |  | 0 | 0 | 85 | 10 | 76 | 50 | 22 | 27 | 80 | 0 | 0 | 310 | 290 | 181 | 68 | 90 | 37 | 52 | 0 | 34 | 0 | 0 | 38 | 19 | 11 | 33 | 14 | 154 | 148 | 95 | 22 | 0 | 54 | 69 | 53 | 47 | 100 | 266 | 65 | 75 | 40 | 110 | 17 | 44 | 10 | 300 | 0 | 11 | 0 | 36 | 0 | 0 | 95 | 0 | 144 | 0 | 100 | 152 | 50 | 233 | 115 | 102 | 17 | 0 | 213 | 0 | 0 |  | 925 | 32 | 0 | 0 | 115 | 0 | 0 | 0 | 27 | 80 | 40 | 173 | 31 | 48 | 0 | 0 | 60 | 43 | 0 | 95 | 33 | 42 | 47 | 43 | 37 | 22 | 15 | 11 | 68 | 0 | 249 | 0 | 15 | 189 | 0 | 145 | 0 | 96 | 87 | 195 | 0 | 330 | 105 | 0 | 113 | 77 | 0 | 0 | 0 |  | 7991 | 3588 | 11579 | 4565 | 925 | 1969 | 2851 | 317 | 210 | 588 | 154 | 0 | 0 | 106.21
21:00 | 32 | 220 | 200 | 0 | 0 | 22 | 50 | 340 | 252 |  | 0 | 300 | 230 | 24 | 32 | 15 | 313 | 0 | 0 | 0 | 0 | 75 | 130 | 70 | 72 | 0 | 48 | 53 | 55 | 17 | 19 | 25 | 32 | 25 | 33 | 42 | 0 | 121 | 90 | 95 | 120 | 25 | 204 | 0 | 131 | 0 |  | 0 | 0 | 85 | 10 | 52 | 50 | 22 | 34 | 80 | 0 | 0 | 310 | 290 | 184 | 75 | 90 | 37 | 52 | 0 | 43 | 0 | 0 | 48 | 19 | 11 | 33 | 14 | 154 | 145 | 95 | 22 | 0 | 54 | 69 | 53 | 47 | 130 | 263 | 64 | 75 | 40 | 112 | 17 | 45 | 10 | 285 | 16 | 11 | 0 | 14 | 0 | 0 | 160 | 0 | 112 | 0 | 100 | 192 | 50 | 232 | 115 | 100 | 17 | 0 | 213 | 0 | 0 |  | 925 | 32 | 0 | 0 | 115 | 0 | 0 | 0 | 27 | 68 | 40 | 173 | 36 | 32 | 0 | 0 | 60 | 50 | 0 | 95 | 33 | 42 | 45 | 52 | 37 | 22 | 16 | 11 | 70 | 0 | 232 | 0 | 15 | 184 | 0 | 146 | 0 | 95 | 100 | 191 | 0 | 390 | 105 | 0 | 93 | 68 | 0 | 0 | 0 |  | 8063 | 3600 | 11663 | 4649 | 925 | 2072 | 2766 | 302 | 211 | 584 | 154 | 0 | 0 | 106.21
22:00 | 32 | 220 | 220 | 0 | 0 | 22 | 50 | 341 | 252 |  | 0 | 300 | 230 | 24 | 30 | 0 | 294 | 0 | 0 | 0 | 0 | 75 | 130 | 0 | 72 | 0 | 47 | 53 | 55 | 17 | 19 | 25 | 32 | 25 | 33 | 42 | 0 | 122 | 90 | 95 | 120 | 25 | 203 | 0 | 130 | 0 |  | 0 | 0 | 71 | 10 | 44 | 50 | 22 | 38 | 80 | 0 | 0 | 310 | 290 | 182 | 75 | 90 | 33 | 51 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 14 | 156 | 147 | 95 | 22 | 0 | 54 | 69 | 53 | 47 | 130 | 262 | 64 | 75 | 43 | 109 | 17 | 45 | 10 | 305 | 16 | 11 | 0 | 15 | 0 | 0 | 140 | 0 | 100 | 0 | 100 | 199 | 50 | 232 | 115 | 100 | 17 | 0 | 214 | 0 | 0 |  | 925 | 16 | 0 | 0 | 115 | 0 | 0 | 0 | 27 | 65 | 40 | 173 | 33 | 32 | 0 | 0 | 60 | 50 | 0 | 95 | 33 | 42 | 45 | 52 | 37 | 22 | 16 | 11 | 69 | 0 | 199 | 0 | 15 | 186 | 0 | 146 | 0 | 96 | 100 | 192 | 0 | 360 | 105 | 0 | 93 | 79 | 0 | 0 | 0 |  | 7955 | 3529 | 11484 | 4644 | 925 | 2066 | 2662 | 268 | 212 | 551 | 156 | 0 | 0 | 106.07
23:00 | 32 | 220 | 201 | 0 | 0 | 66 | 50 | 348 | 252 |  | 0 | 300 | 230 | 0 | 30 | 0 | 295 | 0 | 0 | 0 | 0 | 75 | 126 | 0 | 72 | 0 | 0 | 53 | 55 | 17 | 19 | 25 | 32 | 25 | 33 | 42 | 0 | 124 | 90 | 95 | 120 | 25 | 205 | 0 | 130 | 0 |  | 0 | 0 | 36 | 10 | 32 | 50 | 22 | 38 | 80 | 0 | 0 | 310 | 290 | 191 | 75 | 90 | 33 | 52 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 14 | 150 | 146 | 95 | 22 | 0 | 53 | 69 | 53 | 50 | 130 | 264 | 63 | 75 | 45 | 115 | 17 | 45 | 10 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 140 | 0 | 100 | 0 | 100 | 200 | 55 | 233 | 115 | 98 | 17 | 0 | 214 | 0 | 0 |  | 928 | 16 | 0 | 0 | 115 | 0 | 0 | 0 | 27 | 65 | 40 | 173 | 36 | 32 | 0 | 0 | 60 | 50 | 0 | 95 | 12 | 42 | 45 | 52 | 37 | 22 | 16 | 11 | 70 | 0 | 200 | 0 | 15 | 200 | 0 | 145 | 0 | 96 | 100 | 198 | 0 | 360 | 105 | 0 | 92 | 68 | 0 | 0 | 0 |  | 7869 | 3523 | 11392 | 4669 | 928 | 2114 | 2535 | 270 | 214 | 512 | 150 | 0 | 0 | 106.06
24:00 | 32 | 219 | 200 | 0 | 0 | 99 | 50 | 340 | 252 |  | 0 | 300 | 230 | 0 | 15 | 0 | 295 | 0 | 0 | 0 | 0 | 7 | 100 | 0 | 72 | 0 | 13 | 53 | 55 | 17 | 19 | 25 | 31 | 25 | 33 | 42 | 0 | 124 | 90 | 95 | 120 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 17 | 10 | 32 | 50 | 22 | 40 | 80 | 0 | 0 | 310 | 290 | 183 | 75 | 91 | 33 | 51 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 14 | 140 | 148 | 95 | 22 | 0 | 54 | 69 | 53 | 50 | 130 | 265 | 64 | 75 | 45 | 115 | 17 | 45 | 10 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 140 | 0 | 77 | 0 | 100 | 200 | 100 | 232 | 115 | 98 | 17 | 0 | 214 | 0 | 0 |  | 928 | 16 | 0 | 0 | 115 | 0 | 0 | 0 | 27 | 60 | 40 | 173 | 36 | 16 | 0 | 0 | 60 | 50 | 0 | 95 | 12 | 42 | 0 | 53 | 35 | 22 | 16 | 11 | 70 | 0 | 200 | 0 | 15 | 197 | 0 | 147 | 0 | 97 | 100 | 190 | 0 | 320 | 105 | 0 | 113 | 67 | 0 | 0 | 0 |  | 7785 | 3428 | 11213 | 4645 | 928 | 2109 | 2492 | 270 | 214 | 415 | 140 | 0 | 0 | 106.06
KWH | 732000 | 5340300 | 4954000 | 0 | 0 | 1572363 | 1494 | 8125440 | 6481000 |  | 0 | 8056250 | 5952902 | 153600 | 410136 | 60029 | 2082546 | 0 | 0 | 0 | 58560 | 587232 | 996000 | 830258 | 1252800 | 0 | 416592 | 883800 | 746881 | 374915 | 329364 | 600000 | 615240 | 564900 | 790000 | 816012 | 0 | 2762733 | 2176000 | 2300000 | 2900000 | 189549 | 4927805 | 0 | 2965534 | 0 |  | 0 | 0 | 351172 | 256080 | 423360 | 871680 | 373584 | 496800 | 2342982 | 0 | 0 | 7399700 | 7279000 | 4719000 | 1706181 | 2123420 | 735912 | 1226880 | 0 | 893698 | 0 | 0 | 494947 | 448740 | 226980 | 819500 | 351620 | 3286080 | 3423000 | 1325760 | 521352 | 11700 | 1289000 | 1649400 | 837600 | 987696 | 3144894 | 6035000 | 1486560 | 1322880 | 798120 | 2719610 | 432050 | 748700 | 242100 | 7427250 | 428568 | 264000 | 0 | 85309 | 0 | 0 | 1435200 | 0 | 1604160 | 72090 | 1802880 | 1945440 | 568727 | 5742000 | 2613600 | 2407848 | 422361 | 26280 | 3924218 | 26280 | 0 |  | 22077091 | 121600 | 0 | 0 | 887040 | 0 | 0 | 0 | 280320 | 584832 | 499125 | 4217788 | 546890 | 252384 | 0 | 0 | 1400000 | 258672 | 32956 | 1016744 | 131680 | 694853 | 330322 | 506400 | 322914 | 512400 | 372240 | 198090 | 1676072 | 0 | 5920800 | 0 | 153000 | 4773382 | 0 | 4149309 | 0 | 1832766 | 668160 | 4707936 | 0 | 7159273 | 1172640 | 0 | 2284512 | 1237824 | 149760 | 0 | 39700 |  | 166605184 | 71169475 | 237774659 | 107484612 | 22077091 | 46367475 | 41425494 | 7596872 | 4938733 | 4448532 | 3286080 | 149770 | 0
Fuel Cost | 819840 | 5767524 | 5300780 | 0 | 0 | 1525192.11 | 2181.24 | 5850316.8 | 4925560 |  | 0 | 6445000 | 5357611.8 | 1566720 | 4441772.88 | 615897.54 | 2582357.04 | 0 | 0 | 0 | 650016 | 5966277.12 | 9870360 | 8701103.84 | 11400480 | 0 | 3899301.12 | 8475642 | 7125244.74 | 3734153.4 | 247023 | 450000 | 0 | 0 | 0 | 7817394.96 | 0 | 718310.58 | 565760 | 3519000 | 4437000 | 1821565.89 | 5174195.25 | 0 | 3766228.18 | 0 |  | 0 | 0 | 3683794.28 | 2635063.2 | 4026153.6 | 8158924.8 | 343697.28 | 1381104 | 2460131.1 | 0 | 0 | 5475778 | 6114360 | 4341480 | 1672057.38 | 2824148.6 | 603447.84 | 1263686.4 | 0 | 1277988.14 | 0 | 0 | 4652501.8 | 457714.8 | 170235 | 1548855 | 263715 | 22673952 | 2806860 | 12607977.6 | 531779.04 | 191880 | 1753040 | 2243184 | 1139136 | 1234620 | 3899668.56 | 5552200 | 2214974.4 | 2328268.8 | 885913.2 | 4133807.2 | 686959.5 | 875979 | 568935 | 5273347.5 | 321426 | 200640 | 0 | 893185.23 | 0 | 0 | 13806624 | 0 | 16185974.4 | 831918.6 | 16802841.6 | 18248227.2 | 5328971.99 | 5397480 | 22921272 | 21453925.68 | 3991311.45 | 0 | 36181289.96 | 0 | 0 |  | 59608145.7 | 3556800 | 0 | 0 | 8551065.6 | 0 | 0 | 0 | 3251712 | 7661299.2 | 4936346.25 | 3374230.4 | 847679.5 | 2710604.16 | 0 | 0 | 2632000 | 2881606.08 | 403711 | 10065765.6 | 1365521.6 | 8136728.63 | 3980380.1 | 5043744 | 3180702.9 | 563640 | 614196 | 149954.13 | 10676578.64 | 0 | 24216072 | 0 | 4319190 | 4200576.16 | 0 | 3858857.37 | 0 | 2914097.94 | 11291904 | 4142983.68 | 0 | 5226269.29 | 11093174.4 | 0 | 20971820.16 | 11029011.84 | 1398758.4 | 0 | 0 |  | 421062215.62 | 248855126.73 | 669917342.35 | 106718778.77 | 59608145.7 | 44864520.06 | 345996104.84 | 34892650.64 | 1284070.58 | 52855321.16 | 22673952 | 1023798.6 | 0
Yesterday Day Peak | 32 | 219 | 220 | 0 | 0 | 90 | 73 | 340 | 283 |  | 0 | 340 | 230 | 0 | 15 | 0 | 3 | 0 | 0 | 0 | 0 | 24 | 16 | 0 | 68 | 0 | 13 | 17 | 17 | 17 | 0 | 25 | 21 | 25 | 25 | 42 | 0 | 123 | 90 | 95 | 120 | 0 | 206 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 5 | 13 | 0 | 2 | 100 | 0 | 0 | 310 | 310 | 189 | 72 | 90 | 27 | 49 | 0 | 42 | 0 | 0 | 8 | 19 | 0 | 33 | 12 | 124 | 145 | 16 | 22 | 1 | 54 | 69 | 50 | 46 | 130 | 259 | 63 | 71 | 40 | 111 | 17 | 40 | 10 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 103 | 11 | 60 | 17 | 10 | 234 | 115 | 102 | 17 | 1.83 | 182 | 11 | 0 |  | 912 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 173 | 13 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 18 | 8 | 0 | 8 | 0 | 22 | 13 | 8 | 68 | 0 | 249 | 0 | 0 | 189 | 0 | 194 | 0 | 82 | 0 | 196 | 0 | 300 | 17 | 0 | 100 | 33 | 27 | 0 | 3 |  | 9406.83 | DayPeak
Yesterday Evening Peak | 32 | 220 | 200 | 0 | 0 | 22 | 50 | 340 | 252 | 0 | 0 | 300 | 230 | 24 | 32 | 15 | 313 | 0 | 0 | 0 | 0 | 75 | 130 | 70 | 72 | 0 | 48 | 53 | 55 | 17 | 19 | 25 | 32 | 25 | 33 | 42 | 0 | 121 | 90 | 95 | 120 | 25 | 204 | 0 | 131 | 0 | 0 | 0 | 0 | 85 | 10 | 52 | 50 | 22 | 34 | 80 | 0 | 0 | 310 | 290 | 184 | 75 | 90 | 37 | 52 | 0 | 43 | 0 | 0 | 48 | 19 | 11 | 33 | 14 | 154 | 145 | 95 | 22 | 0 | 54 | 69 | 53 | 47 | 130 | 263 | 64 | 75 | 40 | 112 | 17 | 45 | 10 | 285 | 16 | 11 | 0 | 14 | 0 | 0 | 160 | 0 | 112 | 0 | 100 | 192 | 50 | 232 | 115 | 100 | 17 | 0 | 213 | 0 | 0 |  | 925 | 32 | 0 | 0 | 115 | 0 | 0 | 0 | 27 | 68 | 40 | 173 | 36 | 32 | 0 | 0 | 60 | 50 | 0 | 95 | 33 | 42 | 45 | 52 | 37 | 22 | 16 | 11 | 70 | 0 | 232 | 0 | 15 | 184 | 0 | 146 | 0 | 95 | 100 | 191 | 0 | 390 | 105 | 0 | 93 | 68 | 0 | 0 | 0 |  | 11663 | EvPeak
Forecast for Evening | 32 | 220 | 220 | 0 | 0 | 100 | 50 | 370 | 250 | 0 | 0 | 300 | 280 | 100 | 100 | 55 | 10 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 72 | 0 | 47 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 42 | 0 | 130 | 90 | 95 | 120 | 25 | 215 | 0 | 136 | 0 | 0 | 0 | 0 | 85 | 100 | 96 | 50 | 22 | 35 | 100 | 0 | 0 | 360 | 360 | 220 | 68 | 90 | 37 | 50 | 0 | 45 | 0 | 42 | 52 | 22 | 11 | 33 | 20 | 184 | 145 | 95 | 22 | 0 | 53 | 69 | 51 | 44 | 163 | 267 | 66 | 75 | 42 | 125 | 17 | 45 | 10 | 320 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 300 | 115 | 100 | 100 | 0 | 260 |  |  |  | 931 | 32 | 0 | 0 | 115 | 150 | 0 | 0 | 35 | 70 | 40 | 175 | 33 | 110 | 30 | 0 | 60 | 50 | 30 | 100 | 33 | 42 | 45 | 52 | 36 | 22 | 16 | 11 | 100 | 0 | 250 | 0 | 18 | 215 | 0 | 210 | 0 | 95 | 100 | 215 | 0 | 400 | 105 | 0 | 113 | 85 | 100 | 0
Forecast for Day | 32 | 220 | 220 | 0 | 0 | 100 | 50 | 370 | 250 | 0 | 0 | 300 | 280 | 100 | 100 | 55 | 10 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 47 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 42 | 0 | 130 | 90 | 95 | 120 | 25 | 215 | 0 | 136 | 0 | 0 | 0 | 0 | 0 | 100 | 90 | 50 | 22 | 15 | 100 | 0 | 0 | 360 | 340 | 220 | 68 | 0 | 37 | 51 | 0 | 45 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 140 | 145 | 95 | 22 | 1.6 | 53 | 69 | 51 | 44 | 163 | 260 | 64 | 75 | 42 | 120 | 17 | 45 | 10 | 315 | 24 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 149 | 20 | 100 | 200 | 150 | 300 | 115 | 100 | 50 | 4.4 | 230 |  |  |  | 931 | 0 | 0 | 0 | 115 | 150 | 0 | 0 | 0 | 0 | 40 | 175 | 33 | 70 | 0 | 0 | 60 | 50 | 0 | 80 | 12 | 42 | 45 | 52 | 0 | 22 | 16 | 11 | 100 | 0 | 250 | 0 | 0 | 215 | 0 | 200 | 0 | 95 | 0 | 205 | 0 | 400 | 105 | 0 | 110 | 84 | 0 | 0 | 3
Generation at 08:00(Today) | 32 | 220 | 200 | 0 | 0 | 99 | 50 | 354 | 253 | 0 | 0 | 300 | 230 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 13 | 17 | 0 | 0 | 19 | 25 | 32 | 25 | 33 | 3 | 0 | 125 | 90 | 95 | 120 | 0 | 213 | 0 | 132 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 6 | 22 | 8 | 80 | 0 | 0 | 325 | 305 | 196 | 68 | 30 | 33 | 52 | 0 | 10 | 0 | 0 | 0 | 19 | 8 | 33 | 10 | 112 | 145 | 8 | 22 | 0.6 | 54 | 69 | 11 | 50 | 100 | 264 | 63 | 40 | 45 | 92 | 17 | 45 | 10 | 320 | 12 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 10 | 17 | 10 | 242 | 115 | 70 | 17 | 1.6 | 87 | 0 | 0 | 0 | 928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 21 | 0 | 0 | 0 | 55 | 0 | 0 | 30 | 12 | 16 | 0 | 0 | 0 | 22 | 16 | 8 | 67 | 0 | 250 | 0 | 0 | 187 | 0 | 100 | 0 | 96 | 0 | 201 | 0 | 280 | 17 | 0 | 37 | 67 | 0 | 0 | 0.8 | 0
199
| Minimum Generation |  | 8421.22 | 8:00
| Highest Generation |  | 11663 | 21:00
| Day Peak Generation |  | 9406.83 | 11:00
| Evening Peak Generation |  | 11663 | 21:00
| HVDC Max Flow |  | 934 | 1:00
| HVDC EvPeak Flow |  | 925 | 21:00
| Load factor L.F |  | 84.95%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-07-31
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-07-30 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9406.83 | MW Hour : | 11:00 | Min. Gen. at | 8:00 | 8557.5 | MW
Evening Peak Generation : |  | 11663 | MW Hour : | 21:00 | Available Max Generation : |  | 14643 | MW
E.P. Demand (at gen end) : |  | 11663 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12100 | MW
Maximum Generation : |  | 11663 | MW Hour : | 21:00 | Reserve(Generation end) |  | 2543 | MW
Total Gen. (MKWH) : |  | 237.7747 | System Load Factor : | 84.95% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -330 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-07-31
Actual : | 105.85 | Ft.(MSL) , | Rule curve : | 88.83 | Ft.( MSL )
Gas Consumed : | Total = | 1404.89 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 151583298.83
|  | Coal : | 34892650.64 | Oil : | 398851426 | Total : | 585327375.47
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4276.8081 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1456.7357 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1305.6118 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1179.8812 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 1066.1584 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 860.3581 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 478.0017 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 221.4379 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 663.5656 |  |  | 0 | 0%
Total | 0 |  | 11508.5585 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2. | 7) Baghabari 100 MW
|  |  |  | 2) Khulna ST 110 MW | 8) Ghorasal Unit-7
|  |  |  | 3) Sikalbaha ST 60 MW | 9) Ghorasal Unit-2
|  |  |  | 4) Bheramara 410 MW. | 10) Ghorasal Unit-5
5) Siddhirganj ST
6) Ashuganj #4,5
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Rangpur-Lalmonirhat 132 kV Ckt tripped at 12:05 from Kurigram end showing Dist. R-phase relay and was
switched on at 12:38.
b) Fenchuganj 132/33 kV T1 transformer was shut down from 14:47 to 15:25 due to silicagel replacement.
c) Sirajganj Unit-2 ST was force shut down at 15:38 due to valve problem.
d) Joydevpur 132/33 kV T3 & T4 transformers tripped at 18:55 from both end showing O/C relay & due to 33 |  |  |  |  | About 80 MW power interruption occurred under Joydevpur S/S area
kV Burulia feeder fault and was switched on at 18:39. |  |  |  |  | from 18:35 to 18:39.
e) Rajshahi-Nator 132 kV Ckt-1 was under shut down from 01:59 to 10:40 (31/07/2019) due to red hot
maintenance at Bus isolator.
f) Siddirganj 335 MW CCPP STG tripped at 06:15(31/07/2019).
g) Jashore 132/33 kV T2 transformer was under shut down from 07:24 to 07:43(31/07/2019) fro C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-07-30 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 32 | 732000 | #2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 220 | 5340300
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 200 | 4954000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 50 | 1494 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 22 | 1572363 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 340 | 8125440 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 252 | 6481000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 8056250 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 24 | 153600 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 230 | 5952902 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 32 | 410136 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 15 | 60029 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 70 | 830258 | Low demand
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 329364
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
| Siddhirganj Desh |  | QRPP | 96*1.2 | 0 | 0 | 0 | Contract Expired
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 58560 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217 | 217 | 313 | 2082546 | Testing
| Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 75 | 587232 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 48 | 416592 | Engine problem
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 883800
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 130 | 996000 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 746881
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 374915 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 72 | 1252800 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1215240 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 564900 | Machine Problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 790000
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 42 | 816012 | Engine problem
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 14 | 85309 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 112 | 1604160 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 100 | 2407848
| Dhaka area Total |  |  |  | 5693 | 2952 | 57881931
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 95 | 2300000
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 120 | 2900000
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 189549
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 72090
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 871680
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 211 | 4938733
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4927805 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 131 | 2965534 | FGMO
44 | Sikalbaha 51 MW PP(Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 0 | 0 | Contract Expired
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 17 | 422361 | Transformer over load
46 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0
47 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 351172
48 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 256080 | Line O/L
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1802880
50 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 373584
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 34 | 496800
51 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 52 | 423360 | Line O/L
52 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26280
53 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 213 | 3924218 | Transformer over load
| Jodiac Power |  | IPP | 54.36 | 0 | 0 | 26280 | on test
| Karnaphuli Power Lid. |  | IPP | 110 | 0 | 0 | 0 | on test
| Chattogram area Total |  |  |  | 2053 | 1369 | 27268406
54 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 2342982 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
55 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 184 | 4719000 | FGMO
56 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7399700 | FGMO
57 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 290 | 7279000 | FGMO
58 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 37 | 735912 | Engine problem
59 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 52 | 1226880
60 | Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
61 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 75 | 1706181 | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 893698 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 50 | 568727 | Transformer over load
64 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
65 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
66 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2123420 | Gas shortage
67 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 192 | 1945440 | Low demand
68 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 448740
69 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 226980
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 154 | 3286080
70 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 819500
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 48 | 494947 | Engine problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 14 | 351620 | Engine problem
73 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1682 | 36568807
74 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 145 | 3423000 | GT-1 under maint.
75 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 521352
76 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 1325760
77 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11700
78 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 160 | 1435200 | Line O/L
79 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2613600
| Mymensingh Area Total |  |  |  | 637 | 537 | 9330612
80 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 54 | 1289000
81 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 69 | 1649400
82 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3144894 | Frequency control
83 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 263 | 6035000 | FGMO
84 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 837600
85 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 47 | 987696
86 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
87 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 64 | 1486560
88 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 75 | 1322880 | Engine problem
89 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 40 | 798120 | Engine problem
90 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 112 | 2719610 | FGMO
91 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 432050
92 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 45 | 748700 | Engine problem
93 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 428568
94 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7427250 | FGMO
95 | Bibiyana-III 400 MW CCPP |  | PDB | 285 MW | 285 | 232 | 5742000 | FGMO
96 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 242100
| Sylhet Area Total |  |  |  | 1834 | 1523 | 35555428
97 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 32 | 121600
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 925 | 22077091
| Khulna 115 MW PP (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
98 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 887040
99 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 27 | 280320
100 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
101 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 68 | 584832
102 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
103 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 499125
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
104 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 668160
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1172640
106 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 68 | 1237824 | Engine problem
| Khulna Area Total |  |  |  | 2314 | 1480 | 27528632
107 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 252384 | Line O/L
108 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
109 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 36 | 546890
110 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 173 | 4217788
111 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 95 | 1832766
| Barisal Area Total |  |  |  | 462 | 336 | 6849828
112 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 60 | 1400000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
113 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 258672
114 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 32956 | Reserve
115 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 33 | 131680 | Engine problem
116 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 42 | 694853 | Engine problem
117 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 45 | 330322
118 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 184 | 4773382 | FGMO
119 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 146 | 4149309 | ST under S/D
120 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 191 | 4707936 | FGMO
121 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 390 | 7159273 | Frequency control
122 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 322914
123 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 512400
124 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 16 | 372240
125 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 198090
126 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 506400
127 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 1016744
128 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
129 | Bagura 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 93 | 2284512
| Rajshahi Area Total |  |  |  | 2070 | 1467 | 28851683
130 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 70 | 1676072
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
131 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 232 | 5920800
132 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
133 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 153000
| Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 0 | 0 | 149760 | On test
| Sympa Solar Power 8MW |  | IPP | 8 MW | 0 | 0 | 39700
| Rangpur Area Total |  |  |  | 484 | 317 | 7939332
| Total |  |  |  | 18438 | 11663 | 237774659
| Eastern Grid Total |  |  |  | 13108 | 8063 | 166605184
| Western Grid Total |  |  |  | 5330 | 3600 | 71169475
| National Grid Total |  |  |  | 18438 | 11663 | 237774659
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2019-07-30
(a) ENTIRE EASTERN GRID : |  | 7481 | MW | (b) ENTIRE WESTERN GRID : |  | 3601 | MW
i) Dhaka area |  | 3994 | MW | i) Khulna area |  | 1387 | MW
ii) Chittagong area |  | 1128 | MW | ii) Rajshahi area |  | 1228 | MW
iii) Comilla area |  | 938 | MW | iii) Barisal area |  | 305 | MW
iv) Mymensingh area |  | 957 | MW | iv) Rangpur area |  | 681 | MW
v) Sylhet area |  | 464 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11082 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 118 | 1500 | Jamalpur | 131 | 100 | Jessore | 114 | 2000
Munsiganj | 106 | 100 | Sherpur | 94 | 2100 | Benapol | 42 | 2000
Sonargaon | 74 | 100 | Srimongal | 43 | 1930 | Jhenida | 110 | 2000
Shyampur | 196 | 1300 | Shahjibazar | 114 | 2000 | Bottail | 124 | 2000
Bhulta | 192 | 2100 | Fenchuganj | 36 | 2200 | G.K Project | 57 | 2000
Madanganj | 47 | 2100 | Kulawara | 42 | 2100 | Faridpur | 172 | 2000
Shitalakhya | 101 | 1500 | Sylhet | 125 | 1930 | Madaripur | 110 | 2200
Rahim steel | 19 | 1100 | Chatak | 29 | 1930 | Sariatpur | 29 | 1830
Matuail | 94 | 900 | Sunamganj | 35 | 2000 | Gopalganj | 84 | 1930
Ghorasal | 83 | 2100 | Biani Bazar | 54 | 2100 | Bagerhat | 81 | 2100
Narsingdi | 136 | 100 | Comilla (S) | 156 | 1930 | Mongla | 40 | 100
Haripur (SBU) | 98 | 800 | Comilla(N) | 101 | 1930 | Satkhira | 100 | 2100
Ullon | 86 | 1600 | Chandpur | 81 | 2000 | Gallamari | 47 | 1300
Hasnabad | 200 | 2100 | Feni | 114 | 2100 | Magura | 53 | 2000
Magbazar | 137 | 1400 | Chowmuhani | 146 | 2300 | Chuadanga | 82 | 2100
Maniknagar | 114 | 1100 | Ashuganj | 53 | 2300 | Barisal(N) | 39 | 2100
Bangabhaban | 36 | 1700 | Daudkandi | 114 | 2000 | Barisal (S) | 94 | 2000
Narinda | 94 | 1500 | B.Baria | 131 | 2200 | Patuakhali | 102 | 2200
Dhanmondi | 163 | 1100 | Ramganj | 76 | 2100 | Bhandaria | 54 | 2200
Lalbag | 80 | 1300 | Madunaghat | 56 | 2000 | Borhan Uddin | 36 | 2100
Madartek | 55 | 2100 | Hathazari | 97 | 2100 | Ishurdi | 69 | 1930
Mirpur | 106 | 1900 | Khulshi | 199 | 1500 | Ruppur Paromanobik | 1 | 100
Kalyanpur | 114 | 1930 | Halishahar | 139 | 1700 | Natore | 125 | 2000
Gulshan | 158 | 1300 | Baraulia | 160 | 500 | Bogra | 233 | 2000
Uttara | 84 | 1300 | Sikalbaha | 37 | 2000 | Noagaon | 114 | 2100
Uttara New | 18 | 1000 | Dohazari | 88 | 1900 | Rajshahi | 154 | 2100
Kamrangirchar | 72 | 1300 | Cox'sbazar | 88 | 1900 | C.Nawabganj | 74 | 2000
Savar | 139 | 1500 | Chandraghona | 24 | 1900 | Amnura | 36 | 2100
Bhasantec | 161 | 1300 | Kaptai | 4.1 | 1900 | Pabna | 110 | 2000
Agargaon | 58 | 1300 | A. Khaer Stl. | 9 | 1800 | Shahjadpur | 100 | 2000
Satmosjid | 110 | 1900 | Bakulia | 100 | 1500 | Serajganj | 105 | 2100
Tongi | 145 | 2000 | Julda | 22 | 1100 | Niyamatpur | 59 | 2100
Kabirpur | 205 | 1300 | TK chemical | 1.6 | 100 | Joypurhat | 56 | 2300
Basundhara | 122 | 2100 | Modern Steel | 17 | 500 | Mohastangor | 15 | 2100
Manikganj | 88 | 2100 | Shahmirpur | 27 | 100 | Rangpur | 142 | 2000
Joydevpur | 198 | 1600 | Khagrachhari | 17 | 1830 | Lalmonirhat | 67 | 1930
New Tongi | 101 | 1600 | Matarbari | 27 | 2000 | Saidpur | 105 | 2000
Korda | 256 | 2100 | Baroiar Hat | 32 | 1830 | Purbasadipur | 101 | 2200
Dhamrai | 60 | 2100 | Rangamati | 12 | 1930 | Thakurgaon | 71 | 2000
Valuka | 94 | 2100 | Abul Khair 230 | 160 | 1700 | Palashbari | 112 | 2000
Tangail | 196 | 2100 | BSRM | 158 | 1900 | Barapukuria | 51 | 2000
Mymensing | 238 | 2100 | Goalpara | 27 | 2000 | Panchagar | 38 | 2100
Kishorganj | 126 | 2100 | Central (S) | 90 | 1930 | Joldhaka | 27 | 2000
Netrokona | 95 | 1930 | Noapara | 99 | 1930
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-07-30
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | 126
Bibiyana | 390 | 5:00 | 380 | 22:00 | Kaliakoir | 366 | 6:00 | 357
Bheramara | 402 | 7:00 | 352 | 13:00 | Bhulta | 382 | 3:00 | 371
Ashuganj(N) | 386 | 4:00 | 376 | 9:00
230 KV | KV |  | KV |  | 230 KV | KV |  | 10:00
Ghorasal | 230 | 1:00 | 224 | 15:00 | Hathazari | 221 | 3:00 | 214
Ishurdi | 236 | 5:00 | 0 | 7:00 | Megnaghat | 223 | 20:00 | 216
Ashuganj | 236 | 3:00 | 231 | 9:00 | Fenchuganj | 236 | 3:00 | 232
Serajganj | 232 | 6:00 | 226 | 21:00 | Siddhirganj | 221 | 5:00 | 213
Baghabari | 235 | 7:00 | 230 | 1:00 | Maniknagar | 219 | 3:00 | 212
Barapukuria | 235 | 7:00 | 220 | 21:00 | Old Airport | 219 | 4:00 | 211
Bogra | 227 | 6:00 | 210 | 21:00 | Barisal | 232 | 14:00 | 221
Khulna South | 225 | 6:00 | 214 | 2:00 | AKSML | 217 | 3:00 | 212
Rampura | 220 | 3:00 | 213 | 11:00 | BSRM | 220 | 4:00 | 213
Haripur | 220 | 23:00 | 212 | 11:00 | Bibiyana | 231 | 3:00 | 227
Hasnabad | 217 | 3:00 | 212 | 10:00 | Bhulta | 222 | 6:00 | 214
Aminbazar | 219 | 4:00 | 212 | 9:00 | Ashuganj (S) | 234 | 4:00 | 228
Tongi | 219 | 19:00 | 210 | 9:00 | Kaliakoir | 222 | 5:00 | 215
Comilla (N) | 229 | 3:00 | 224 | 9:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 130 | 500 | 125 | 1000 | Hathazari | 131 | 300 | 127
Munsiganj | 132 | 1930 | 124 | 1000 | Khulshi | 128 | 100 | 124
Megnaghat | 131 | 1930 | 125 | 1100 | Halishahar | 132 | 100 | 125
Shyampur | 130 | 300 | 124 | 1100 | Baraulia | 130 | 1930 | 124
Bhulta | 124 | 700 | 118 | 1300 | Sikalbaha | 132 | 1930 | 128
Madanganj | 132 | 1930 | 124 | 900 | Dohazari | 130 | 1700 | 127
Shitalakhya | 134 | 1930 | 124 | 1000 | Cox'sbazar | 125 | 1200 | 119
Rahim steal | 131 | 1930 | 126 | 1000 | Chandraghona | 132 | 1830 | 129
Matuail | 129 | 500 | 123 | 1200 | Kaptai | 132 | 100 | 130
Ghorasal | 136 | 2000 | 134 | 900 | A. Khaer Stl. | 130 | 2100 | 125
Narsinghdi | 125 | 600 | 120 | 1300 | Bakulia | 131 | 2000 | 126
Haripur (SBU) | 131 | 500 | 126 | 1600 | Julda | 131 | 100 | 126
Ullon | 134 | 600 | 127 | 1200 | TK Chemical | 134 | 100 | 129
Hasnabad | 130 | 600 | 126 | 1300 | Modern Steel | 132 | 1900 | 127
Magbazar | 135 | 700 | 127 | 1200 | Shahmirpur | 132 | 2000 | 126
Maniknagar | 135 | 600 | 127 | 1200 | Khagrachhari | 131 | 1200 | 128
Bangabhaban | 135 | 600 | 127 | 1200 | Matarbari | 127 | 1700 | 122
Narinda | 135 | 600 | 127 | 1200 | Baroiar Hat | 127 | 700 | 126
Dhanmondi | 134 | 600 | 127 | 1200 | Rangamati | 131 | 1400 | 128
Lalbag | 132 | 2000 | 121 | 1200 | Goalpara | 137 | 1800 | 128
Madartek | 135 | 600 | 127 | 1200 | Central s/s | 137 | 2300 | 129
Mirpur | 133 | 500 | 127 | 1100 | Noapara | 135 | 500 | 124
Kalyanpur | 136 | 200 | 130 | 1100 | Jessore | 129 | 1830 | 118
Gulshan | 134 | 400 | 127 | 1100 | Benapol | 131 | 1800 | 121
Uttara | 132 | 100 | 125 | 1200 | Jhenida | 129 | 1800 | 114
Uttara New | 130 | 400 | 125 | 1000 | Bottail | 134 | 1800 | 121
Kamrangirchar | 130 | 2000 | 122 | 1100 | G.K Project | 140 | 1800 | 130
Savar | 132 | 300 | 126 | 1200 | Faridpur | 132 | 700 | 118
Bhasantec | 135 | 400 | 127 | 1100 | Madaripur | 132 | 1800 | 120
Agargaon | 135 | 300 | 129 | 1000 | Sariatpur | 131 | 600 | 118
Satmosjid | 135 | 400 | 128 | 1200 | Gopalganj | 139 | 800 | 129
Tongi | 133 | 1900 | 127 | 900 | Bagerhat | 136 | 1830 | 127
Kabirpur | 131 | 600 | 126 | 2100 | Mongla | 133 | 1800 | 125
Basundhara | 130 | 2000 | 124 | 900 | Satkhira | 136 | 1800 | 126
Manikganj | 137 | 2000 | 130 | 800 | Gallamari | 138 | 400 | 129
Joydevpur | 137 | 2000 | 130 | 900 | Magura | 128 | 1800 | 111
New Tongi | 132 | 2000 | 125 | 900 | Chuadanga | 125 | 1800 | 105
Kodda | 133 | 1300 | 121 | 900 | Barisal(N) | 137 | 600 | 130
Dhamrai | 132 | 600 | 126 | 2100 | Barisal (S) | 136 | 700 | 129
Valuka | 125 | 1000 | 116 | 2100 | Patuakhali | 135 | 600 | 125
Tangail | 134 | 600 | 122 | 2200 | Bhandaria | 135 | 1800 | 127
Mymensing | 128 | 600 | 118 | 2200 | Ishurdi | 138 | 1800 | 129
Kishorganj | 129 | 700 | 120 | 1900 | Ruppur Paromanobik | 137 | 1800 | 131
Netrokona | 129 | 1100 | 119 | 1930 | Natore | 134 | 600 | 125
Jamalpur | 138 | 100 | 125 | 900 | Bogra | 135 | 600 | 123
Sherpur | 134 | 100 | 125 | 1400 | Noagaon | 130 | 600 | 116
Srimongal | 135 | 400 | 132 | 1930 | Rajshahi | 133 | 1830 | 122
Shahjibazar | 134 | 1100 | 130 | 2100 | C.Nawabganj | 129 | 1900 | 120
Fenchuganj | 136 | 1400 | 133 | 100 | Amnura | 134 | 1900 | 119
Khulawara | 134 | 700 | 130 | 100 | Pabna | 134 | 500 | 124
Sylhet | 134 | 300 | 132 | 1500 | Shahjadpur | 140 | 1830 | 135
Chatak | 134 | 600 | 130 | 1930 | Serajganj | 135 | 600 | 125
Sunamganj | 133 | 600 | 129 | 1900 | Niyamatpur | 130 | 1800 | 113
Biani Bazar | 133 | 600 | 128 | 2100 | Joypurhat | 130 | 600 | 113
Comilla(s) | 125 | 700 | 120 | 1800 | Mohastangor | 134 | 600 | 119
Comilla(n) | 134 | 700 | 132 | 1100 | Rangpur | 130 | 600 | 110
Chandpur | 135 | 2000 | 128 | 1500 | Lalmonirhat | 126 | 700 | 105
Feni | 127 | 700 | 124 | 1500 | Saidpur | 131 | 600 | 110
Chowmuhani | 124 | 700 | 120 | 1900 | Purbasadipur | 128 | 600 | 108
Ashuganj | 132 | 2100 | 135 | 1600 | Thakurgaon | 126 | 600 | 100
Daudkandi | 128 | 1300 | 125 | 1000 | Palashbari | 130 | 600 | 112
B.Baria | 131 | 700 | 127 | 2100 | Barapukuria | 135 | 700 | 120

## L-Curve
Date | 2019-07-30
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 280 | 7785 | 3428 | 11213 |  |  |  | QF-LDC-12
0:30 | 240 | 7657 | 3348.5 | 11005.5 | Date: | 2019-07-30
1:00 | 200 | 7529 | 3269 | 10798
1:30 | 200 | 7388.5 | 3199.5 | 10588
2:00 | 200 | 7248 | 3130 | 10378
2:30 | 195 | 7177.5 | 3097.5 | 10275 | [5 empty] | Gen. at Eve. Peak | 11663 | 11663 MW (21:00 )
3:00 | 190 | 7107 | 3065 | 10172 | [6 empty] | 21:00
3:30 | 182.5 | 7006.5 | 3039 | 10045.5 | [5 empty] | Gen. at Day Peak | 9406.83 | 9406.83 MW (11:00 )
4:00 | 175 | 6906 | 3013 | 9919 | [6 empty] | 11:00
4:30 | 152.5 | 6806.5 | 2918.5 | 9725 | [5 empty] | Highest Generation | 11663
5:00 | 130 | 6707 | 2824 | 9531 | [6 empty] | 21:00
5:30 | 80 | 6342.425 | 2749 | 9091.425
6:00 | 30 | 5977.85 | 2674 | 8651.85
6:30 | 50 | 5926.415 | 2656.6 | 8583.015
7:00 | 70 | 5874.98 | 2639.2 | 8514.18
7:30 | 100 | 5862.1 | 2605.6 | 8467.7
8:00 | 130 | 5849.22 | 2572 | 8421.22
8:30 | 185 | 5984.47 | 2614 | 8598.47
9:00 | 240 | 6119.72 | 2656 | 8775.72
9:30 | 167.5 | 6324.12 | 2670.95 | 8995.07
10:00 | 95 | 6528.52 | 2685.9 | 9214.42
10:30 | 117.5 | 6611.675 | 2698.95 | 9310.625
11:00 | 140 | 6694.83 | 2712 | 9406.83
11:30 | 80 | 6703.625 | 2697.95 | 9401.575
12:00 | 20 | 6712.42 | 2683.9 | 9396.32
12:30 | 37.5 | 6767.28 | 2695.95 | 9463.23
13:00 | 55 | 6822.14 | 2708 | 9530.14
13:30 | 55 | 6719.37 | 2650.7 | 9370.07
14:00 | 55 | 6616.6 | 2593.4 | 9210
14:30 | 52.5 | 6839.8 | 2602.3 | 9442.1
15:00 | 50 | 7063 | 2611.2 | 9674.2
15:30 | 60 | 7011.05 | 2657.2 | 9668.25
16:00 | 70 | 6959.1 | 2703.2 | 9662.3
16:30 | 65 | 6851.485 | 2653.35 | 9504.835
17:00 | 60 | 6743.87 | 2603.5 | 9347.37
17:30 | 90 | 6556.62 | 2583.4 | 9140.02
18:00 | 120 | 6369.37 | 2563.3 | 8932.67
18:30 | 100 | 6796.185 | 2889.15 | 9685.335
19:00 | 80 | 7223 | 3215 | 10438
19:30 | 255 | 7752 | 3591 | 11343
20:00 | 330 | 7991 | 3588 | 11579 |  |  |  | Executive Engineer
20:30 | 310 | 8027 | 3594 | 11621 |  |  |  | Network Operation Division
21:00 | 290 | 8063 | 3600 | 11663
21:30 | 290 | 8009 | 3564.5 | 11573.5
22:00 | 290 | 7955 | 3529 | 11484 |  |  |  |  | Page 6 of 7
22:30 | 275 | 7912 | 3526 | 11438
23:00 | 260 | 7869 | 3523 | 11392
23:30 | 270 | 7827 | 3475.5 | 11302.5
24:00 | 280 | 7785 | 3428 | 11213
11663 MW (21:00 )
9406.83 MW (11:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-07-30 |  | Energy | 237774659
[10 empty] | 2019-07-30 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4645 | 928 | 2109 | 2492 | 270 | 214 | 415 | 0 | 140
0:30 | 4546 | 931 | 2146.5 | 2365.5 | 295.5 | 213.5 | 357.5 | 0 | 150 | Date: | 2019-07-30
1:00 | 4447 | 934 | 2184 | 2239 | 321 | 213 | 300 | 0 | 160
1:30 | 4470.5 | 931.5 | 2200.5 | 2019.5 | 321 | 213.5 | 272.5 | 0 | 159 | [7 empty] | Total Energy | 237.7747 | Total Energy Gen 197.480 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 197.480 MKWHr
2:00 | 4494 | 929 | 2217 | 1800 | 321 | 214 | 245 | 0 | 158 | [7 empty] | Energy not Served | 0
2:30 | 4481 | 924.5 | 2208 | 1749 | 321 | 214 | 220.5 | 0 | 157 | [7 empty] | Energy Requirement | 237.7747
3:00 | 4468 | 920 | 2199 | 1698 | 321 | 214 | 196 | 0 | 156
3:30 | 4467 | 920 | 2164 | 1621 | 321.5 | 215 | 184 | 0 | 153 | [6 empty] | Shortage
4:00 | 4466 | 920 | 2129 | 1544 | 322 | 216 | 172 | 0 | 150
4:30 | 4476.5 | 920 | 2142 | 1383.5 | 322 | 216 | 118 | 0 | 147
5:00 | 4487 | 920 | 2155 | 1223 | 322 | 216 | 64 | 0 | 144
5:30 | 4407.5 | 920 | 1911.5 | 1119 | 322 | 216 | 56 | 0 | 139
6:00 | 4328 | 920 | 1668 | 1015 | 322 | 216 | 48 | 0 | 134
6:30 | 4328.5 | 920 | 1664.5 | 949.5 | 321.5 | 216 | 52 | 0 | 128 |  |  |  |  | Coal
7:00 | 4329 | 920 | 1661 | 884 | 321 | 216 | 56 | 0 | 122
7:30 | 4323 | 919.5 | 1648.5 | 863.5 | 321 | 216 | 49 | 0 | 122 |  |  |  | Oil |  |  |  | ,
8:00 | 4317 | 919 | 1636 | 843 | 321 | 216 | 42 | 0 | 122
8:30 | 4424 | 917.5 | 1676.5 | 866.5 | 320.5 | 216 | 46.5 | 0 | 123
9:00 | 4531 | 916 | 1717 | 890 | 320 | 216 | 51 | 0 | 124
9:30 | 4547 | 913 | 1866 | 958 | 320.5 | 215 | 44 | 0 | 121
10:00 | 4563 | 910 | 2015 | 1026 | 321 | 214 | 37 | 0 | 118
10:30 | 4465 | 911 | 2046.5 | 1194.5 | 319 | 213.5 | 26.5 | 0 | 121
11:00 | 4367 | 912 | 2078 | 1363 | 317 | 213 | 16 | 0 | 124
11:30 | 4351.5 | 911.5 | 2052 | 1394 | 317.5 | 209 | 16 | 0 | 129
12:00 | 4336 | 911 | 2026 | 1425 | 318 | 205 | 16 | 0 | 134
12:30 | 4383 | 912.5 | 2021 | 1447 | 318 | 208.5 | 16 | 0 | 135
13:00 | 4430 | 914 | 2016 | 1469 | 318 | 212 | 16 | 0 | 136
13:30 | 4430 | 914 | 2016 | 1469 | 318 | 212 | 16 | 0 | 136
14:00 | 4430 | 914 | 2016 | 1469 | 318 | 212 | 16 | 0 | 136
14:30 | 4550 | 914.5 | 1916 | 1527.5 | 317.5 | 211 | 19.5 | 0 | 128
15:00 | 4670 | 915 | 1816 | 1586 | 317 | 210 | 23 | 0 | 120
15:30 | 4594.5 | 915 | 1868 | 1598 | 317 | 209 | 39.5 | 0 | 114
16:00 | 4519 | 915 | 1920 | 1610 | 317 | 208 | 56 | 0 | 108
16:30 | 4452 | 920 | 1863 | 1564 | 317.5 | 208 | 60 | 0 | 114
17:00 | 4385 | 925 | 1806 | 1518 | 318 | 208 | 64 | 0 | 120
17:30 | 4293 | 925 | 1672 | 1517 | 318.5 | 209 | 75.5 | 0 | 128
18:00 | 4201 | 925 | 1538 | 1516 | 319 | 210 | 87 | 0 | 136
18:30 | 4379.5 | 925 | 1695 | 1749.5 | 318 | 210 | 263 | 0 | 145
19:00 | 4558 | 925 | 1852 | 1983 | 317 | 210 | 439 | 0 | 154
19:30 | 4576 | 924 | 1979 | 2618 | 317 | 210 | 563 | 0 | 156
20:00 | 4565 | 925 | 1969 | 2851 | 317 | 210 | 588 | 0 | 154
20:30 | 4607 | 925 | 2020.5 | 2808.5 | 309.5 | 210.5 | 586 | 0 | 154
21:00 | 4649 | 925 | 2072 | 2766 | 302 | 211 | 584 | 0 | 154
21:30 | 4646.5 | 925 | 2069 | 2714 | 285 | 211.5 | 567.5 | 0 | 155
22:00 | 4644 | 925 | 2066 | 2662 | 268 | 212 | 551 | 0 | 156
22:30 | 4656.5 | 926.5 | 2090 | 2598.5 | 269 | 213 | 531.5 | 0 | 153
23:00 | 4669 | 928 | 2114 | 2535 | 270 | 214 | 512 | 0 | 150
23:30 | 4657 | 928 | 2111.5 | 2513.5 | 270 | 214 | 463.5 | 0 | 145 | Max Temp. in Dhaka |  | 31.6° C
24:00 | 4645 | 928 | 2109 | 2492 | 270 | 214 | 415 | 0 | 140
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 197.480 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 197.480 MKWHr
Note on W13: Author:

## Generation
2019-07-30
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 123 | 124 | 124 | 126 | 126 | 126 | 126 | 126 | 126 | 124 | 123 | 115 | 122 | 120 | 120 | 118 | 118 | 120 |  | 120 | 120 | 120 | 121 | 122 | 124 | 124 | 2762733
2 | Karnaphuli Hydro PP Unit-4 & 5 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2176000
3 | Chattogram TPP-1 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 2300000
4 | Chattogram TPP-2 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
5 | Raozan 25 MW PP | 8 | 0 | [14 empty] | 0 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 189549
| Teknaf 20MW PP (Solartech) |  |  |  |  | 0 | 0.49 | 2.78 | 1 | 5 | 2 | 11 | 13 | 9 | 9.5 | 9.1 | 3.6 | 0.97 | 0.17 |  | 0 | [6 empty] | 72090
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 206 | 205 | 204 | 205 | 202 | 204 | 205 | 217 | 227 | 206 | 205 | 205 | 204 | 217 | 205 | 214 | 204 |  | 210 | 204 | 203 | 204 | 203 | 205 | 204 | 4927805
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 136 | 143 | 130 | 130 | 130 | 130 | 130 | 133 | 130 | 90 | 90 |  | 135 | 130 | 130 | 131 | 130 | 130 | 130 | 2965534
10 | Sikalbaha 150MW GTPP(Oil) | [26 empty] | 0
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 0 |  | 78 | 85 | 85 | 85 | 71 | 36 | 17 | 351172
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 422361
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 9 | 9 | 9 | 9 | 9 | 9 | 1 | 9 | 4 | 3 | 3 | 3 | 58 | 77 | 327 | 330 | 330 | 308 |  | 308 | 308 | 233 | 313 | 294 | 295 | 295 | 2082546
18 | Kodda 300 MW PP Unit-2 (Summit) | [17 empty] | 0 |  | 11 | 30 | 36 | 14 | 15 | 0 | 0 | 85309
19 | Ashuganj 195MW PP (APSCL-United) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 72 | 68 | 72 | 68 | 68 | 68 | 68 | 68 |  | 68 | 68 | 68 | 75 | 75 | 75 | 75 | 1706181
20 | Ghorasal TPP (Unit-1&2) | 30 | 30 | 30 | 30 | 30 | 30 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 732000
21 | Ghorasal Repowered CCPP Unit-3 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 220 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 160 | 160 |  | 159 | 159 | 220 | 220 | 220 | 220 | 219 | 5340300
22 | Ghorasal Repowered CCPP Unit-4 | 220 | 220 | 220 | 220 | 222 | 221 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 221 | 221 | 220 | 120 | 120 |  | 200 | 200 | 201 | 200 | 220 | 201 | 200 | 4954000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2342982
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 27 | 27 | 27 | 27 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 33 | 33 | 33 | 735912
33 | Ashuganj 225 MW CCPP | 186 | 217 | 219 | 218 | 219 | 182 | 186 | 189 | 204 | 194 | 189 | 182 | 182 | 182 | 203 | 184 | 197 | 189 |  | 203 | 182 | 181 | 184 | 182 | 191 | 183 | 4719000
34 | Ashuganj 450 MW CCPP(South) | 310 | 315 | 305 | 305 | 305 | 270 | 305 | 310 | 340 | 315 | 310 | 310 | 310 | 260 | 285 | 260 | 265 | 260 |  | 295 | 290 | 290 | 290 | 290 | 290 | 290 | 7279000
| Ashuganj 450 MW CCPP(North) | 310 | 315 | 310 | 310 | 310 | 270 | 255 | 260 | 285 | 365 | 310 | 310 | 310 | 260 | 285 | 260 | 270 | 260 |  | 335 | 310 | 310 | 310 | 310 | 310 | 310 | 7399700
35 | Ashuganj 55 MW PP (Precision) | 51 | 52 | 51 | 49 | 51 | 51 | 52 | 51 | 50 | 51 | 49 | 49 | 48 | 51 | 53 | 52 | 51 | 52 |  | 52 | 52 | 52 | 52 | 51 | 52 | 51 | 1226880
36 | Chandpur 150 MW CCPP | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 87 | 91 | 90 | 87 | 90 | 91 |  | 90 | 91 | 90 | 90 | 90 | 90 | 91 | 2123420
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 340 | 340 | 340 | 340 | 345 | 340 | 340 | 339 | 366 | 370 | 340 | 340 | 340 | 300 | 300 | 300 | 300 | 270 |  | 270 | 340 | 342 | 340 | 341 | 348 | 340 | 8125440
40 | Meghnaghat 450 MW CCPP(MPL) | 370 | 370 | 370 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 300 | 300 | 300 | 330 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 8056250
41 | Haripur 360MW CCPP(HPL) | 303 | 303 | 303 | 303 | 303 | 252 | 252 | 252 | 254 | 283 | 283 | 283 | 283 | 252 | 253 | 252 | 283 | 252 |  | 252 | 253 | 254 | 252 | 252 | 252 | 252 | 6481000
42 | RPCL 210MW CCPP | 147 | 148 | 148 | 148 | 148 | 148 | 148 | 145 | 145 | 145 | 145 | 145 | 143 | 143 | 145 | 144 | 145 | 145 |  | 145 | 145 | 148 | 145 | 147 | 146 | 148 | 3423000
43
44 | Fenchugonj CCPP Phase-1 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 53 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 53 | 54 | 1289000
45 | Fenchugonj CCPP Phase-2 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 |  | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 1649400
46 | Shajibazar 330 MW CCPP | 265 | 262 | 263 | 263 | 264 | 262 | 265 | 263 | 275 | 272 | 259 | 261 | 263 | 267 | 267 | 263 | 264 | 262 |  | 267 | 262 | 266 | 263 | 262 | 264 | 265 | 6035000
47 | Shahjibazar GTPP Unit- 8 & 9 | 63 | 63 | 57 | 64 | 56 | 51 | 63 | 63 | 61 | 61 | 63 | 63 | 64 | 64 | 67 | 65 | 62 | 63 |  | 62 | 63 | 65 | 64 | 64 | 63 | 64 | 1486560
48 | Shahjibazar 86MW PP (Shahjibazar) | 73 | 73 | 73 | 73 | 73 | 30 | 10 | 10 | 10 | 50 | 71 | 73 | 70 | 40 | 40 | 40 | 40 | 10 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1322880
49 | Shahjibazar 50MW PP (EPL) | 43 | 43 | 43 | 43 | 43 | 10 | 10 | 10 | 10 | 40 | 40 | 40 | 40 | 40 | 42 | 42 | 10 | 10 |  | 10 | 40 | 40 | 40 | 43 | 45 | 45 | 798120
50 | Sylhet 150 MW CCPP | 109 | 109 | 109 | 110 | 110 | 110 | 110 | 122 | 124 | 112 | 111 | 110 | 110 | 120 | 123 | 98 | 98 | 75 |  | 123 | 109 | 110 | 112 | 109 | 115 | 115 | 2719610
51 | Sylhet 20 MW GTPP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 432050
52 | Sylhet 50MW PP (EPL) | 44 | 44 | 44 | 44 | 44 | 10 | 12 | 12 | 12 | 42 | 40 | 41 | 42 | 12 | 12 | 12 | 12 | 12 |  | 43 | 44 | 44 | 45 | 45 | 45 | 45 | 748700
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 242100
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 11 | 11 | 11 | 11 | 44 | 50 | 53 | 53 | 11 | 11 | 11 | 11 | 11 |  | 52 | 53 | 53 | 53 | 53 | 53 | 53 | 837600
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 24 | 24 | 16 | 16 | 16 | 16 | 0 |  | 0 | 16 | 0 | 16 | 16 | 16 | 16 | 428568
57 | Bibiana-II 341 MW CCPP (Summit) | 295 | 300 | 285 | 275 | 300 | 265 | 290 | 290 | 320 | 320 | 310 | 300 | 300 | 290 | 310 | 315 | 310 | 290 |  | 305 | 310 | 300 | 285 | 305 | 300 | 300 | 7427250
58 | Nababganj 55 MW PP (Southern power ) | 17 | 0 | [7 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 35 | 35 | 17 | 17 | 17 | 17 | 374915
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | [5 empty] | 10 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 373584
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 0 |  |  |  | 19 | 19 | 0 | 0 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 329364
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 521352
63 | Impoprt (Tripura) | 160 | 158 | 156 | 150 | 144 | 134 | 122 | 122 | 124 | 118 | 124 | 134 | 136 | 132 | 120 | 108 | 120 | 136 |  | 154 | 156 | 154 | 154 | 156 | 150 | 140 | 3286080
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 40 | 40 | 40 | 33 | 10 | 3 | 2 | 2 | 4 | 11 | 6 | 4 | 5 | 8 | 9 |  | 21 | 27 | 27 | 34 | 38 | 38 | 40 | 496800
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 448740
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 0 |  |  | 0 | 11 | 11 | 11 | 11 | 11 | 226980
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 819500
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 13 | 14 | 15 | 0 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 8 | 8 | 8 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 351620
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 21 | 21 | 21 | 21 | 0 | 0 | 21 | 21 | 21 | 21 | 25 |  | 20 | 29 | 32 | 32 | 32 | 32 | 31 | 615240
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 20 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 564900
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 32 | 33 | 32 | 32 | 32 | 25 | 32 | 32 | 32 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 790000
73 | Ghorashal 108MW PP (Regent) | 101 | 101 | 101 | 101 | 101 | 22 | 22 | 22 | 22 | 85 | 90 | 97 | 100 | 101 | 101 | 100 | 52 | 22 |  | 22 | 22 | 21 | 22 | 22 | 66 | 99 | 1572363
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [17 empty] | 0 |  | 5 | 10 | 40 | 0 |  |  | 0 | 58560
78 | Gazipur 52 MW PP | 41 | 41 | 25 | 25 | 0 |  |  | 3 | 30 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 816012
79 | Kodda 150MW PP | 62 | 32 | 32 | 32 | 0 |  |  |  | 10 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 60 | 100 | 127 | 130 | 130 | 126 | 100 | 996000
80 | Jamalpur 95 MW PP(Powerpac) | 95 | 95 | 95 | 95 | 95 | 67 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 42 | 95 | 95 | 95 | 95 | 95 | 95 | 1325760
81 | Jangalia 52 MW PP (Lakdanavi) | 25 | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 10 | 38 | 48 | 52 | 52 | 52 | 494947
| Gazipur 100 MW PP | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 |  | 102 | 102 | 102 | 100 | 100 | 98 | 98 | 2407848
| Kaptai 7 MW Solar PP |  |  |  |  | 0 | 0.26 | 1 | 2.72 | 3.62 | 2.12 | 1.83 | 4.02 | 0.74 | 1.6 | 1.9 | 2.1 | 0.7 | 0.1 |  | 0 | [6 empty] | 26280
| Jodiac Power | [9 empty] | 0 | 11 | 0 | [14 empty] | 26280
Karnaphuli Power Lid.
82 | Madanganj 102 PP(Summit) | 25 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 0 |  |  |  | 0 |  | 10 | 30 | 45 | 32 | 30 | 30 | 15 | 410136
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [12 empty] | 5 | 61 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 70 |  |  | 0 | 830258
86 | Meghnaghat CCPP(Summit) | 265 | 272 | 272 | 265 | 255 | 230 | 260 | 272 | 286 | 283 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5952902
87 | Meghnaghat 100 MW(IEL) | 30 | 0 | [15 empty] | 0 |  | 7 | 56 | 56 | 24 | 24 | 0 | 0 | 153600
88 | Ghorashal 78.5 MW PP(MAX) | 74 | 74 | 74 | 74 | 74 | 50 | 50 | 50 | 50 | 50 | 73 | 73 | 72 | 72 | 72 | 71 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1494
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 256080
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 50 | 50 | 10 | 10 | 10 | 10 | 36 | 46 | 46 | 50 | 50 | 50 | 50 | 10 | 10 |  | 23 | 47 | 47 | 47 | 47 | 50 | 50 | 987696
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 10 | 10 | 10 | 10 | 20 | 42 | 43 | 43 | 43 | 43 | 43 | 43 | 10 |  | 10 | 35 | 34 | 43 | 43 | 43 | 43 | 893698
94 | Gagnagar 102 MW PP (Digital Power) | 7 | 0 | [5 empty] | 0 | 4 | 16 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 40 | 60 | 75 | 75 | 75 | 75 | 7 | 587232
95 | Patenga 50MW PP (Baraka) | 50 | 42 | 25 | 25 | 24 | 20 | 12 | 12 | 12 | 12 | 13 | 25 | 39 | 48 | 50 | 50 | 50 | 48 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 871680
96 | Chattogram 108 MW PP (ECPV) | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 9 | 10 | 9 |  | 32 | 70 | 76 | 52 | 44 | 32 | 32 | 423360
97 | Katpotti 52 MW PP (Sinha) | 11 | 10 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 20 | 30 | 48 | 47 | 0 | 13 | 416592
98 | Bosila 108MW PP(CLC) | 72 | 72 | 72 | 72 | 8 | 8 | 8 | 8 | 8 | 31 | 68 | 67 | 72 | 72 | 72 | 72 | 40 | 40 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1252800
99 | Madanganj-55 MW PP(Summit) | [17 empty] | 0 |  | 12 | 15 | 15 | 15 | 0 | 0 |  | 60029
100 | Manikganj 55 MW PP (Northern) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 |  | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 746881
101 | Kushiara 163 MW CCPP (KP) | 100 | 130 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 163 | 130 | 100 | 100 | 100 | 100 | 130 | 163 | 100 |  | 100 | 100 | 100 | 130 | 130 | 130 | 130 | 3144894
102 | Sarishabari 3 MW Solar Plant |  |  |  |  | 0 | 0.1 | 0.2 | 0.5 | 1.1 | 0.4 | 1 | 2.4 | 2.4 | 0.5 | 2 | 0.4 | 0.2 | 0.1 |  | 0 | [6 empty] | 11700
103 | Kamalaghat 54 MW PP(Banco Energy) | 53 | 53 | 53 | 53 | 53 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 |  | 53 | 30 | 35 | 53 | 53 | 53 | 53 | 883800
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 150 | 100 | 100 | 55 | 55 | 7 | 7 | 7 | 7 | 7 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 31 | 95 | 160 | 140 | 140 | 140 | 1435200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 69 | 0 | [7 empty] | 40 | 103 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 120 | 144 | 112 | 100 | 100 | 77 | 1604160
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 60 | 60 | 60 | 20 | 20 | 20 | 20 | 20 | 20 | 60 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1802880
116 | Chandpur 200MW (Desh energy) | 199 | 160 | 130 | 105 | 60 | 52 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 34 | 125 | 152 | 192 | 199 | 200 | 200 | 1945440
117 | Ashuganj 150MW PP (Midland) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 22 | 50 | 50 | 50 | 50 | 55 | 100 | 568727
118 | Bibiyana-III 400 MW CCPP | 233 | 236 | 233 | 232 | 233 | 233 | 234 | 249 | 269 | 247 | 234 | 232 | 232 | 232 | 249 | 232 | 239 | 233 |  | 260 | 232 | 233 | 232 | 232 | 233 | 232 | 5742000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 78 | 70 | 70 | 70 | 94 | 115 | 115 | 111 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2613600
| Anwara 300 MW PP (United) | 233 | 180 | 142 | 106 | 107 | 94 | 52 | 52 | 52 | 52 | 182 | 194 | 194 | 196 | 196 | 196 | 207 | 196 |  | 199 | 213 | 213 | 213 | 214 | 214 | 214 | 3924218
120 | Eastern Zone Total | 7529 | 7248 | 7107 | 6906 | 6707 | 5977.85 | 5874.98 | 5849.22 | 6119.72 | 6528.52 | 6694.83 | 6712.42 | 6822.14 | 6616.6 | 7063 | 6959.1 | 6743.87 | 6369.37 |  | 7223 | 7752 | 7991 | 8063 | 7955 | 7869 | 7785 | 166605184
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 60 | 115 | 115 | 115 | 115 | 115 | 115 | 887040
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 23 | 23 | 23 | 18 | 12 | 12 | 6 | 0 | [7 empty] | 0 | 3 | 18 |  | 30 | 29 | 27 | 27 | 27 | 27 | 27 | 280320
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 70 | 70 | 70 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 87 | 105 | 105 | 105 | 105 | 105 | 105 | 1172640
130
131
132
133
| Barisal 110 MW PP (Summit ) | 32 | 16 | 0 | [14 empty] | 0 |  | 48 | 64 | 48 | 32 | 32 | 32 | 16 | 252384
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 97 | 95 | 96 | 97 | 97 | 54 | 52 | 52 | 52 | 64 | 82 | 88 | 91 | 91 | 54 | 54 | 23 | 23 |  | 97 | 98 | 96 | 95 | 96 | 96 | 97 | 1832766
| Bhola 225 MW CCPP | 173 | 173 | 173 | 173 | 173 | 173 | 172 | 173 | 173 | 173 | 173 | 173 | 172 | 173 | 172 | 172 | 173 | 173 |  | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 4217788
140 | Bhola 33 MW PP (Venture) | 34 | 33 | 30 | 31 | 30 | 27 | 21 | 20 | 17 | 12 | 13 | 11 | 15 | 15 | 7 | 9 | 16 | 22 |  | 25 | 28 | 31 | 36 | 33 | 36 | 36 | 546890
141 | Noapara 100 MW PP (Bangla Trac) | 50 | 10 | 10 | 10 | 10 | 0 | [11 empty] | 0 |  | 8 | 78 | 87 | 100 | 100 | 100 | 100 | 668160
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 40 | 40 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 499125
143 | Gopalganj 100 MW Peaking PP | 20 | 16 | 12 | 12 | 12 | 12 | 8 | 0 | [5 empty] | 0 | 7 | 40 | 45 | 53 |  | 85 | 80 | 80 | 68 | 65 | 65 | 60 | 584832
144 | Bheramara GTPP Unit-1,2 & 3 | [17 empty] | 0 |  | 10 | 32 | 32 | 32 | 16 | 16 | 16 | 121600
145 | Madhumati 100 MW PP | 85 | 84 | 86 | 87 | 51 | 34 | 34 | 34 | 35 | 34 | 33 | 34 | 36 | 33 | 32 | 33 | 33 | 33 |  | 60 | 68 | 77 | 68 | 79 | 68 | 67 | 1237824
146 | Bheramara HVDC | 934 | 929 | 920 | 920 | 920 | 920 | 920 | 919 | 916 | 910 | 912 | 911 | 914 | 915 | 915 | 915 | 925 | 925 |  | 925 | 924 | 925 | 925 | 925 | 928 | 928 | 22077091
147 | Bheramara 360 MW CCPP
148
149
150 | Barapukuria TPP Unit-1 | 71 | 71 | 71 | 72 | 72 | 71 | 72 | 71 | 70 | 71 | 68 | 68 | 68 | 68 | 68 | 68 | 69 | 69 |  | 68 | 68 | 68 | 70 | 69 | 70 | 70 | 1676072
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 250 | 250 | 250 | 250 | 250 | 251 | 249 | 250 | 250 | 250 | 249 | 250 | 250 | 250 | 249 | 249 | 249 | 250 |  | 249 | 249 | 249 | 232 | 199 | 200 | 200 | 5920800
153 | Baghabari 71 MW GTPP | 55 | 55 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 55 | 55 | 55 | 55 | 60 | 60 | 60 | 60 | 60 |  | 55 | 55 | 60 | 60 | 60 | 60 | 60 | 1400000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 0 |  | 50 | 43 | 43 | 50 | 50 | 50 | 50 | 258672
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 188 | 185 | 183 | 181 | 189 | 178 | 167 | 163 | 190 | 203 | 189 | 182 | 190 | 185 | 183 | 203 | 202 | 184 |  | 190 | 195 | 189 | 184 | 186 | 200 | 197 | 4773382
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 186 | 189 | 187 | 185 | 193 | 182 | 153 | 164 | 178 | 204 | 194 | 187 | 192 | 164 | 171 | 122 | 143 | 145 |  | 145 | 144 | 145 | 146 | 146 | 145 | 147 | 4149309
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 189 | 192 | 190 | 187 | 196 | 187 | 192 | 189 | 208 | 209 | 196 | 190 | 198 | 157 | 174 | 171 | 169 | 158 |  | 175 | 201 | 195 | 191 | 192 | 198 | 190 | 4707936
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 300 | 300 | 300 | 300 | 300 | 270 | 270 | 270 | 300 | 300 | 300 | 270 | 240 | 220 | 250 | 320 | 280 | 250 |  | 300 | 330 | 330 | 390 | 360 | 360 | 320 | 7159273
160 | Sirajgonj 400MW CCPP Unit-4 (Oil) | [26 empty] | 0
161 | Bera 70 MW Peaking PP | 21 | 0 | [24 empty] | 32956
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 22 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 512400
163 | Bogura 20 MW PP (Energyprima) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 13 | 13 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 16 | 16 | 16 | 16 | 372240
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 198090
165 | Amnura 50 MW PP(Sinha) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 18 | 18 | 12 | 12 | 12 | 12 | 12 | 12 |  | 33 | 33 | 33 | 33 | 33 | 12 | 12 | 131680
166 | Katakhali 50 MW PP (Northern) | 42 | 42 | 42 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 694853
167 | Katakhali 50 MW Peaking PP | 45 | 45 | 0 | [14 empty] | 0 |  | 28 | 46 | 47 | 45 | 45 | 45 | 0 | 330322
168 | Santahar 50 MW Peaking PP | 36 | 36 | 36 | 17 | 0 | [12 empty] | 0 |  | 21 | 38 | 37 | 37 | 37 | 37 | 35 | 322914
169 | Natore 52 MW PP (Rajlanka) | 52 | 25 | 17 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 16 | 42 | 43 | 52 | 52 | 52 | 53 | 506400
170 | Chapainawabganj 100 MW Peaking PP | 93 | 93 | 93 | 93 | 40 | 24 | 24 | 24 | 24 | 21 | 0 | [6 empty] | 0 |  | 60 | 95 | 95 | 95 | 95 | 95 | 95 | 1016744
171 | Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence) | 80 | 90 | 108 | 109 | 110 | 110 | 111 | 55 | 56 | 56 | 100 | 112 | 112 | 112 | 113 | 113 | 55 | 55 |  | 70 | 113 | 113 | 93 | 93 | 92 | 113 | 2284512
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | [5 empty] | 0 | 18 | 18 | 17 | 0 | [7 empty] | 0 |  | 17 | 15 | 15 | 15 | 15 | 15 | 15 | 153000
176 | Rangpur 113 MW PP (Confidence) | [8 empty] | 0 | 12 | 27 | 27 | 21 | 0 | 8 | 27 | 13 | 0 | [8 empty] | 149760
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1.2 | 1 | 1 | 5.9 | 3 | 5.9 | 7 | 5.4 | 4.2 | 3.2 | 1.5 | 0.3 |  | 0 | [6 empty] | 39700
178
178