## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2018-06-26 | Tuesday
|  | Date (day): | 2018-06-26 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10868 | MW |  |  | (b) At Evening Peak Hour : |  | 12231 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2018-06-25 | 2018-06-26 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | # 1& 2 under maint
| Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 120 | 120 | 120 | 120 |  | 50 | Gas shortage
| Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Under maint.
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 365 | 365 | 365 | 365
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 73 | 74 | 78 | 78
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 99 | 87 | 100 | 108
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Under shut down.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 350 | 370 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 40 | 84 | 84 |  | 26 | Engine problem
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 231 | 180 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 340 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 100 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 100 | 100 | 150 | 305
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 0 | 0 |  |  | Cable Fault.
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 60 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 19 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 162 | 97 | 209 | 209
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 17 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 93 | 90 | 93 |  | 7 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 194 | 150 | 200 | 200
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 11 | 50 | 50 | 50
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 20 | 58 | 102 | 102
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 39 | 37 | 42 | 42 |  |  | Engine problem
24 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 36 | 54 | 54 | 54
25 | Kodda 150MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 98 | 149 | 149 | 149
26 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 36 | 56 | 55 | 55
27 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 36 | 55 | 55 | 55
28 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 89 | 91 | 100 | 100
29 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 55 | 57 | 58 | 58 |  | 22 | Engine problem
30 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
31 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 31 | 33 | 33
32 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 50 | 50 | 42 | 50
33 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
34 | Summit Gazipur |  | HFO | IPP | 18*17.076 | 300 | 300 | 43 | 286 | 100 | 300
| APR Energy , Keranigonj |  | HSD | IPP | 236*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 103 | 105 | 106 | 105
| Dhaka area Total |  |  |  |  | 5435 | 5199 | 2809 | 3379 | 3974 | 4347 | 345 | 475
35 | Chittagong ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
36 | Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas Shortage
36 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
37 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 38 | 44 | 44 | 44
38 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 168 | 168 | 172 | 172 |  | 58 | # 2 under maint
39 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
40 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 220 | 209 | 225 | 225
41 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 50 | 135 | 60 | 135
42 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 51 | 51 | 51 | 51
43 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 66 | 85 | 85
44 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 85 | 85
45 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 68 | 80 | 80 | 80 |  | 20 | Engine problem
46 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 16 | 16 | 16 |  | 6
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 31 | 15 | 31
47 | Chittagong ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 57 | 99 | 98 | 98 |  | 10 | Engine problem
| Chittagong area Total |  |  |  |  | 1641 | 1561 | 696 | 924 | 956 | 1047 | 360 | 134
48 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Under maint.
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 150 | 120 | 150 | 150 |  | 129
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 130 | 100 | 100 | 100 | 34 |  | Gas shortage
49 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 184 | 200 | 225 | 225 |  |  | FGMO
50 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 185 | 222 | 285 | 360 |  |  | FGMO
51 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 301 | 327 | 360 | 360 |  |  | FGMO
52 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 36 | 33 | 42 | 42
53 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  | 55 | Under maint.
54 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 10 | 10 | 10 | 43 |  | Gas shortage
55 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 78 | 78 | 87 | 100 | 95 |  | Gas shortage
56 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 42 | 51 | 51
57 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 85 | 86 | 85 | 85
58 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 47 | 0 | 50
59 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint.
60 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
61 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 5 | 10
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 108 | 158 | 130 | 165
62 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
63 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 52 | 52
64 | Summit Comilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 0 | 22 | 22
65 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Comilla Area Total |  |  |  |  | 2601 | 2541 | 1394 | 1494 | 1656 | 2034 | 307 | 347
66 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 98 | 66 | 100 | 100 | 102 |  | Gas shortage
67 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
68 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 24 | 72 | 95 | 95
69 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 1.5 | 0 | 2 | 0
| United Mymensingh PPL |  | HFO | IPP | 200 | 0 | 0 | 100 | 180 | 54 | 180
| Mymensingh Area Total |  |  |  |  | 330 | 322 | 243.5 | 338 | 273 | 397 | 102 | 0
70 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 54 | 60 | 60
71 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 60 | 60 | 60
72 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 130 | 163 | 163
73 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 314 | 321 | 330 | 330
74 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 48 | 53 | 51 | 51
75 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 50 | 50
76 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8
77 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 30 | 29 | 30 | 30 |  |  | # 8 under maint.
78 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 86 | 86 | 86
79 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 46 | 47 | 50 | 50
80 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 80 | 78 | 80 | 100
81 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  |  | Under maint.
82 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 42 | 42 | 44 | 44
83 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 15 | 23 | 23 | 23
84 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 |  |  | FGMO
85 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 7 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1284 | 1301 | 1386 | 1406 | 0 | 0
86 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 48
| Bheramara (HVDC ) |  | 0 | Imported power | 1*500 | 500 | 500 | 478 | 478 | 488 | 488
87 | Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 110 | 110 | 10 | 106 | 110 | 110
88 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 99 | 99 | 115
89 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 43 | 36 | 43
90 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 120 | 225 | 225 |  |  | FGMO
91 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 8 | 72 | 50 | 83
92 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 150 | 150 | 100 |  | 360
93 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 40 | 40 | 40
94 | Khulna (Aggreko) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 55 | 0 | 53 | 0 | 53
95 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 40 | 0 | 100
| Khulna Area Total |  |  |  |  | 1783 | 1769 | 640 | 1201 | 1198 | 1405 | 0 | 360
96 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 80 | 110 | 110
97 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
98 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 16 | 31 | 30 | 30
99 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 194 | 192 | 194 | 194
100 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 54 | 97 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 280 | 400 | 429 | 459 | 0 | 0
101 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Under maint.
102 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 0 | 43
103 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 38 | 0 | 31
104 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 35 | 40 | 42 | 42 |  | 8 | Engine problem
105 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 35 | 43 | 43 | 43 |  | 7 | Engine problem
106 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 46 | 45 | 45
107 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 193 | 182 | 215 | 215
108 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 179 | 180 | 220 | 220
| Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Under maint.
109 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 43 | 0 | 43
110 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
111 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 10 | 12 | 11 | 12
112 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 8 | 11
113 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 43 | 43 | 43 |  | 9 | Engine problem
114 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 25 | 101 | 100 | 102
| Rajshahi Area Total |  |  |  |  | 1133 | 1123 | 512 | 804 | 749 | 872 | 71 | 24
115 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 64 | 59 | 69 | 69
116 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 159 | 160 | 160 | 160
117 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 16 | 0 | 17
118 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 18 | 18 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 223 | 253 | 247 | 264 | 0 | 85
| Total |  |  |  |  | 15553 | 15010 | 8081.5 | 10094 | 10868 | 12231 | 1185 | 1425
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7802.0822 | 9745 | 10492.239 | 11808.1132
A. |  | 2018-06-25 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 10094 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 6831.3 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10094 | MW
3 | Day peak Generation : |  |  | 8081.5 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9745 | MW
4 | Evening peak Generation : |  |  | 10094 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 200.3064 | MKWHr | By Solar | 0.008928 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 123.1218 | MKWHr |  | By Oil: | 53.0209 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 5.5216 | MKWHr |  | By Hydro: | 3.9856 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1185 | MW | Dhaka | 3474 | 3474 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1425 | MW | Chittagong | 955 | 955 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2610 | MW | Khulna | 1330 | 1330 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1045.18 | MMCFD |  |  | Rajshahi | 1073 | 1073 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 90347246.008 | ii) Oil : | Taka | 419657681.64 | Comilla | 884 | 884 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 9869152.3 | Total | Taka | 519874079.948 | Mymensingh | 735 | 735 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 7.325 | MKWHr. | Sylhet | 426 | 426 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -660 | MW at | 21:00 | hrs | Barisal | 238 | 238 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -660 | MW at | 2:00 | hrs | Rangpur | 630 | 630 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 31.2° C |  |  | Total | 9745 | 9745 |  | 0
B. |  | 2018-06-26 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 35.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12231 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8400 | MW
4 | Reserve(Generation end) |  |  |  | 1631 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 210.3475 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6501.1 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.5775 | MKWHr. | ii) HVDC Flow at Peak Time |  | 478 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.0701 | MKWHr. | iii) Maximum HVDC Flow : |  | 478 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 101.82 |  | (b) Today: | 102.2 |  | (c) Rule Curve: |  | 82.65
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2018-06-25
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal ST: Unit-3 | Ghorasal ST: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 150MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chittagong ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chittagong ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Comilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreko) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 36 | 120 | 0 | 0 | 280 | 111 | 74 | 345 | 354 | 0 | 0 | 400 | 100 | 24 | 50 | 30 | 192 | 0 | 130 | 0 | 7 | 7 | 100 | 10 | 91 | 0 | 40 | 54 | 55 | 17 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 85 | 80 | 0 | 0 | 25 | 0 | 202 | 0 | 50 | 0 | 51 | 55 | 79 | 80 | 99 | 44 | 16 | 42 | 70 | 70 | 100 | 162 | 301 | 155 | 78 | 0 | 39 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 20 | 142 | 129 | 8 | 20 | 0 | 60 | 60 | 50 | 50 | 130 | 146 | 31 | 86 | 46 | 80 | 0 | 44 | 10 | 300 | 21 | 8 | 0 | 200 | 0 | 0 | 130 | 102 |  | 478 | 0 | 274 | 27 | 107 | 120 | 0 | 0 | 48 | 32 | 40 | 192 | 24 | 64 | 0 | 0 | 0 | 0 | 37 | 100 | 40 | 43 | 0 | 43 | 42 | 22 | 11 | 5 | 0 | 70 | 160 | 0 | 18 | 183 | 0 | 0 | 174 | 97 | 0 | 0 | 0 |  | 6783 | 2451 | 9234 | 3453 | 478 | 2070 | 1639 | 230 | 165 | 1057 | 142 | 0 | 0 | 101.62
2:00 | 36 | 120 | 0 | 0 | 280 | 111 | 74 | 345 | 321 | 0 | 0 | 400 | 100 | 7 | 15 | 15 | 192 | 0 | 132 | 0 | 7 | 7 | 64 | 10 | 91 | 0 | 39 | 54 | 55 | 17 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 85 | 80 | 0 | 0 | 8 | 0 | 200 | 0 | 50 | 0 | 51 | 55 | 47 | 80 | 99 | 44 | 16 | 42 | 0 | 95 | 100 | 162 | 301 | 183 | 78 | 0 | 39 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 20 | 136 | 129 | 8 | 20 | 0 | 60 | 60 | 50 | 50 | 130 | 162 | 31 | 86 | 46 | 80 | 0 | 44 | 9 | 295 | 15 | 8 | 0 | 200 | 0 | 0 | 100 | 102 |  | 478 | 0 | 274 | 10 | 36 | 120 | 0 | 0 | 21 | 32 | 40 | 191 | 13 | 48 | 0 | 0 | 0 | 0 | 37 | 100 | 35 | 43 | 0 | 43 | 0 | 22 | 11 | 5 | 0 | 71 | 160 | 0 | 18 | 181 | 0 | 0 | 173 | 98 | 0 | 0 | 0 |  | 6548 | 2260 | 8808 | 3445 | 478 | 2021 | 1415 | 231 | 165 | 917 | 136 | 0 | 0 | 101.66
3:00 | 36 | 120 | 0 | 0 | 280 | 111 | 74 | 345 | 311 | 0 | 0 | 400 | 100 | 7 | 15 | 15 | 192 | 0 | 130 | 0 | 7 | 7 | 64 | 10 | 42 | 0 | 39 | 18 | 18 | 17 | 22 | 25 | 32 | 33 | 33 | 35 | 0 | 85 | 80 | 0 | 0 | 8 | 0 | 201 | 0 | 50 | 0 | 51 | 24 | 16 | 68 | 83 | 44 | 16 | 42 | 0 | 100 | 100 | 162 | 301 | 184 | 78 | 0 | 39 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 8 | 20 | 130 | 128 | 8 | 20 | 0 | 60 | 60 | 50 | 50 | 130 | 283 | 31 | 86 | 46 | 80 | 0 | 44 | 10 | 280 | 15 | 8 | 0 | 100 | 0 | 0 | 93 | 101 |  | 478 | 0 | 274 | 10 | 24 | 120 | 0 | 0 | 18 | 31 | 8 | 191 | 20 | 16 | 0 | 0 | 0 | 0 | 37 | 100 | 40 | 43 | 0 | 8 | 0 | 22 | 11 | 5 | 0 | 70 | 160 | 0 | 0 | 183 | 0 | 0 | 175 | 98 | 0 | 0 | 0 |  | 6282 | 2142 | 8424 | 3546 | 478 | 2004 | 1035 | 230 | 165 | 836 | 130 | 0 | 0 | 101.7
4:00 | 36 | 120 | 0 | 0 | 280 | 111 | 73 | 345 | 301 | 0 | 0 | 400 | 100 | 7 | 15 | 15 | 191 | 0 | 130 | 0 | 7 | 7 | 64 | 10 | 8 | 0 | 6 | 18 | 18 | 17 | 22 | 25 | 32 | 33 | 33 | 35 | 0 | 87 | 80 | 0 | 0 | 8 | 0 | 204 | 0 | 50 | 0 | 51 | 0 | 16 | 68 | 53 | 44 | 16 | 42 | 0 | 100 | 100 | 162 | 301 | 183 | 78 | 0 | 39 | 0 | 5 | 51 | 50 | 0 | 0 | 19 | 8 | 8 | 20 | 122 | 129 | 8 | 20 | 0 | 60 | 60 | 50 | 50 | 130 | 302 | 31 | 50 | 46 | 80 | 0 | 44 | 10 | 286 | 15 | 8 | 0 | 50 | 0 | 0 | 72 | 101 |  | 478 | 0 | 274 | 10 | 16 | 120 | 0 | 0 | 18 | 25 | 8 | 190 | 19 | 16 | 0 | 0 | 0 | 0 | 37 | 68 | 40 | 43 | 0 | 8 | 0 | 22 | 11 | 5 | 0 | 70 | 160 | 0 | 0 | 182 | 0 | 0 | 173 | 98 | 0 | 0 | 0 |  | 6026 | 2091 | 8117 | 3559 | 478 | 1927 | 859 | 230 | 167 | 775 | 122 | 0 | 0 | 101.74
5:00 | 36 | 120 | 0 | 0 | 280 | 111 | 60 | 340 | 301 | 0 | 0 | 400 | 100 | 7 | 15 | 15 | 188 | 0 | 130 | 0 | 7 | 7 | 60 | 10 | 8 | 0 | 6 | 18 | 18 | 17 | 22 | 25 | 30 | 33 | 33 | 34 | 0 | 87 | 80 | 0 | 0 | 8 | 0 | 201 | 0 | 50 | 0 | 24 | 0 | 16 | 80 | 25 | 44 | 16 | 42 | 0 | 100 | 100 | 162 | 301 | 183 | 78 | 0 | 39 | 0 | 5 | 6 | 10 | 0 | 0 | 19 | 8 | 8 | 20 | 110 | 129 | 8 | 20 | 0 | 60 | 60 | 50 | 50 | 100 | 302 | 31 | 10 | 45 | 80 | 0 | 44 | 10 | 285 | 17 | 8 | 0 | 17 | 0 | 0 | 50 | 103 |  | 478 | 0 | 278 | 10 | 24 | 120 | 0 | 0 | 0 | 8 | 8 | 187 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 68 | 40 | 43 | 0 | 8 | 0 | 22 | 11 | 5 | 0 | 71 | 160 | 0 | 0 | 178 | 0 | 0 | 170 | 95 | 0 | 0 | 0 |  | 5732 | 2019 | 7751 | 3548 | 478 | 1754 | 770 | 231 | 167 | 693 | 110 | 0 | 0 | 101.78
6:00 | 36 | 120 | 0 | 0 | 200 | 25 | 40 | 340 | 262 | 0 | 0 | 340 | 100 | 7 | 0 | 15 | 156 | 0 | 80 | 0 | 7 | 7 | 16 | 10 | 8 | 0 | 6 | 0 | 18 | 17 | 22 | 25 | 30 | 33 | 33 | 34 | 0 | 87 | 80 | 0 | 0 | 8 | 0 | 199 | 0 | 50 | 0 | 24 | 0 | 16 | 80 | 25 | 44 | 16 | 42 | 0 | 100 | 100 | 162 | 312 | 190 | 78 | 0 | 39 | 0 | 5 | 6 | 10 | 0 | 0 | 19 | 8 | 8 | 20 | 100 | 129 | 8 | 17 | 0 | 60 | 60 | 5 | 5 | 100 | 319 | 30 | 10 | 5 | 80 | 0 | 7 | 10 | 260 | 21 | 8 | 0 | 15 | 0 | 0 | 7 | 102 |  | 478 | 0 | 215 | 10 | 16 | 120 | 0 | 0 | 0 | 8 | 8 | 191 | 14 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 43 | 0 | 8 | 0 | 14 | 11 | 5 | 0 | 71 | 160 | 0 | 0 | 175 | 0 | 0 | 168 | 54 | 0 | 0 | 0 |  | 5073 | 1822 | 6895 | 3359 | 478 | 1303 | 655 | 231 | 167 | 602 | 100 | 0 | 0 | 101.82
7:00 | 36 | 120 | 0 | 0 | 200 | 25 | 30 | 355 | 266 | 0 | 0 | 340 | 100 | 7 | 0 | 15 | 120 | 0 | 80 | 0 | 7 | 7 | 16 | 10 | 8 | 0 | 6 | 0 | 18 | 17 | 22 | 25 | 30 | 33 | 33 | 34 | 0 | 87 | 80 | 0 | 0 | 8 | 0 | 216 | 0 | 50 | 0 | 24 | 0 | 0 | 80 | 25 | 20 | 16 | 38 | 0 | 100 | 100 | 162 | 334 | 205 | 78 | 0 | 39 | 0 | 5 | 6 | 10 | 0 | 0 | 19 | 8 | 8 | 12 | 96 | 120 | 8 | 17 | 0.3 | 60 | 60 | 5 | 5 | 100 | 322 | 30 | 10 | 5 | 80 | 0 | 8 | 10 | 315 | 22 | 8 | 0 | 15 | 0 | 0 | 7 | 103 |  | 478 | 0 | 140 | 10 | 16 | 120 | 0 | 0 | 0 | 8 | 8 | 193 | 12 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 43 | 0 | 8 | 0 | 18 | 11 | 5 | 0 | 67 | 160 | 0 | 0 | 190 | 0 | 0 | 182 | 13 | 0 | 0 | 0 |  | 5096.3 | 1735 | 6831.3 | 3304 | 478 | 1310 | 632 | 227 | 167 | 617 | 96 | 0.3 | 0 | 101.85
8:00 | 0 | 120 | 0 | 0 | 200 | 25 | 30 | 375 | 300 | 0 | 0 | 370 | 100 | 7 | 0 | 15 | 120 | 0 | 125 | 0 | 7 | 7 | 16 | 10 | 8 | 0 | 6 | 0 | 18 | 17 | 22 | 25 | 30 | 33 | 33 | 34 | 0 | 87 | 80 | 0 | 0 | 8 | 0 | 186 | 0 | 30 | 0 | 0 | 0 | 0 | 80 | 12 | 18 | 16 | 17 | 0 | 100 | 100 | 162 | 334 | 205 | 78 | 0 | 39 | 0 | 5 | 6 | 10 | 0 | 0 | 19 | 0 | 8 | 12 | 102 | 98 | 8 | 17 | 0.3 | 60 | 60 | 5 | 5 | 100 | 332 | 30 | 10 | 5 | 80 | 0 | 7 | 10 | 320 | 22 | 8 | 0 | 15 | 0 | 0 | 7 | 104 |  | 478 | 0 | 290 | 10 | 16 | 120 | 0 | 0 | 0 | 8 | 8 | 193 | 11 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 43 | 0 | 8 | 0 | 22 | 11 | 5 | 0 | 63 | 158 | 0 | 0 | 197 | 0 | 0 | 189 | 13 | 0 | 0 | 0 |  | 5070.3 | 1896 | 6966.3 | 3470 | 478 | 1360 | 594 | 221 | 167 | 574 | 102 | 0.3 | 0 | 101.87
9:00 | 0 | 120 | 0 | 0 | 345 | 25 | 30 | 375 | 302 | 0 | 0 | 400 | 100 | 7 | 0 | 15 | 120 | 0 | 197 | 0 | 7 | 7 | 98 | 10 | 51 | 0 | 17 | 0 | 18 | 36 | 22 | 25 | 30 | 33 | 33 | 44 | 0 | 87 | 80 | 0 | 0 | 25 | 0 | 205 | 0 | 30 | 0 | 0 | 0 | 0 | 80 | 13 | 22 | 16 | 7 | 0 | 100 | 100 | 160 | 334 | 218 | 78 | 0 | 36 | 0 | 5 | 10 | 50 | 0 | 0 | 19 | 11 | 15 | 9 | 110 | 98 | 8 | 17 | 0.7 | 89 | 60 | 31 | 25 | 163 | 334 | 30 | 50 | 45 | 79 | 0 | 43 | 9 | 320 | 22 | 8 | 0 | 15 | 0 | 0 | 7 | 103 |  | 478 | 0 | 120 | 10 | 16 | 120 | 0 | 0 | 0 | 8 | 8 | 193 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 43 | 0 | 8 | 0 | 22 | 11 | 5 | 0 | 63 | 158 | 0 | 0 | 196 | 0 | 0 | 188 | 14 | 0 | 0 | 0 |  | 5843.7 | 1725 | 7568.7 | 3569 | 478 | 1652 | 697 | 221 | 167 | 674 | 110 | 0.7 | 0 | 101.89
10:00 | 0 | 120 | 0 | 0 | 365 | 22 | 30 | 375 | 260 | 0 | 0 | 400 | 100 | 7 | 0 | 15 | 120 | 0 | 191 | 0 | 7 | 7 | 98 | 10 | 51 | 10 | 39 | 18 | 18 | 17 | 22 | 25 | 28 | 33 | 33 | 51 | 0 | 88 | 80 | 0 | 0 | 25 | 0 | 195 | 0 | 30 | 0 | 17 | 0 | 0 | 80 | 58 | 37 | 16 | 5 | 0 | 100 | 100 | 200 | 320 | 198 | 78 | 0 | 39 | 0 | 5 | 30 | 86 | 0 | 0 | 19 | 11 | 33 | 10 | 116 | 98 | 24 | 17 | 1 | 59 | 60 | 45 | 47 | 163 | 314 | 30 | 84 | 45 | 79 | 0 | 42 | 7 | 320 | 15 | 8 | 0 | 15 | 0 | 0 | 50 | 95 |  | 477 | 0 | 120 | 10 | 16 | 120 | 0 | 0 | 0 | 8 | 8 | 195 | 14 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 43 | 0 | 8 | 0 | 22 | 10 | 5 | 0 | 67 | 159 | 0 | 0 | 196 | 0 | 0 | 187 | 52 | 0 | 0 | 0 |  | 6066 | 1783 | 7849 | 3554 | 477 | 1767 | 877 | 226 | 168 | 663 | 116 | 1 | 0 | 101.91
11:00 | 0 | 120 | 0 | 0 | 365 | 45 | 40 | 360 | 231 | 0 | 0 | 400 | 100 | 7 | 0 | 15 | 160 | 0 | 192 | 0 | 7 | 7 | 98 | 10 | 50 | 11 | 39 | 18 | 36 | 36 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 88 | 80 | 0 | 0 | 25 | 0 | 202 | 0 | 31 | 0 | 51 | 0 | 0 | 68 | 53 | 38 | 16 | 5 | 0 | 150 | 130 | 203 | 323 | 200 | 78 | 0 | 39 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 10 | 116 | 98 | 24 | 20 | 1.2 | 60 | 60 | 48 | 50 | 163 | 307 | 30 | 84 | 44 | 78 | 0 | 42 | 7 | 320 | 15 | 8 | 0 | 15 | 0 | 0 | 50 | 102 |  | 478 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 8 | 8 | 195 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 35 | 0 | 8 | 0 | 22 | 10 | 0 | 0 | 62 | 158 | 0 | 0 | 190 | 0 | 0 | 183 | 54 | 0 | 0 | 0 |  | 6276.2 | 1639 | 7915.2 | 3535 | 478 | 1800 | 930 | 220 | 168 | 667 | 116 | 1.2 | 0 | 101.93
12:00 | 0 | 120 | 0 | 0 | 365 | 99 | 73 | 350 | 231 | 0 | 0 | 380 | 100 | 7 | 0 | 15 | 194 | 0 | 162 | 0 | 7 | 20 | 98 | 10 | 89 | 11 | 39 | 36 | 36 | 36 | 22 | 25 | 30 | 33 | 25 | 50 | 0 | 88 | 80 | 0 | 0 | 25 | 0 | 220 | 0 | 50 | 0 | 51 | 0 | 0 | 68 | 57 | 38 | 16 | 3 | 0 | 150 | 130 | 185 | 301 | 184 | 78 | 0 | 36 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 18 | 108 | 98 | 24 | 20 | 1.5 | 60 | 60 | 48 | 50 | 130 | 314 | 30 | 84 | 46 | 80 | 0 | 42 | 7 | 310 | 15 | 8 | 0 | 43 | 0 | 0 | 100 | 103 |  | 478 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 8 | 8 | 194 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 35 | 35 | 0 | 8 | 0 | 22 | 10 | 5 | 0 | 64 | 159 | 0 | 0 | 193 | 0 | 0 | 179 | 54 | 0 | 0 | 0 |  | 6426.5 | 1655 | 8081.5 | 3486 | 478 | 1824 | 1093 | 223 | 168 | 700 | 108 | 1.5 | 0 | 101.95
13:00 | 0 | 120 | 0 | 0 | 365 | 98 | 71 | 375 | 231 | 0 | 0 | 360 | 100 | 34 | 0 | 15 | 194 | 0 | 101 | 7 | 20 | 32 | 98 | 50 | 89 | 10 | 39 | 36 | 36 | 36 | 22 | 25 | 31 | 33 | 25 | 50 | 0 | 88 | 80 | 0 | 0 | 25 | 0 | 188 | 0 | 50 | 0 | 51 | 0 | 0 | 68 | 62 | 45 | 14 | 11 | 0 | 150 | 130 | 15 | 300 | 186 | 185 | 0 | 36 | 0 | 53 | 51 | 86 | 0 | 0 | 19 | 11 | 33 | 18 | 114 | 82 | 24 | 20 | 2 | 60 | 60 | 47 | 50 | 163 | 307 | 31 | 86 | 45 | 78 | 0 | 42 | 5 | 320 | 15 | 8 | 0 | 49 | 0 | 0 | 100 | 103 |  | 477 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 8 | 8 | 194 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 35 | 0 | 8 | 0 | 22 | 9 | 5 | 0 | 66 | 159 | 0 | 0 | 198 | 0 | 0 | 186 | 94 | 0 | 0 | 0 |  | 6469 | 1712 | 8181 | 3261 | 477 | 2045 | 1214 | 225 | 168 | 675 | 114 | 2 | 0 | 101.97
14:00 | 0 | 120 | 0 | 0 | 300 | 101 | 71 | 330 | 231 | 0 | 0 | 300 | 100 | 55 | 0 | 15 | 190 | 0 | 60 | 0 | 50 | 8 | 90 | 10 | 90 | 10 | 39 | 36 | 37 | 36 | 22 | 25 | 31 | 33 | 22 | 50 | 0 | 88 | 80 | 0 | 0 | 25 | 0 | 188 | 0 | 50 | 0 | 51 | 0 | 0 | 80 | 65 | 44 | 13 | 5 | 0 | 150 | 130 | 14 | 316 | 193 | 195 | 0 | 36 | 0 | 53 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 18 | 118 | 65 | 8 | 20 | 1 | 60 | 60 | 50 | 50 | 163 | 334 | 30 | 86 | 45 | 80 | 0 | 44 | 9 | 280 | 15 | 8 | 0 | 49 | 0 | 0 | 100 | 103 |  | 477 | 0 | 140 | 10 | 16 | 120 | 0 | 0 | 0 | 15 | 8 | 193 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 35 | 0 | 8 | 0 | 22 | 9 | 5 | 0 | 67 | 159 | 0 | 0 | 183 | 0 | 0 | 175 | 95 | 0 | 0 | 0 |  | 6233 | 1834 | 8067 | 3259 | 477 | 1961 | 1194 | 226 | 168 | 663 | 118 | 1 | 0 | 101.99
15:00 | 0 | 120 | 0 | 0 | 300 | 102 | 72 | 355 | 227 | 0 | 0 | 340 | 100 | 55 | 0 | 15 | 190 | 0 | 97 | 0 | 50 | 16 | 82 | 10 | 91 | 10 | 39 | 36 | 37 | 36 | 0 | 25 | 28 | 33 | 22 | 50 | 0 | 88 | 80 | 0 | 0 | 25 | 0 | 210 | 0 | 135 | 0 | 51 | 0 | 0 | 80 | 90 | 44 | 13 | 3 | 0 | 150 | 130 | 20 | 327 | 178 | 195 | 0 | 36 | 0 | 10 | 51 | 86 | 0 | 0 | 19 | 11 | 33 | 18 | 122 | 64 | 8 | 20 | 0.3 | 54 | 60 | 50 | 50 | 130 | 322 | 30 | 86 | 46 | 78 | 0 | 44 | 9 | 320 | 15 | 8 | 0 | 49 | 0 | 0 | 150 | 103 |  | 478 | 0 | 140 | 10 | 16 | 120 | 0 | 0 | 0 | 22 | 8 | 193 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 35 | 0 | 8 | 0 | 22 | 9 | 5 | 0 | 69 | 160 | 0 | 0 | 196 | 0 | 0 | 188 | 95 | 0 | 0 | 0 |  | 6439.3 | 1872 | 8311.3 | 3290 | 478 | 1964 | 1278 | 229 | 168 | 782 | 122 | 0.3 | 0 | 102.01
16:00 | 0 | 120 | 0 | 0 | 300 | 103 | 60 | 360 | 222 | 0 | 0 | 340 | 100 | 55 | 0 | 25 | 190 | 0 | 97 | 0 | 50 | 16 | 82 | 10 | 91 | 11 | 39 | 54 | 56 | 55 | 0 | 25 | 28 | 33 | 22 | 50 | 0 | 88 | 80 | 0 | 0 | 25 | 0 | 202 | 0 | 60 | 0 | 51 | 0 | 0 | 80 | 99 | 44 | 13 | 2 | 0 | 150 | 130 | 20 | 272 | 184 | 78 | 0 | 36 | 0 | 10 | 41 | 86 | 0 | 0 | 19 | 11 | 33 | 18 | 120 | 64 | 8 | 20 | 0.2 | 52 | 60 | 53 | 50 | 130 | 303 | 30 | 84 | 46 | 78 | 0 | 44 | 10 | 280 | 20 | 8 | 0 | 98 | 0 | 0 | 150 | 104 |  | 478 | 0 | 125 | 10 | 32 | 120 | 0 | 0 | 0 | 25 | 33 | 183 | 17 | 32 | 0 | 0 | 0 | 0 | 0 | 51 | 40 | 35 | 0 | 8 | 0 | 22 | 9 | 5 | 0 | 69 | 160 | 0 | 0 | 182 | 0 | 0 | 174 | 70 | 0 | 0 | 0 |  | 6238.2 | 1880 | 8118.2 | 3191 | 478 | 1757 | 1461 | 229 | 168 | 714 | 120 | 0.2 | 0 | 102.03
17:00 | 0 | 120 | 0 | 0 | 250 | 101 | 40 | 349 | 211 | 0 | 0 | 340 | 100 | 55 | 0 | 30 | 190 | 0 | 60 | 0 | 50 | 16 | 82 | 10 | 91 | 10 | 39 | 54 | 56 | 55 | 0 | 25 | 28 | 33 | 22 | 50 | 0 | 88 | 80 | 0 | 0 | 25 | 0 | 201 | 0 | 50 | 0 | 51 | 0 | 0 | 68 | 99 | 44 | 16 | 6 | 0 | 120 | 100 | 100 | 250 | 183 | 78 | 0 | 33 | 0 | 10 | 42 | 50 | 0 | 0 | 19 | 11 | 33 | 18 | 118 | 64 | 8 | 20 | 0.1 | 56 | 60 | 53 | 50 | 130 | 304 | 29 | 86 | 20 | 78 | 0 | 44 | 10 | 280 | 20 | 8 | 0 | 98 | 0 | 0 | 150 | 104 |  | 478 | 0 | 120 | 10 | 32 | 120 | 0 | 0 | 0 | 25 | 8 | 173 | 17 | 32 | 0 | 0 | 0 | 0 | 0 | 51 | 40 | 35 | 0 | 8 | 0 | 22 | 9 | 8 | 0 | 68 | 160 | 0 | 0 | 169 | 0 | 0 | 168 | 35 | 0 | 0 | 0 |  | 6032.1 | 1788 | 7820.1 | 3069 | 478 | 1634 | 1428 | 228 | 168 | 697 | 118 | 0.1 | 0 | 102.05
18:00 | 0 | 120 | 0 | 0 | 250 | 101 | 40 | 356 | 206 | 13 | 0 | 340 | 100 | 55 | 0 | 30 | 110 | 0 | 60 | 0 | 50 | 16 | 82 | 10 | 91 | 10 | 39 | 54 | 56 | 55 | 19 | 25 | 10 | 33 | 22 | 44 | 0 | 88 | 80 | 0 | 0 | 25 | 0 | 201 | 0 | 50 | 0 | 51 | 0 | 0 | 68 | 99 | 44 | 16 | 11 | 0 | 120 | 100 | 100 | 250 | 183 | 78 | 0 | 33 | 0 | 10 | 42 | 50 | 0 | 0 | 19 | 11 | 33 | 17 | 122 | 64 | 8 | 20 | 0.1 | 52 | 60 | 53 | 50 | 130 | 303 | 31 | 86 | 20 | 78 | 0 | 44 | 10 | 290 | 23 | 8 | 0 | 98 | 0 | 0 | 151 | 105 |  | 478 | 0 | 110 | 10 | 32 | 120 | 0 | 0 | 18 | 35 | 8 | 171 | 18 | 32 | 0 | 0 | 0 | 0 | 9 | 51 | 40 | 35 | 0 | 8 | 0 | 22 | 9 | 8 | 0 | 68 | 160 | 0 | 0 | 169 | 0 | 0 | 168 | 35 | 0 | 0 | 0 |  | 5982.1 | 1814 | 7796.1 | 2984 | 478 | 1645 | 1437 | 228 | 168 | 734 | 122 | 0.1 | 0 | 102.07
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 120 | 0 | 0 | 300 | 102 | 60 | 372 | 206 | 13 | 0 | 340 | 100 | 61 | 0 | 30 | 110 | 0 | 98 | 0 | 55 | 16 | 90 | 40 | 91 | 10 | 39 | 54 | 56 | 55 | 19 | 25 | 26 | 33 | 22 | 42 | 0 | 88 | 80 | 0 | 0 | 25 | 0 | 215 | 0 | 135 | 0 | 51 | 63 | 0 | 68 | 99 | 44 | 16 | 19 | 0 | 120 | 100 | 160 | 287 | 206 | 78 | 0 | 33 | 0 | 10 | 42 | 86 | 23 | 4 | 19 | 11 | 33 | 17 | 146 | 64 | 15 | 20 | 0 | 52 | 60 | 53 | 50 | 130 | 338 | 30 | 86 | 20 | 78 | 0 | 44 | 10 | 300 | 23 | 8 | 0 | 178 | 0 | 0 | 180 | 106 |  | 478 | 0 | 110 | 103 | 99 | 135 | 0 | 11 | 44 | 45 | 40 | 191 | 25 | 48 | 0 | 0 | 0 | 43 | 37 | 51 | 40 | 43 | 36 | 8 | 30 | 22 | 9 | 8 | 0 | 67 | 160 | 17 | 17 | 181 | 0 | 0 | 180 | 92 | 19 | 0 | 0 |  | 6708 | 2389 | 9097 | 3290 | 478 | 1784 | 1843 | 227 | 168 | 1161 | 146 | 0 | 0 | 102.09
19:30 | 0 | 120 | 0 | 0 | 350 | 102 | 70 | 356 | 192 | 40 | 0 | 340 | 100 | 93 | 0 | 55 | 110 | 0 | 62 | 5 | 70 | 58 | 140 | 60 | 91 | 50 | 39 | 54 | 56 | 55 | 19 | 25 | 26 | 33 | 31 | 50 | 0 | 88 | 80 | 0 | 0 | 25 | 0 | 201 | 0 | 110 | 0 | 51 | 66 | 0 | 72 | 99 | 44 | 16 | 21 | 0 | 120 | 100 | 164 | 272 | 183 | 78 | 0 | 28 | 0 | 10 | 42 | 85 | 50 | 8 | 19 | 11 | 33 | 17 | 154 | 65 | 72 | 20 | 0 | 52 | 60 | 53 | 50 | 163 | 307 | 31 | 86 | 46 | 78 | 0 | 44 | 10 | 280 | 23 | 8 | 0 | 279 | 0 | 0 | 180 | 104 |  | 477 | 0 | 100 | 110 | 99 | 150 | 0 | 46 | 43 | 55 | 40 | 186 | 27 | 72 | 0 | 0 | 0 | 43 | 37 | 100 | 40 | 43 | 45 | 43 | 43 | 22 | 11 | 8 | 0 | 67 | 160 | 17 | 17 | 183 | 0 | 0 | 180 | 95 | 40 | 0 | 0 |  | 7110 | 2599 | 9709 | 3216 | 477 | 1827 | 2343 | 227 | 168 | 1297 | 154 | 0 | 0 | 0
20:00 | 0 | 120 | 0 | 0 | 365 | 75 | 74 | 368 | 191 | 40 | 0 | 340 | 100 | 92 | 0 | 55 | 110 | 0 | 37 | 10 | 92 | 58 | 149 | 60 | 91 | 51 | 39 | 54 | 56 | 55 | 19 | 25 | 26 | 33 | 31 | 50 | 0 | 88 | 80 | 0 | 0 | 25 | 0 | 201 | 0 | 90 | 0 | 51 | 66 | 0 | 80 | 99 | 44 | 16 | 27 | 0 | 120 | 100 | 203 | 272 | 183 | 78 | 0 | 33 | 0 | 10 | 42 | 86 | 48 | 8 | 19 | 11 | 33 | 17 | 158 | 65 | 72 | 20 | 0 | 54 | 60 | 53 | 50 | 130 | 313 | 31 | 86 | 47 | 78 | 0 | 44 | 10 | 260 | 23 | 8 | 0 | 279 | 0 | 0 | 180 | 104 |  | 477 | 0 | 110 | 110 | 99 | 140 | 0 | 53 | 43 | 76 | 40 | 190 | 25 | 80 | 0 | 0 | 0 | 43 | 37 | 101 | 40 | 43 | 47 | 43 | 43 | 22 | 11 | 11 | 0 | 68 | 160 | 16 | 18 | 176 | 0 | 0 | 174 | 97 | 40 | 0 | 0 |  | 7121 | 2633 | 9754 | 3280 | 477 | 1758 | 2393 | 228 | 168 | 1292 | 158 | 0 | 0 | 102.11
21:00 | 0 | 120 | 0 | 0 | 365 | 87 | 74 | 370 | 180 | 40 | 0 | 340 | 100 | 100 | 0 | 55 | 150 | 0 | 97 | 17 | 93 | 58 | 149 | 60 | 91 | 50 | 37 | 54 | 56 | 55 | 19 | 25 | 32 | 33 | 31 | 50 | 0 | 88 | 80 | 0 | 0 | 25 | 0 | 209 | 0 | 135 | 0 | 51 | 66 | 0 | 80 | 99 | 44 | 16 | 31 | 0 | 120 | 100 | 222 | 327 | 200 | 78 | 0 | 33 | 0 | 10 | 42 | 86 | 47 | 8 | 19 | 11 | 33 | 0 | 158 | 66 | 72 | 20 | 0 | 54 | 60 | 53 | 50 | 130 | 321 | 29 | 86 | 47 | 78 | 0 | 42 | 10 | 310 | 23 | 8 | 0 | 286 | 0 | 0 | 180 | 105 |  | 478 | 0 | 150 | 106 | 99 | 120 | 0 | 53 | 43 | 72 | 40 | 192 | 31 | 80 | 0 | 0 | 0 | 43 | 38 | 101 | 40 | 43 | 46 | 43 | 43 | 22 | 12 | 11 | 0 | 59 | 160 | 16 | 18 | 182 | 0 | 0 | 180 | 97 | 40 | 0 | 0 |  | 7436 | 2658 | 10094 | 3517 | 478 | 1818 | 2410 | 219 | 168 | 1326 | 158 | 0 | 0 | 102.13
22:00 | 0 | 120 | 0 | 0 | 365 | 87 | 73 | 350 | 172 | 40 | 0 | 340 | 100 | 100 | 0 | 55 | 180 | 0 | 100 | 17 | 93 | 58 | 149 | 60 | 91 | 21 | 39 | 54 | 56 | 55 | 19 | 25 | 22 | 33 | 31 | 50 | 0 | 88 | 80 | 0 | 0 | 26 | 0 | 201 | 0 | 135 | 0 | 51 | 65 | 0 | 80 | 99 | 38 | 16 | 31 | 0 | 120 | 100 | 194 | 300 | 183 | 78 | 0 | 32 | 0 | 10 | 51 | 85 | 48 | 8 | 19 | 11 | 33 | 19 | 160 | 73 | 72 | 20 | 0 | 58 | 60 | 53 | 50 | 130 | 318 | 31 | 86 | 47 | 79 | 0 | 45 | 10 | 290 | 23 | 8 | 0 | 300 | 0 | 0 | 180 | 100 |  | 477 | 0 | 150 | 106 | 99 | 120 | 0 | 51 | 43 | 66 | 33 | 191 | 30 | 80 | 0 | 0 | 0 | 43 | 38 | 102 | 40 | 43 | 46 | 43 | 43 | 21 | 12 | 11 | 0 | 69 | 160 | 16 | 18 | 182 | 0 | 0 | 180 | 96 | 40 | 0 | 0 |  | 7349 | 2649 | 9998 | 3476 | 477 | 1797 | 2378 | 229 | 168 | 1313 | 160 | 0 | 0 | 102.15
23:00 | 0 | 120 | 0 | 0 | 365 | 87 | 73 | 350 | 171 | 0 | 0 | 340 | 100 | 100 | 0 | 15 | 180 | 0 | 38 | 0 | 93 | 7 | 149 | 10 | 91 | 11 | 39 | 54 | 55 | 55 | 19 | 25 | 32 | 33 | 31 | 51 | 0 | 88 | 80 | 0 | 0 | 25 | 0 | 202 | 0 | 135 | 0 | 42 | 65 | 0 | 80 | 99 | 38 | 16 | 31 | 0 | 120 | 100 | 190 | 315 | 195 | 78 | 0 | 32 | 0 | 10 | 51 | 86 | 0 | 0 | 19 | 11 | 33 | 20 | 156 | 69 | 40 | 20 | 0 | 58 | 60 | 53 | 50 | 130 | 315 | 30 | 86 | 47 | 80 | 0 | 44 | 10 | 270 | 23 | 8 | 0 | 300 | 0 | 0 | 185 | 102 |  | 473 | 0 | 150 | 106 | 99 | 120 | 0 | 0 | 43 | 66 | 0 | 192 | 29 | 80 | 0 | 0 | 0 | 43 | 0 | 66 | 40 | 43 | 45 | 43 | 42 | 22 | 12 | 11 | 0 | 71 | 159 | 0 | 19 | 172 | 0 | 0 | 171 | 96 | 0 | 0 | 0 |  | 6991 | 2413 | 9404 | 3432 | 473 | 1776 | 2003 | 230 | 168 | 1166 | 156 | 0 | 0 | 102.17
24:00 | 0 | 120 | 0 | 0 | 365 | 86 | 74 | 350 | 182 | 0 | 0 | 340 | 100 | 100 | 0 | 15 | 180 | 0 | 62 | 0 | 93 | 7 | 115 | 0 | 91 | 11 | 39 | 54 | 55 | 36 | 19 | 25 | 32 | 33 | 31 | 51 | 0 | 88 | 80 | 0 | 0 | 26 | 0 | 223 | 0 | 135 | 0 | 42 | 65 | 0 | 80 | 99 | 37 | 16 | 30 | 0 | 120 | 100 | 130 | 349 | 217 | 78 | 0 | 32 | 0 | 10 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 22 | 150 | 69 | 8 | 20 | 0 | 60 | 60 | 50 | 50 | 130 | 332 | 30 | 86 | 47 | 80 | 0 | 44 | 10 | 310 | 23 | 8 | 0 | 300 | 0 | 0 | 180 | 104 |  | 473 | 0 | 150 | 69 | 99 | 120 | 0 | 0 | 43 | 65 | 24 | 191 | 29 | 64 | 0 | 0 | 0 | 0 | 0 | 63 | 40 | 43 | 45 | 43 | 42 | 22 | 12 | 11 | 0 | 70 | 160 | 0 | 19 | 185 | 0 | 0 | 186 | 97 | 0 | 0 | 0 |  | 6995 | 2365 | 9360 | 3485 | 473 | 1823 | 1910 | 230 | 168 | 1121 | 150 | 0 | 0 | 102.19
KWH | 261000 | 2870280 | 0 | 0 | 8319163 | 1969636 | 1477056 | 8635390 | 5932000 | 151300 | 0 | 8341250 | 2556596 | 1020480 | 92040 | 595118 | 4138747 | 0 | 2718000 | 63360 | 940800 | 472320 | 2121600 | 549840 | 1553280 | 236280 | 781056 | 834480 | 952257 | 822178 | 428832 | 600000 | 680940 | 789800 | 758700 | 1102896 | 0 | 2072091 | 1913500 | 0 | 0 | 475020 | 0 | 4871875 | 0 | 1633952 | 0 | 981600 | 533552 | 207545 | 1745880 | 1706880 | 971520 | 378144 | 557280 | 138404 | 2750810 | 2584644 | 3613700 | 7430500 | 4632000 | 2258182 | 0 | 825336 | 0 | 266000 | 888347 | 92040 | 167320 | 38011 | 447336 | 235440 | 657100 | 389630 | 3070080 | 2215320 | 516600 | 448524 | 8928 | 1352000 | 143256 | 1068000 | 1037000 | 3242372 | 6697473 | 720000 | 1669440 | 881640 | 1927290 | 0 | 938280 | 229500 | 7592600 | 456792 | 194784 | 0 | 2697271 | 0 | 0 | 2553600 | 2476590 |  | 11577455 | 0 | 3856896 | 557920 | 1061760 | 3060480 | 0 | 146180 | 384000 | 682368 | 398625 | 4631053 | 447913 | 846720 | 0 | 0 | 0 | 224520 | 331228 | 1340012 | 842640 | 929888 | 252041 | 454560 | 268159 | 498000 | 251928 | 150174 | 0 | 1625890 | 3895700 | 64000 | 139000 | 4664409 | 0 | 0 | 4463972 | 1741477 | 149760 | 0 | 0 |  | 150367654 | 49938728 | 200306382 | 81741867 | 11577455 | 41379941 | 32275306 | 5521590 | 3985591 | 20745624 | 3070080 | 8928 | 0
Fuel Cost | 224460 | 2468440.8 | 0 | 0 | 7154480.18 | 1595405.16 | 1388432.64 | 5267587.9 | 3618520 | 1453993 | 0 | 5588637.5 | 38834693.24 | 6408614.4 | 614827.2 | 3636170.98 | 2690185.55 | 0 | 3016980 | 985881.6 | 5880000 | 3112588.8 | 20515872 | 3502480.8 | 9304147.2 | 3778117.2 | 5209643.52 | 5949842.4 | 5951606.25 | 5155056.06 | 321624 | 450000 | 0 | 0 | 0 | 10433396.16 | 0 | 0 | 0 | 0 | 0 | 4498439.4 | 0 | 66501093.75 | 0 | 35799888.32 | 0 | 8628264 | 5746355.04 | 2019412.85 | 10806997.2 | 11026444.8 | 6353740.8 | 321422.4 | 0 | 125947.64 | 2503237.1 | 2352026.04 | 3288467 | 5127045 | 3242400 | 1558145.58 | 0 | 552975.12 | 0 | 244720 | 728444.54 | 86517.6 | 1813748.8 | 282041.62 | 344448.72 | 176580 | 505967 | 292222.5 | 20999347.2 | 1661490 | 4747554 | 345363.48 | 0 | 1406080 | 148986.24 | 1025280 | 933300 | 4182659.88 | 4688231.1 | 820800 | 1786300.8 | 969804 | 2197110.6 | 0 | 872600.4 | 213435 | 4859264 | 342594 | 148035.84 | 0 | 0 | 0 | 0 | 0 | 0 |  | 59045020.5 | 0 | 2584120.32 | 3682272 | 7113792 | 49212518.4 | 0 | 2333032.8 | 4323840 | 8038295.04 | 2539241.25 | 4584742.47 | 443433.87 | 5232729.6 | 0 | 0 | 0 | 2570754 | 3550764.16 | 12006507.52 | 7288836 | 8276003.2 | 2684236.65 | 4509235.2 | 2888072.43 | 547800 | 236812.32 | 113681.718 | 0 | 9869152.3 | 0 | 1476480 | 2980160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 391786913.9 | 208131533.748 | 599918447.648 | 59467732.718 | 59045020.5 | 30879513.29 | 197529682.68 | 9869152.3 | 0 | 222127998.96 | 20999347.2 | 0 | 0
Yesterday Day Peak | 0 | 120 | 0 | 0 | 365 | 99 | 73 | 350 | 231 | 0 | 0 | 380 | 100 | 7 | 0 | 15 | 194 | 0 | 162 | 0 | 7 | 20 | 98 | 10 | 89 | 11 | 39 | 36 | 36 | 36 | 22 | 25 | 30 | 33 | 25 | 50 | 0 | 88 | 80 | 0 | 0 | 25 | 0 | 220 | 0 | 50 | 0 | 51 | 0 | 0 | 68 | 57 | 38 | 16 | 3 | 0 | 150 | 130 | 185 | 301 | 184 | 78 | 0 | 36 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 18 | 108 | 98 | 24 | 20 | 1.5 | 60 | 60 | 48 | 50 | 130 | 314 | 30 | 84 | 46 | 80 | 0 | 42 | 7 | 310 | 15 | 8 | 0 | 43 | 0 | 0 | 100 | 103 |  | 478 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 8 | 8 | 194 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 35 | 35 | 0 | 8 | 0 | 22 | 10 | 5 | 0 | 64 | 159 | 0 | 0 | 193 | 0 | 0 | 179 | 54 | 0 | 0 | 0 |  | 8081.5 | DayPeak
Yesterday Evening Peak | 0 | 120 | 0 | 0 | 365 | 87 | 74 | 370 | 180 | 40 | 0 | 340 | 100 | 100 | 0 | 55 | 150 | 0 | 97 | 17 | 93 | 58 | 149 | 60 | 91 | 50 | 37 | 54 | 56 | 55 | 19 | 25 | 32 | 33 | 31 | 50 | 0 | 88 | 80 | 0 | 0 | 25 | 0 | 209 | 0 | 135 | 0 | 51 | 66 | 0 | 80 | 99 | 44 | 16 | 31 | 0 | 120 | 100 | 222 | 327 | 200 | 78 | 0 | 33 | 0 | 10 | 42 | 86 | 47 | 8 | 19 | 11 | 33 | 0 | 158 | 66 | 72 | 20 | 0 | 54 | 60 | 53 | 50 | 130 | 321 | 29 | 86 | 47 | 78 | 0 | 42 | 10 | 310 | 23 | 8 | 0 | 286 | 0 | 0 | 180 | 105 |  | 478 | 0 | 150 | 106 | 99 | 120 | 0 | 53 | 43 | 72 | 40 | 192 | 31 | 80 | 0 | 0 | 0 | 43 | 38 | 101 | 40 | 43 | 46 | 43 | 43 | 22 | 12 | 11 | 0 | 59 | 160 | 16 | 18 | 182 | 0 | 0 | 180 | 97 | 40 | 0 | 0 |  | 10094 | EvPeak
Forecast for Evening | 0 | 120 | 0 | 0 | 365 | 108 | 78 | 412 | 360 | 84 | 0 | 450 | 305 | 100 | 0 | 55 | 200 | 0 | 209 | 100 | 93 | 102 | 149 | 100 | 100 | 50 | 42 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 50 | 0 | 92 | 80 | 0 | 0 | 25 | 0 | 225 | 0 | 135 | 0 | 51 | 85 | 85 | 80 | 98 | 44 | 16 | 31 | 0 | 150 | 100 | 360 | 360 | 225 | 100 | 0 | 42 | 0 | 10 | 51 | 85 | 50 | 52 | 19 | 10 | 33 | 22 | 165 | 100 | 95 | 22 | 0 | 60 | 60 | 51 | 50 | 163 | 330 | 30 | 86 | 50 | 100 | 0 | 44 | 10 | 341 | 23 | 8 | 200 | 300 | 0 | 0 | 180 | 105 |  | 488 | 48 | 100 | 110 | 115 | 225 | 0 | 53 | 43 | 83 | 40 | 194 | 30 | 110 | 30 | 0 | 0 | 43 | 31 | 102 | 42 | 43 | 45 | 43 | 43 | 22 | 12 | 11 | 0 | 69 | 160 | 17 | 18 | 215 | 0 | 0 | 220 | 95 | 100
Forecast for Day | 0 | 120 | 0 | 0 | 365 | 100 | 78 | 412 | 360 | 84 | 0 | 450 | 150 | 100 | 0 | 55 | 200 | 0 | 209 | 100 | 90 | 102 | 149 | 100 | 100 | 50 | 42 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 42 | 0 | 92 | 80 | 0 | 0 | 25 | 0 | 225 | 0 | 60 | 0 | 51 | 85 | 85 | 80 | 98 | 44 | 16 | 15 | 0 | 150 | 100 | 285 | 360 | 225 | 87 | 0 | 42 | 0 | 10 | 51 | 85 | 0 | 52 | 19 | 5 | 33 | 22 | 130 | 100 | 95 | 22 | 2 | 60 | 60 | 51 | 50 | 163 | 330 | 30 | 86 | 50 | 80 | 0 | 44 | 10 | 341 | 23 | 8 | 0 | 100 | 0 | 0 | 54 | 106 |  | 488 | 0 | 150 | 110 | 99 | 225 | 0 | 0 | 36 | 50 | 40 | 194 | 30 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 42 | 43 | 45 | 43 | 0 | 22 | 11 | 8 | 0 | 69 | 160 |  | 18 | 215 | 0 | 0 | 220 | 95
Generation at 08:00(Today) | 0 | 120 | 0 | 0 | 200 | 25 | 40 | 300 | 291 | 0 | 0 | 320 | 100 | 7 | 0 | 0 | 110 | 0 | 38 | 0 | 7 | 7 | 82 | 0 | 8 | 0 | 12 | 18 | 18 | 17 | 19 | 25 | 30 | 33 | 31 | 25 | 0 | 92 | 80 | 0 | 0 | 8 | 0 | 215 | 0 | 50 | 0 | 8 | 0 | 29 | 80 | 19 | 18 | 16 | 7 | 0 | 120 | 100 | 285 | 231 | 187 | 78 | 0 | 32 | 0 | 10 | 6 | 10 | 0 | 0 | 16 | 5 | 8 | 15 | 106 | 87 | 8 | 20 | 0.3 | 60 | 60 | 11 | 20 | 100 | 303 | 30 | 10 | 10 | 80 | 0 | 20 | 10 | 290 | 15 | 8 | 0 | 32 | 0 | 0 | 25 | 106 | 0 | 472 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 36 | 8 | 33 | 192 | 6 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 16 | 0 | 8 | 0 | 18 | 11 | 8 | 0 | 73 | 160 | 0 | 0 | 160 | 0 | 0 | 144 | 54 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 6831.3 | 7:00
| Highest Generation |  | 10094 | 21:00
| Day Peak Generation |  | 8081.5 | 12:00
| Evening Peak Generation |  | 10094 | 21:00
| HVDC Max Flow |  | 478 | 1:00
| HVDC EvPeak Flow |  | 478 | 21:00
| Load factor L.F |  | 82.68%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2018-06-26
Till now the maximum generation is : - |  |  | 10958 | 21:00 | Hrs on | 2018-05-28
The Summary of Yesterday's |  | 2018-06-25 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8081.5 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 6501.1 | MW
Evening Peak Generation : |  | 10094 | MW Hour : | 21:00 | Available Max Generation : |  | 12231 | MW
E.P. Demand (at gen end) : |  | 10094 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 10600 | MW
Maximum Generation : |  | 10094 | MW Hour : | 21:00 | Reserve(Generation end) |  | 1631 | MW
Total Gen. (MKWH) : |  | 200.3064 | System Load Factor : | 82.68% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -660 | MW at | 2:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2018-06-26
Actual : | 102.2 | Ft.(MSL) , | Rule curve : | 82.65 | Ft.( MSL )
Gas Consumed : | Total = | 1045.18 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 90347246.008
|  | Coal : | 9869152.3 | Oil : | 419657681.64 | Total : | 519874079.948
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3811.1155 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1294.9982 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1160.0987 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1048.1843 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 947.2636 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 764.4057 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 428.6946 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 196.8477 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 589.5415 |  |  | 0 | 0%
Total | 0 |  | 10241.1496 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1 |  | 10) Ashuganj 55 MW
| Nil |  |  | 2) Khulna ST 110 MW |  | 11) Haripur GT-1,2
|  |  |  | 3) Ghorasal Unit-1,4,5 |  | 12)Shajibazar GT-8
|  |  |  | 4) Baghabari 100 MW |  | 13) Chandpur 163 MW
5) Tongi GT
6) Chittagong Unit-1,2
7) Baghabari-71 MW
8) Siddhirganj 210 MW ST
9) Ashuganj unit-3
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Sikalbaha 132 kV bus-A was under shut down from 07:58 to 08:40 for C/M.
b) Hasnabad 132/33 kV T1 transformer was under shut down from 11:56 to 17:43 for C/M.
c) Hasnabad 132/33 kV T2 transformer was under shut down from 09:20 to 11:55 for C/M.
d) Bakulia 132/33 kV bus-A was under shut down from 09:11 to 11:55 for C/M.
e) Bheramara 230/132 kV T1 transformer tripped at 03:07(26/06/2018) showing differential E/F relay and was
switched on at 06:39.
f) Joypurhat 132/33 kV T3 transformer was shut down from 08:05 to 09:25 for C/M.
g) Saidpur 132/33 kV T5 transformer was under shut down from 11:30 to 11:38 for C/M.
h) Thakurgaon-Purbasadipur 132 kV Ckt-1 was under shut down from 14:22 to 15:13 for PT box maintenance at
Thakurgaon end.
i) Panchaghar 33 kV bus-section-2 was under shut down from 16:46 to 17:15 due to red hot at bus loop. |  |  |  | About 15 MW Power interruption occurred under Panchaghar S/S
area from 16:46 to 17:15.
j) Fenchuganj 132/33 kV T2 transformer tripped at 15:14 due to 33 kV bus PT burst and was switched on at 17:04. |  |  |  | About 7 MW Power interruption occurred under Fenchuganj S/S
area from 15:14 to 17:04.
k) Ashuganj(N) 360 MW ST was synchronized at 14:24 and again tripped at 14:25 due to tripping of condenser vacuum
pressure and was synchronized at 03:37(26/06/2018).
l) Bakulia 132/33 kV T1 & T2 transformers tripped at 04:20(26/06/2018) due to problem at Auxiliary supply and were |  |  |  | About 52 MW Power interruption occurred under Bakulia S/S
switched on at 05:28. |  |  |  | area from 04:20 to 05:28(26/06/2018).
m) Bheramara 360 MW GT was shut down at 05:42 for conduct some test on control system.
n) Thakurgaon-Panchaghar 132 kV Ckt tripped at 06:14 (26/06/2018) from Thakurgaon end showing auto reclose trip, |  |  |  | About 36 MW Power interruption occurred under Thakurgaon S/S
Main protection trip and was switched on at 06:17. |  |  |  | area from 06:14 to 06:17(26/06/2018).
o) Thakurgaon-Purbasadipur 132 kV Ckt-2 tripped at 06:06 (26/06/2018) from Thakurgaon end showing auto reclose trip,
Main protection trip and was switched on at 06:17.
p) Noapara 132/33 kV T1 & T2 transformers & 33 kV bus were under shut down from 06:31 to 07:50 (26/06/2018) due to |  |  |  | About 15MW Power interruption occurred under Noapara S/S
red hot at 33 kV side bus isolator. |  |  |  | area from 06:31 to 07:50(26/06/2018)
q) Noapara 132/33 kV T4 transformer was under shut down from 22:37 to 23:32 for red hot at 33 kV Monirampur feeder. |  |  |  | About 53MW Power interruption occurred under Noapara S/S
area from 22:37 to 23:32(26/06/2018)
r) Ishurdi-Bheramara 132 kV Ckt-1 was shut down from 03:47 to 05:26 due to PT burst of T1 transformer at Roppur S/S.
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2018-06-25 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 0 | 261000 | Under maint.
| Ghorasal ST: Unit-3 |  | PDB | 1*210 | 170 | 120 | 2870280 | Gas shortage
| Ghorasal ST: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 365 | 8319163
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 74 | 1477056
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 87 | 1969636
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 370 | 8635390 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 40 | 151300 | Low demand
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 180 | 5932000 | Gas shortage
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 340 | 8341250 | Frequency control.
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1020480
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 100 | 2556596 | Low demand
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 0 | 92040 | Cable fault
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 595118
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 60 | 549840 | Low demand
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 428832
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 97 | 2718000 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 17 | 63360 | Low demand
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 93 | 940800 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 150 | 4138747 | Gas shortage
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 50 | 50 | 236280
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 58 | 472320 | Low demand
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 37 | 781056 | Engine problem
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 834480
25 | Kodda 150MW |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 2121600
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 56 | 952257
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 822178
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 91 | 1553280 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1280940 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 789800
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 31 | 758700 | Engine problem
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 50 | 1102896
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
34 | Summit Gazipur |  | IPP | 18*17.076 | 300 | 286 | 2697271
| APR Energy , Keranigonj |  | IPP | 236*1.4 | 0 | 0 | 0
| Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 0 | 0 | 0 | On test.
| Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 0 | 105 | 2476590 | On test.
| Dhaka area Total |  |  |  | 5199 | 3379 | 67940536
35 | Chittagong ST-1 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
36 | Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
36 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 475020
37 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 44 | 971520
38 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 168 | 3985591 | # 5 under maint.
39 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
40 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 209 | 4871875 | FGMO
41 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 135 | 1633952
42 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 981600
43 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 66 | 533552
44 | Dohazari Peaking |  | PDB | 6*17 | 102 | 0 | 207545 | Machine problem
45 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 80 | 1745880 | Engine problem
46 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 378144
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 31 | 557280
47 | Chittagong ECPV 108 MW |  | IPP | 16*7 | 108 | 99 | 1706880
| Chittagong area Total |  |  |  | 1561 | 924 | 18048839
48 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 138404 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 120 | 2750810
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2584644 | Gas shortage
49 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 200 | 4632000 | FGMO
50 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 222 | 3613700 | Only GT in FGMO
51 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 327 | 7430500 | FGMO
52 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 33 | 825336 | Engine problem
53 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
54 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 10 | 266000
55 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 78 | 2258182 | Low demand
56 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 42 | 888347
57 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 86 | 92040
58 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 47 | 167320
59 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
60 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 19 | 447336
61 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 235440
** | Tripura |  | Imported power | 0 | 160 | 158 | 3070080
62 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 657100
63 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 8 | 38011 | Low demand
64 | Summit Comilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 0 | 389630 | Machine tripped
65 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Comilla Area Total |  |  |  | 2541 | 1494 | 30484880
66 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 66 | 2215320
67 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 20 | 448524
68 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 72 | 516600 | Low demand
69 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 8928
| United Mymensingh PPL |  | IPP | 200 | 0 | 180 | 2553600 | On test.
| Mymensingh Area Total |  |  |  | 322 | 338 | 5742972
70 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 54 | 1352000
71 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 60 | 143256
72 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 130 | 3242372 | Low demand
73 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 321 | 6697473 | FGMO
74 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 53 | 1068000
75 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 50 | 1037000
76 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 8 | 194784 | Engine problem
77 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 29 | 720000 | FGMO
78 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 86 | 1669440
79 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 47 | 881640 | Engine problem
80 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 78 | 1927290
81 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
82 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 42 | 938280 | Engine problem
83 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 23 | 456792
84 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 310 | 7592600 | FGMO
85 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 10 | 229500
| Sylhet Area Total |  |  |  | 1549 | 1301 | 28150427
86 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
| Bheramara (HVDC ) |  | Imported power | 1*500 | 500 | 478 | 11577455
87 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 110 | 106 | 557920
88 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 1061760 | Engine problem
89 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 43 | 384000
90 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 120 | 3060480 | Low demand
91 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 72 | 682368 | Low demand
92 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 150 | 3856896 | Gas shortage
93 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 398625 | Engine problem
94 | Khulna (Aggreko) 55MW |  | QRPP | 71*0.85 | 55 | 53 | 146180
95 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 40 | 149760 | Low demand
| Khulna Area Total |  |  |  | 1769 | 1201 | 21875444
96 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 80 | 846720
97 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
98 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 31 | 447913
99 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 192 | 4631053
100 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 97 | 1741477
| Barisal Area Total |  |  |  | 462 | 400 | 7667163
101 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Under maint.
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
102 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 43 | 224520
103 | Bera Peaking |  | PDB | 9*8.29 | 71 | 38 | 331228 | Engine problem
104 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 40 | 842640 | Engine problem
105 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 929888 | Engine problem
106 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 46 | 252041
107 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | FGMO
108 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 180 | 0 | FGMO
| Sirajgonj Unit-3 225MW |  | NWPGCL | 1*150+1*75 | 0 | 0 | 0
109 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 43 | 268159
110 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 498000
111 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 12 | 251928
112 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 150174
113 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 43 | 454560 | Engine problem
114 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 101 | 1340012
| Rajshahi Area Total |  |  |  | 1123 | 622 | 5543150
115 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 59 | 1625890
116 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 160 | 3895700
117 | Rangpur GT |  | PDB | 1*20 | 20 | 16 | 64000
118 | Saidpur GT |  | PDB | 1*20 | 20 | 18 | 139000
| Rangpur Area Total |  |  |  | 484 | 253 | 5724590
| Total |  |  |  | 15010 | 9912 | 191178001
| Eastern Grid Total |  |  |  | 11172 | 7436 | 150367654
| Western Grid Total |  |  |  | 3838 | 2476 | 40810347
| National Grid Total |  |  |  | 15010 | 9912 | 191178001
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2018-06-25 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 6474 | MW | (b) ENTIRE WESTERN GRID : |  |  | 3271 | MW
i) Dhaka area |  |  | 3474 | MW | i) Khulna area |  |  | 1330 | MW
ii) Chittagong area |  |  | 955 | MW | ii) Rajshahi area |  |  | 1073 | MW
iii) Comilla area |  |  | 884 | MW | iii) Barisal area |  |  | 238 | MW
iv) Mymensingh area |  |  | 735 | MW | iv) Rangpur area |  |  | 630 | MW
v) Sylhet area |  |  | 426 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 9745 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 122 | 1200 | Netrokona | 75 | 2100 | Central s/s | 62 | 2100
Munsiganj | 102 | 100 | Jamalpur | 110 | 2200 | Noapara | 79 | 2100
Megnaghat | 44 | 1830 | Sherpur | 80 | 2000 | Jessore | 126 | 2100
Shyampur | 135 | 1200 | Srimongal | 32 | 2000 | Jhenida | 86 | 2100
Bhulta | 157 | 2100 | Shahjibazar | 104 | 2100 | Bottail | 120 | 1930
Madanganj | 42 | 1400 | Fenchuganj | 42 | 2000 | G.K Project | 54 | 2000
Shitalakhya | 90 | 100 | Kulawara | 37 | 2100 | Faridpur | 140 | 2000
Rahim steel | 9 | 1300 | Sylhet | 120 | 2100 | Madaripur | 124 | 2100
Matuail | 73 | 1200 | Chatak | 24 | 2100 | Gopalganj | 72 | 2100
Ghorasal | 77 | 1930 | Sunamganj | 31 | 2100 | Bagerhat | 75 | 1930
Narsingdi | 109 | 2100 | Biani Bazar | 38 | 2000 | Mongla | 32 | 1000
Haripur (SBU) | 74 | 2100 | Comilla (S) | 160 | 2200 | Satkhira | 74 | 100
Ullon | 86 | 1900 | Comilla(N) | 77 | 2200 | Gallamari | 43 | 1300
Hasnabad | 178 | 2100 | Chandpur | 105 | 2200 | Magura | 40 | 2100
Magbazar | 128 | 1100 | Feni | 110 | 2100 | Chuadanga | 77 | 2100
Maniknagar | 86 | 1100 | Chowmuhani | 172 | 2100 | Barisal | 108 | 1930
Bangabhaban | 36 | 1600 | Ashuganj | 56 | 2200 | Patuakhali | 77 | 1930
Narinda | 69 | 1500 | Daudkandi | 102 | 2200 | Bhandaria | 42 | 2100
Dhanmondi | 115 | 1300 | B.Baria | 120 | 2100 | Ishurdi | 53 | 100
Lalbag | 46 | 2100 | Ramganj | 25 | 2200 | Ruppur Paromanobik | 1 | 100
Madartek | 98 | 2000 | Madunaghat | 50 | 2000 | Natore | 115 | 2000
Mirpur | 111 | 1930 | Hathazari | 87 | 2100 | Bogra | 229 | 2000
Kalyanpur | 138 | 1200 | Khulshi | 178 | 1500 | Noagaon | 97 | 2000
Gulshan | 79 | 1930 | Halishahar | 116 | 2100 | Rajshahi | 136 | 2000
Uttara | 58 | 1800 | Baraulia | 128 | 2400 | C.Nawabganj | 69 | 2000
Kamrangirchar | 140 | 2000 | Sikalbaha | 32 | 1830 | Amnura | 32 | 100
Savar | 141 | 1200 | Dohazari | 80 | 1900 | Pabna | 109 | 2000
Bhasantec | 44 | 1300 | Cox'sbazar | 79 | 1900 | Shahjadpur | 82 | 2000
Agargaon | 86 | 1830 | Chandraghona | 32 | 2100 | Serajganj | 73 | 2000
Satmosjid | 130 | 900 | Kaptai | 4 | 2000 | Niyamatpur | 53 | 2000
Tongi | 186 | 1600 | A. Khaer Stl. | 13 | 1600 | Joypurhat | 50 | 2000
Kabirpur | 121 | 1300 | Bakulia | 91 | 1900 | Rangpur | 122 | 2000
Basundhara | 100 | 2100 | Julda | 13 | 2200 | Lalmonirhat | 81 | 2000
Manikganj | 215 | 2000 | TK chemical | 6 | 1830 | Saidpur | 105 | 1930
Joydevpur | 102 | 1500 | Modern Steel | 13 | 1600 | Purbasadipur | 97 | 2000
New Tongi | 126 | 1930 | Shahmirpur | 27 | 1830 | Thakurgaon | 72 | 2000
Korda | 212 | 2100 | Abul Khair 230 | 186 | 800 | Palashbari | 100 | 2000
Tangail | 166 | 2100 | BSRM | 109 | 300 | Barapukuria | 50 | 2000
Mymensing | 225 | 1900 | Khagrachhari | 17 | 2000 | Panchagar | 38 | 2000
Kishorganj | 85 | 1900 | Goalpara | 41 | 2000
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  |  | (27) NLDC

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS.
Date: | 2018-06-25
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 393 | 17:00 | 384 | 10:00 | Kaliakoir | 375 | 2:00 | 365 | 10:00
Bheramara | 410 | 13:00 | 395 | 1:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 230 | 1:00 | 228 | 11:00 | Tongi | 225 | 5:00 | 214 | 10:00
Ishurdi | 233 | 18:00 | 225 | 12:00 | Comilla (N) | 230 | 4:00 | 224 | 9:00
Ashuganj | 235 | 5:00 | 230 | 1:00 | Hathazari | 222 | 3:00 | 215 | 16:00
Serajganj | 224 | 5:00 | 216 | 1:00 | Megnaghat | 230 | 4:00 | 222 | 12:00
Baghabari | 228 | 19:30 | 220 | 1:00 | Fenchuganj | 239 | 19:30 | 235 | 9:00
Barapukuria | 233 | 7:00 | 223 | 21:00 | Siddhirganj | 225 | 4:00 | 219 | 10:00
Bogra | 226 | 18:30 | 212 | 21:00 | Maniknagar | 223 | 2:00 | 217 | 10:00
Khulna South | 240 | 18:30 | 230 | 13:00 | Old Airport | 225 | 2:00 | 216 | 11:00
Rampura | 221 | 2:00 | 218 | 11:00 | Barisal | 228 | 4:00 | 222 | 12:00
Haripur | 223 | 23:00 | 218 | 10:00 | AKSML | 220 | 20:00 | 210 | 12:00
Hasnabad | 226 | 22:00 | 220 | 9:00 | BSRM | 228 | 21:00 | 213 | 9:00
Aminbazar | 225 | 1:00 | 218 | 10:00 | Bibiyana | 234 | 8:00 | 231 | 17:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 136 | 1930 | 131 | 1100 | Ramganj | 126 | 700 | 120 | 1400
Munsiganj | 137 | 1930 | 131 | 900 | Madanhat | 133 | 1700 | 128 | 800
Megnaghat | 132 | 100 | 130 | 800 | Hathazari | 132 | 300 | 127 | 1500
Shyampur | 134 | 2100 | 128 | 900 | Khulshi | 127 | 100 | 123 | 900
Bhulta | 128 | 400 | 123 | 1200 | Halishahar | 130 | 100 | 125 | 800
Madanganj | 136 | 600 | 127 | 1000 | Baraulia | 128 | 1400 | 125 | 800
Shitalakhya | 139 | 1930 | 131 | 1000 | Sikalbaha | 131 | 200 | 127 | 900
Rahim steal | 136 | 400 | 131 | 1000 | Dohazari | 130 | 400 | 124 | 2400
Matuail | 135 | 1930 | 130 | 900 | Cox'sbazar | 125 | 600 | 116 | 1900
Ghorasal | 136 | 100 | 132 | 800 | Chandraghona | 132 | 500 | 128 | 900
Narsinghdi | 133 | 400 | 128 | 1600 | Kaptai | 135 | 2100 | 130 | 100
Haripur (SBU) | 136 | 2000 | 132 | 900 | A. Khaer Stl. | 129 | 2000 | 124 | 800
Ullon | 134 | 600 | 128 | 1200 | Bakulia | 129 | 200 | 125 | 1300
Hasnabad | 137 | 400 | 132 | 1200 | Julda | 130 | 200 | 125 | 800
Magbazar | 138 | 400 | 128 | 1100 | TK Chemical | 132 | 100 | 129 | 1000
Maniknagar | 136 | 600 | 131 | 1100 | Modern Steel | 130 | 300 | 125 | 900
Bangabhaban | 136 | 600 | 131 | 1100 | Shahmirpur | 130 | 200 | 125 | 900
Narinda | 136 | 600 | 131 | 1100 | Khagrachhari | 131 | 400 | 128 | 2400
Dhanmondi | 134 | 600 | 128 | 1200 | Goalpara | 138 | 1930 | 131 | 1300
Lalbag | 140 | 600 | 133 | 1100 | Central s/s | 137 | 1930 | 133 | 200
Madartek | 135 | 400 | 129 | 1700 | Noapara | 135 | 600 | 129 | 1300
Mirpur | 135 | 500 | 129 | 1200 | Jessore | 132 | 700 | 125 | 1300
Kalyanpur | 135 | 200 | 130 | 1100 | Jhenida | 130 | 600 | 121 | 2100
Gulshan | 134 | 400 | 128 | 1100 | Bottail | 135 | 500 | 130 | 1200
Uttara | 132 | 500 | 126 | 900 | G.K.Project | 140 | 600 | 133 | 1300
Kamrangirchar | 137 | 400 | 131 | 1100 | Faridpur | 132 | 1830 | 125 | 2100
Savar | 134 | 200 | 127 | 900 | Madaripur | 133 | 400 | 127 | 2100
Bhasantec | 133 | 300 | 126 | 1100 | Gopalganj | 137 | 2300 | 127 | 1300
Agargaon | 134 | 200 | 128 | 1000 | Bagerhat | 135 | 100 | 130 | 1200
Satmosjid | 133 | 200 | 127 | 1000 | Mongla | 133 | 1000 | 128 | 1300
Tongi | 136 | 700 | 127 | 1000 | Satkhira | 136 | 600 | 130 | 1300
Kabirpur | 133 | 200 | 128 | 900 | Gallamari | 138 | 1930 | 132 | 1300
Basundhara | 131 | 100 | 124 | 1100 | Magura | 130 | 600 | 120 | 100
Manikganj | 138 | 400 | 132 | 900 | Chuadanga | 128 | 600 | 115 | 2100
Joydevpur | 136 | 800 | 129 | 1200 | Barisal | 139 | 600 | 135 | 1200
New Tongi | 134 | 400 | 126 | 1000 | Patuakhali | 142 | 500 | 130 | 1300
Kodda | 135 | 2100 | 130 | 1400 | Bhandaria | 137 | 500 | 131 | 1300
Tangail | 135 | 500 | 127 | 2100 | Ishurdi | 140 | 600 | 134 | 1300
Mymensing | 130 | 1600 | 122 | 2100 | Ruppur Paromanobik | 139 | 600 | 132 | 1300
Kishorganj | 131 | 100 | 124 | 2100 | Natore | 138 | 600 | 128 | 1300
Netrokona | 131 | 700 | 122 | 2000 | Bogra | 134 | 1800 | 122 | 100
Jamalpur | 135 | 1600 | 126 | 600 | Noagaon | 130 | 600 | 119 | 2000
Sherpur | 133 | 1600 | 124 | 900 | Rajshahi | 135 | 1800 | 126 | 1300
Srimongal | 138 | 1300 | 135 | 800 | C.Nawabganj | 134 | 1400 | 123 | 1500
Shahjibazar | 136 | 1000 | 133 | 2100 | Amnura | 138 | 1800 | 128 | 1200
Fenchuganj | 136 | 300 | 134 | 2100 | Pabna | 135 | 1800 | 127 | 100
Khulawara | 136 | 1600 | 134 | 1900 | Shahjadpur | 140 | 600 | 134 | 1300
Sylhet | 136 | 400 | 133 | 2100 | Serajganj | 135 | 1830 | 128 | 100
Chatak | 136 | 500 | 132 | 2100 | Niyamatpur | 129 | 1830 | 114 | 2000
Sunamganj | 130 | 100 | 129 | 700 | Joypurhat | 130 | 600 | 115 | 2000
Biani Bazar | 135 | 400 | 131 | 2100 | Rangpur | 125 | 600 | 108 | 100
Comilla(s) | 128 | 400 | 122 | 1900 | Lalmonirhat | 120 | 600 | 100 | 2000
Comilla(n) | 134 | 700 | 129 | 1400 | Saidpur | 124 | 600 | 106 | 2000
Chandpur | 128 | 800 | 118 | 2200 | Purbasadipur | 132 | 700 | 118 | 2000
Feni | 120 | 1800 | 116 | 2100 | Thakurgaon | 125 | 600 | 107 | 2000
Chowmuhani | 132 | 500 | 115 | 1900 | Palashbari | 125 | 600 | 112 | 2000
Ashuganj | 137 | 1400 | 134 | 2100 | Barapukuria | 133 | 600 | 123 | 2000
Daudkandi | 135 | 1930 | 128 | 1000 | Panchagar | 125 | 400 | 101 | 2000
B.Baria | 137 | 1400 | 132 | 2100
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division
Page 7 of 7

## L-Curve
Date | 2018-06-25
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 640 | 6995 | 2365 | 9360 |  |  |  | QF-LDC-12
0:30 | 640 | 6889 | 2408 | 9297 | Date: | 2018-06-25
1:00 | 640 | 6783 | 2451 | 9234
1:30 | 650 | 6665.5 | 2355.5 | 9021
2:00 | 660 | 6548 | 2260 | 8808
2:30 | 640 | 6415 | 2201 | 8616 | [5 empty] | Gen. at Eve. Peak | 10094 | 10094 MW (21:00 )
3:00 | 620 | 6282 | 2142 | 8424 | [6 empty] | 21:00
3:30 | 610 | 6154 | 2116.5 | 8270.5 | [5 empty] | Gen. at Day Peak | 8081.5 | 8081.5 MW (12:00 )
4:00 | 600 | 6026 | 2091 | 8117 | [6 empty] | 12:00
4:30 | 560 | 5879 | 2055 | 7934 | [5 empty] | Highest Generation | 10094
5:00 | 520 | 5732 | 2019 | 7751 | [6 empty] | 21:00
5:30 | 420 | 5402.5 | 1920.5 | 7323
6:00 | 320 | 5073 | 1822 | 6895
6:30 | 320 | 5084.65 | 1778.5 | 6863.15
7:00 | 320 | 5096.3 | 1735 | 6831.3
7:30 | 280 | 5083.3 | 1815.5 | 6898.8
8:00 | 240 | 5070.3 | 1896 | 6966.3
8:30 | 280 | 5457 | 1810.5 | 7267.5
9:00 | 320 | 5843.7 | 1725 | 7568.7
9:30 | 330 | 5954.85 | 1754 | 7708.85
10:00 | 340 | 6066 | 1783 | 7849
10:30 | 370 | 6171.1 | 1711 | 7882.1
11:00 | 400 | 6276.2 | 1639 | 7915.2
11:30 | 435 | 6351.35 | 1647 | 7998.35
12:00 | 470 | 6426.5 | 1655 | 8081.5
12:30 | 495 | 6447.75 | 1683.5 | 8131.25
13:00 | 520 | 6469 | 1712 | 8181
13:30 | 510 | 6351 | 1773 | 8124
14:00 | 500 | 6233 | 1834 | 8067
14:30 | 470 | 6336.15 | 1853 | 8189.15
15:00 | 440 | 6439.3 | 1872 | 8311.3
15:30 | 405 | 6338.75 | 1876 | 8214.75
16:00 | 370 | 6238.2 | 1880 | 8118.2
16:30 | 355 | 6135.15 | 1834 | 7969.15
17:00 | 340 | 6032.1 | 1788 | 7820.1
17:30 | 350 | 6007.1 | 1801 | 7808.1
18:00 | 360 | 5982.1 | 1814 | 7796.1
18:30 | 410 | 6345.05 | 2101.5 | 8446.55
19:00 | 460 | 6708 | 2389 | 9097
19:30 | 560 | 7110 | 2599 | 9709
20:00 | 620 | 7121 | 2633 | 9754 |  |  |  | Executive Engineer
20:30 | 640 | 7278.5 | 2645.5 | 9924 |  |  |  | Network Operation Division
21:00 | 660 | 7436 | 2658 | 10094
21:30 | 645 | 7392.5 | 2653.5 | 10046
22:00 | 630 | 7349 | 2649 | 9998 |  |  |  |  | Page 6 of 7
22:30 | 585 | 7170 | 2531 | 9701
23:00 | 540 | 6991 | 2413 | 9404
23:30 | 590 | 6993 | 2389 | 9382
24:00 | 640 | 6995 | 2365 | 9360
10094 MW (21:00 )
8081.5 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2018-06-25 |  | Energy | 200306382
[10 empty] | 2018-06-25 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3485 | 473 | 1823 | 1910 | 230 | 168 | 1121 | 0 | 150
0:30 | 3469 | 475.5 | 1946.5 | 1774.5 | 230 | 166.5 | 1089 | 0 | 146 | Date: | 2018-06-25
1:00 | 3453 | 478 | 2070 | 1639 | 230 | 165 | 1057 | 0 | 142
1:30 | 3449 | 478 | 2045.5 | 1527 | 230.5 | 165 | 987 | 0 | 139 | [7 empty] | Total Energy | 200.3064 | Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
2:00 | 3445 | 478 | 2021 | 1415 | 231 | 165 | 917 | 0 | 136 | [7 empty] | Energy not Served | 0
2:30 | 3495.5 | 478 | 2012.5 | 1225 | 230.5 | 165 | 876.5 | 0 | 133 | [7 empty] | Energy Requirement | 200.3064
3:00 | 3546 | 478 | 2004 | 1035 | 230 | 165 | 836 | 0 | 130
3:30 | 3552.5 | 478 | 1965.5 | 947 | 230 | 166 | 805.5 | 0 | 126 | [6 empty] | Shortage
4:00 | 3559 | 478 | 1927 | 859 | 230 | 167 | 775 | 0 | 122
4:30 | 3553.5 | 478 | 1840.5 | 814.5 | 230.5 | 167 | 734 | 0 | 116
5:00 | 3548 | 478 | 1754 | 770 | 231 | 167 | 693 | 0 | 110
5:30 | 3453.5 | 478 | 1528.5 | 712.5 | 231 | 167 | 647.5 | 0 | 105
6:00 | 3359 | 478 | 1303 | 655 | 231 | 167 | 602 | 0 | 100
6:30 | 3331.5 | 478 | 1306.5 | 643.5 | 229 | 167 | 609.5 | 0 | 98 |  |  |  |  | Coal
7:00 | 3304 | 478 | 1310 | 632 | 227 | 167 | 617 | 0 | 96
7:30 | 3387 | 478 | 1335 | 613 | 224 | 167 | 595.5 | 0 | 99 |  |  |  | Oil |  |  |  | ,
8:00 | 3470 | 478 | 1360 | 594 | 221 | 167 | 574 | 0 | 102
8:30 | 3519.5 | 478 | 1506 | 645.5 | 221 | 167 | 624 | 0 | 106
9:00 | 3569 | 478 | 1652 | 697 | 221 | 167 | 674 | 0 | 110
9:30 | 3561.5 | 477.5 | 1709.5 | 787 | 223.5 | 167.5 | 668.5 | 0 | 113
10:00 | 3554 | 477 | 1767 | 877 | 226 | 168 | 663 | 0 | 116
10:30 | 3544.5 | 477.5 | 1783.5 | 903.5 | 223 | 168 | 665 | 0 | 116
11:00 | 3535 | 478 | 1800 | 930 | 220 | 168 | 667 | 0 | 116
11:30 | 3510.5 | 478 | 1812 | 1011.5 | 221.5 | 168 | 683.5 | 0 | 112
12:00 | 3486 | 478 | 1824 | 1093 | 223 | 168 | 700 | 0 | 108
12:30 | 3373.5 | 477.5 | 1934.5 | 1153.5 | 224 | 168 | 687.5 | 0 | 111
13:00 | 3261 | 477 | 2045 | 1214 | 225 | 168 | 675 | 0 | 114
13:30 | 3261 | 477 | 2045 | 1214 | 225 | 168 | 675 | 0 | 114
14:00 | 3261 | 477 | 2045 | 1214 | 225 | 168 | 675 | 0 | 114
14:30 | 3275.5 | 477.5 | 2004.5 | 1246 | 227 | 168 | 728.5 | 0 | 118
15:00 | 3290 | 478 | 1964 | 1278 | 229 | 168 | 782 | 0 | 122
15:30 | 3240.5 | 478 | 1860.5 | 1369.5 | 229 | 168 | 748 | 0 | 121
16:00 | 3191 | 478 | 1757 | 1461 | 229 | 168 | 714 | 0 | 120
16:30 | 3130 | 478 | 1695.5 | 1444.5 | 228.5 | 168 | 705.5 | 0 | 119
17:00 | 3069 | 478 | 1634 | 1428 | 228 | 168 | 697 | 0 | 118
17:30 | 3026.5 | 478 | 1639.5 | 1432.5 | 228 | 168 | 715.5 | 0 | 120
18:00 | 2984 | 478 | 1645 | 1437 | 228 | 168 | 734 | 0 | 122
18:30 | 3137 | 478 | 1714.5 | 1640 | 227.5 | 168 | 947.5 | 0 | 134
19:00 | 3290 | 478 | 1784 | 1843 | 227 | 168 | 1161 | 0 | 146
19:30 | 3216 | 477 | 1827 | 2343 | 227 | 168 | 1297 | 0 | 154
20:00 | 3280 | 477 | 1758 | 2393 | 228 | 168 | 1292 | 0 | 158
20:30 | 3398.5 | 477.5 | 1788 | 2401.5 | 223.5 | 168 | 1309 | 0 | 158
21:00 | 3517 | 478 | 1818 | 2410 | 219 | 168 | 1326 | 0 | 158
21:30 | 3496.5 | 477.5 | 1807.5 | 2394 | 224 | 168 | 1319.5 | 0 | 159
22:00 | 3476 | 477 | 1797 | 2378 | 229 | 168 | 1313 | 0 | 160
22:30 | 3454 | 475 | 1786.5 | 2190.5 | 229.5 | 168 | 1239.5 | 0 | 158
23:00 | 3432 | 473 | 1776 | 2003 | 230 | 168 | 1166 | 0 | 156
23:30 | 3458.5 | 473 | 1799.5 | 1956.5 | 230 | 168 | 1143.5 | 0 | 153 | Max Temp. in Dhaka |  | 31.2° C
24:00 | 3485 | 473 | 1823 | 1910 | 230 | 168 | 1121 | 0 | 150
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
Note on W13: Author:

## Generation
,. | 2018-06-25
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 85 | 85 | 85 | 87 | 87 | 87 | 87 | 87 | 87 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 2072091
2 | Kaptai Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1913500
3 | Chittagong ST-1 (Raozan)
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 26 | 25 | 26 | 475020
6 | Sikalbaha 225MW (Gas)
7 | Sikalbaha 225MW (Oil) | 202 | 200 | 201 | 204 | 201 | 199 | 216 | 186 | 205 | 195 | 202 | 220 | 188 | 188 | 210 | 202 | 201 | 201 |  | 215 | 201 | 201 | 209 | 201 | 202 | 223 | 4871875
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas)
10 | Sikalbaha GT 150MW (Oil) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 30 | 30 | 30 | 31 | 50 | 50 | 50 | 135 | 60 | 50 | 50 |  | 135 | 110 | 90 | 135 | 135 | 135 | 135 | 1633952
| Dohazari Peaking | 79 | 47 | 16 | 16 | 16 | 16 | 0 | [19 empty] | 207545
12 | Hathazari peaking | 55 | 55 | 24 | 0 | [13 empty] | 0 |  | 63 | 66 | 66 | 66 | 65 | 65 | 65 | 533552
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW | [17 empty] | 0 |  | 23 | 50 | 48 | 47 | 48 | 0 |  | 167320
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 130 | 132 | 130 | 130 | 130 | 80 | 80 | 125 | 197 | 191 | 192 | 162 | 101 | 60 | 97 | 97 | 60 | 60 |  | 98 | 62 | 37 | 97 | 100 | 38 | 62 | 2718000
17 | Siddhirganj CCPP-335 MW | 192 | 192 | 192 | 191 | 188 | 156 | 120 | 120 | 120 | 120 | 160 | 194 | 194 | 190 | 190 | 190 | 190 | 110 |  | 110 | 110 | 110 | 150 | 180 | 180 | 180 | 4138747
18 | Summit Gazipur | 200 | 200 | 100 | 50 | 17 | 15 | 15 | 15 | 15 | 15 | 15 | 43 | 49 | 49 | 49 | 98 | 98 | 98 |  | 178 | 279 | 279 | 286 | 300 | 300 | 300 | 2697271
19 | Ashuganj 195MW Modular | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 185 | 195 | 195 | 78 | 78 | 78 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 2258182
20 | Ghorasal ST: Unit-1,2 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 0 | [18 empty] | 261000
21 | Ghorasal ST: Unit-3 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2870280
22 | Ghorasal ST: Unit-4
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 280 | 280 | 280 | 280 | 280 | 200 | 200 | 200 | 345 | 365 | 365 | 365 | 365 | 300 | 300 | 300 | 250 | 250 |  | 300 | 350 | 365 | 365 | 365 | 365 | 365 | 8319163
26
28 | Ashuganj ST: Unit- 3 | 70 | 0 | [24 empty] | 138404
29 | Ashuganj ST: Unit- 4 | 70 | 95 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 150 | 150 | 150 | 150 | 150 | 150 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2750810
30 | Ashuganj ST: Unit- 5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 130 | 130 | 130 | 130 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2584644
32 | Ashuganj Engines TSK | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 36 | 39 | 39 | 36 | 36 | 36 | 36 | 36 | 33 | 33 |  | 33 | 28 | 33 | 33 | 32 | 32 | 32 | 825336
33 | Ashuganj CCPP 225 MW | 155 | 183 | 184 | 183 | 183 | 190 | 205 | 205 | 218 | 198 | 200 | 184 | 186 | 193 | 178 | 184 | 183 | 183 |  | 206 | 183 | 183 | 200 | 183 | 195 | 217 | 4632000
34 | Ashuganj CCPP(South) | 301 | 301 | 301 | 301 | 301 | 312 | 334 | 334 | 334 | 320 | 323 | 301 | 300 | 316 | 327 | 272 | 250 | 250 |  | 287 | 272 | 272 | 327 | 300 | 315 | 349 | 7430500
| Ashuganj CCPP(North) | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 160 | 200 | 203 | 185 | 15 | 14 | 20 | 20 | 100 | 100 |  | 160 | 164 | 203 | 222 | 194 | 190 | 130 | 3613700
35 | Ashuganj (Precision) 55MW
36 | Chandpur CCPP
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 345 | 345 | 345 | 345 | 340 | 340 | 355 | 375 | 375 | 375 | 360 | 350 | 375 | 330 | 355 | 360 | 349 | 356 |  | 372 | 356 | 368 | 370 | 350 | 350 | 350 | 8635390
40 | Meghnaghat CCPP 450MW | 400 | 400 | 400 | 400 | 400 | 340 | 340 | 370 | 400 | 400 | 400 | 380 | 360 | 300 | 340 | 340 | 340 | 340 |  | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 8341250
41 | Haripur Power CCPP 360MW | 354 | 321 | 311 | 301 | 301 | 262 | 266 | 300 | 302 | 260 | 231 | 231 | 231 | 231 | 227 | 222 | 211 | 206 |  | 206 | 192 | 191 | 180 | 172 | 171 | 182 | 5932000
42 | Mymensingh RPCL 210MW | 129 | 129 | 128 | 129 | 129 | 129 | 120 | 98 | 98 | 98 | 98 | 98 | 82 | 65 | 64 | 64 | 64 | 64 |  | 64 | 65 | 65 | 66 | 73 | 69 | 69 | 2215320
43 | Haripur NEPC 110MW | [16 empty] | 0 | 13 |  | 13 | 40 | 40 | 40 | 40 | 0 |  | 151300
44 | Fenchugonj CCPP-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 89 | 59 | 60 | 60 | 60 | 60 | 54 | 52 | 56 | 52 |  | 52 | 52 | 54 | 54 | 58 | 58 | 60 | 1352000
45 | Fenchugonj CCPP-2 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 143256
46 | Shajibazar 330 MW | 146 | 162 | 283 | 302 | 302 | 319 | 322 | 332 | 334 | 314 | 307 | 314 | 307 | 334 | 322 | 303 | 304 | 303 |  | 338 | 307 | 313 | 321 | 318 | 315 | 332 | 6697473
47 | Shahjibazar GT: Unit- 8, 9 | 31 | 31 | 31 | 31 | 31 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 31 | 30 | 30 | 30 | 29 | 31 |  | 30 | 31 | 31 | 29 | 31 | 30 | 30 | 720000
48 | Shahjibazar 86MW | 86 | 86 | 86 | 50 | 10 | 10 | 10 | 10 | 50 | 84 | 84 | 84 | 86 | 86 | 86 | 84 | 86 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 1669440
49 | Shahjibazar (EPL) 50MW | 46 | 46 | 46 | 46 | 45 | 5 | 5 | 5 | 45 | 45 | 44 | 46 | 45 | 45 | 46 | 46 | 20 | 20 |  | 20 | 46 | 47 | 47 | 47 | 47 | 47 | 881640
50 | Sylhet GT 150 MW | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 79 | 79 | 78 | 80 | 78 | 80 | 78 | 78 | 78 | 78 |  | 78 | 78 | 78 | 78 | 79 | 80 | 80 | 1927290
51 | Sylhet GT 20 MW
52 | Sylhet (EPL) 50MW | 44 | 44 | 44 | 44 | 44 | 7 | 8 | 7 | 43 | 42 | 42 | 42 | 42 | 44 | 44 | 44 | 44 | 44 |  | 44 | 44 | 44 | 42 | 45 | 44 | 44 | 938280
53 | Sylhet (Desh) 10MW | 10 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 7 | 7 | 7 | 5 | 9 | 9 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 229500
54 | Hobiganj 11MW | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 194784
55 | Fenchugonj (Barakatullah) 51MW | 50 | 50 | 50 | 50 | 50 | 5 | 5 | 5 | 31 | 45 | 48 | 48 | 47 | 50 | 50 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 1068000
56 | Shahjahanulla 25 MW | 21 | 15 | 15 | 15 | 17 | 21 | 22 | 22 | 22 | 15 | 15 | 15 | 15 | 15 | 15 | 20 | 20 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 456792
57 | Summit Bibiana- 2 | 300 | 295 | 280 | 286 | 285 | 260 | 315 | 320 | 320 | 320 | 320 | 310 | 320 | 280 | 320 | 280 | 280 | 290 |  | 300 | 280 | 260 | 310 | 290 | 270 | 310 | 7592600
58 | Southern 55MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 36 | 17 | 36 | 36 | 36 | 36 | 36 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 36 | 822178
59 | Sikalbaha (Energis) | 51 | 51 | 51 | 51 | 24 | 24 | 24 | 0 | 0 | 17 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 42 | 42 | 981600
60 | Barabkunda (Regent) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 14 | 13 | 13 | 13 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 378144
61 | Narshingdi (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 |  | 0 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 428832
62 | Tangail (Doreen) 22MW | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 17 | 17 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 448524
63 | Tripura | 142 | 136 | 130 | 122 | 110 | 100 | 96 | 102 | 110 | 116 | 116 | 108 | 114 | 118 | 122 | 120 | 118 | 122 |  | 146 | 154 | 158 | 158 | 160 | 156 | 150 | 3070080
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 38 | 17 | 7 | 5 | 5 | 3 | 11 | 5 | 3 | 2 | 6 | 11 |  | 19 | 21 | 27 | 31 | 31 | 31 | 30 | 557280
65 | Feni (Doreen) 22MW | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 447336
66 | Feni, Mohipal (Doreen) | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 0 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 235440
67 | Jangalia (Summit) 33MW | 33 | 33 | 8 | 8 | 8 | 8 | 8 | 8 | 15 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 657100
68 | Summit Comilla 25MW | 20 | 20 | 20 | 20 | 20 | 20 | 12 | 12 | 9 | 10 | 10 | 18 | 18 | 18 | 18 | 18 | 18 | 17 |  | 17 | 17 | 17 | 0 | 19 | 20 | 22 | 389630
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 32 | 30 | 30 | 30 | 30 | 30 | 28 | 30 | 30 | 31 | 31 | 28 | 28 | 28 | 10 |  | 26 | 26 | 26 | 32 | 22 | 32 | 32 | 680940
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 789800
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 22 | 22 | 22 | 22 | 22 |  | 22 | 31 | 31 | 31 | 31 | 31 | 31 | 758700
73 | Ghorashal (Regent) | 111 | 111 | 111 | 111 | 111 | 25 | 25 | 25 | 25 | 22 | 45 | 99 | 98 | 101 | 102 | 103 | 101 | 101 |  | 102 | 102 | 75 | 87 | 87 | 87 | 86 | 1969636
76 | Siddhirganj (Desh) | [11 empty] | 0 | 7 | 0 | [5 empty] | 0 | 5 | 10 | 17 | 17 | 0 |  | 63360
77 | Siddhirganj (Dutch Bangla) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 20 | 50 | 50 | 50 | 50 | 50 |  | 55 | 70 | 92 | 93 | 93 | 93 | 93 | 940800
78 | Gazipur (RPCL) | 51 | 51 | 35 | 35 | 34 | 34 | 34 | 34 | 44 | 51 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 44 |  | 42 | 50 | 50 | 50 | 50 | 51 | 51 | 1102896
79 | Kodda 150MW | 100 | 64 | 64 | 64 | 60 | 16 | 16 | 16 | 98 | 98 | 98 | 98 | 98 | 90 | 82 | 82 | 82 | 82 |  | 90 | 140 | 149 | 149 | 149 | 149 | 115 | 2121600
80 | Jamalpur 95MW | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 24 | 24 | 24 | 24 | 8 | 8 | 8 | 8 | 8 |  | 15 | 72 | 72 | 72 | 72 | 40 | 8 | 516600
81 | Lakdhanvi 52 MW | [17 empty] | 0 |  | 4 | 8 | 8 | 8 | 8 | 0 |  | 38011
82 | Madanganj 102MW | 50 | 15 | 15 | 15 | 15 | 0 | [20 empty] | 92040
83 | Pagla (DPA ) | [8 empty] | 0 | 10 | 11 | 11 | 10 | 10 | 10 | 11 | 10 | 10 |  | 10 | 50 | 51 | 50 | 21 | 11 | 11 | 236280
84 | B.Baria (Aggreko) 85MW | 85 | 85 | 85 | 50 | 10 | 10 | 10 | 10 | 50 | 86 | 85 | 85 | 86 | 85 | 86 | 86 | 50 | 50 |  | 86 | 85 | 86 | 86 | 85 | 86 | 85 | 92040
85 | Keraniganj (Powerpac) 100MW | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 50 | 10 | 10 | 10 | 10 | 10 |  | 40 | 60 | 60 | 60 | 60 | 10 | 0 | 549840
86 | Meghnaghat CCPP(Summit) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2556596
87 | Meghnaghat (IEL) | 24 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 34 | 55 | 55 | 55 | 55 | 55 |  | 61 | 93 | 92 | 100 | 100 | 100 | 100 | 1020480
88 | Ghorashal 78MW (MAX) | 74 | 74 | 74 | 73 | 60 | 40 | 30 | 30 | 30 | 30 | 40 | 73 | 71 | 71 | 72 | 60 | 40 | 40 |  | 60 | 70 | 74 | 74 | 73 | 73 | 74 | 1477056
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 53 | 53 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 266000
91 | Juldah (Acorn) | 80 | 80 | 68 | 68 | 80 | 80 | 80 | 80 | 80 | 80 | 68 | 68 | 68 | 80 | 80 | 80 | 68 | 68 |  | 68 | 72 | 80 | 80 | 80 | 80 | 80 | 1745880
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 50 | 50 | 5 | 5 | 5 | 25 | 47 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1037000
93 | Ashuganj (Midland) 51MW | 51 | 51 | 51 | 51 | 6 | 6 | 6 | 6 | 10 | 30 | 51 | 51 | 51 | 51 | 51 | 41 | 42 | 42 |  | 42 | 42 | 42 | 42 | 51 | 51 | 51 | 888347
94 | Gagnagar (Orion) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 20 | 32 | 8 | 16 | 16 | 16 | 16 |  | 16 | 58 | 58 | 58 | 58 | 7 | 7 | 472320
95 | Patenga 50MW | 44 | 44 | 44 | 44 | 44 | 44 | 20 | 18 | 22 | 37 | 38 | 38 | 45 | 44 | 44 | 44 | 44 | 44 |  | 44 | 44 | 44 | 44 | 38 | 38 | 37 | 971520
96 | Chittagong ECPV 108 MW | 99 | 99 | 83 | 53 | 25 | 25 | 25 | 12 | 13 | 58 | 53 | 57 | 62 | 65 | 90 | 99 | 99 | 99 |  | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 1706880
97 | Katpotti 51 MW | 40 | 39 | 39 | 6 | 6 | 6 | 6 | 6 | 17 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 |  | 39 | 39 | 39 | 37 | 39 | 39 | 39 | 781056
98 | Bosila 108MW | 91 | 91 | 42 | 8 | 8 | 8 | 8 | 8 | 51 | 51 | 50 | 89 | 89 | 90 | 91 | 91 | 91 | 91 |  | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 1553280
99 | Madanganj-55 MW | 30 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 25 | 30 | 30 |  | 30 | 55 | 55 | 55 | 55 | 15 | 15 | 595118
100 | Northern 55 MW | 55 | 55 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 36 | 36 | 36 | 37 | 37 | 56 | 56 | 56 |  | 56 | 56 | 56 | 56 | 56 | 55 | 55 | 952257
101 | Kushiara 163 MW CCPP GT | 130 | 130 | 130 | 130 | 100 | 100 | 100 | 100 | 163 | 163 | 163 | 130 | 163 | 163 | 130 | 130 | 130 | 130 |  | 130 | 163 | 130 | 130 | 130 | 130 | 130 | 3242372
102 | Sarishabari (Solar) | [5 empty] | 0 | 0.3 | 0.3 | 0.7 | 1 | 1.2 | 1.5 | 2 | 1 | 0.3 | 0.2 | 0.1 | 0.1 | [8 empty] | 8928
103 | Banco Energy 54MW | 54 | 54 | 18 | 18 | 18 | 0 |  |  | 0 | 18 | 18 | 36 | 36 | 36 | 36 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 834480
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 130 | 100 | 93 | 72 | 50 | 7 | 7 | 7 | 7 | 50 | 50 | 100 | 100 | 100 | 150 | 150 | 150 | 151 |  | 180 | 180 | 180 | 180 | 180 | 185 | 180 | 2553600
112 | Aggreko Aurahati 100MW | 102 | 102 | 101 | 101 | 103 | 102 | 103 | 104 | 103 | 95 | 102 | 103 | 103 | 103 | 103 | 104 | 104 | 105 |  | 106 | 104 | 104 | 105 | 100 | 102 | 104 | 2476590
113
114
115
116
117
118 | Eastern Zone Total | 6783 | 6548 | 6282 | 6026 | 5732 | 5073 | 5096.3 | 5070.3 | 5843.7 | 6066 | 6276.2 | 6426.5 | 6469 | 6233 | 6439.3 | 6238.2 | 6032.1 | 5982.1 |  | 6708 | 7110 | 7121 | 7436 | 7349 | 6991 | 6995 | 150367654
120
121
122 | Khulna 60MW
123 | Khulna (KPCL-1 & 3) | 27 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 103 | 110 | 110 | 106 | 106 | 106 | 69 | 557920
124 | Khulna (KPCL-2) | 107 | 36 | 24 | 16 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 32 |  | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 1061760
125
126 | Khulna (Aggreko) 55MW | [17 empty] | 0 |  | 11 | 46 | 53 | 53 | 51 |  |  | 146180
127 | Faridpur Peaking | 48 | 21 | 18 | 18 | 0 | [11 empty] | 0 | 18 |  | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 384000
128 | Khulna CCPP 225MW | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 135 | 150 | 140 | 120 | 120 | 120 | 120 | 3060480
129
130
131
132
133
| Summit Barisal 110 MW | 64 | 48 | 16 | 16 | 16 | 16 | 16 | 16 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 32 |  | 48 | 72 | 80 | 80 | 80 | 80 | 64 | 846720
Barisal GT: Unit-1, 2
136 | Bhola Aggreko 95MW | 97 | 98 | 98 | 98 | 95 | 54 | 13 | 13 | 14 | 52 | 54 | 54 | 94 | 95 | 95 | 70 | 35 | 35 |  | 92 | 95 | 97 | 97 | 96 | 96 | 97 | 1741477
137 | Bhola CCPP 194MW | 192 | 191 | 191 | 190 | 187 | 191 | 193 | 193 | 193 | 195 | 195 | 194 | 194 | 193 | 193 | 183 | 173 | 171 |  | 191 | 186 | 190 | 192 | 191 | 192 | 191 | 4631053
| Bhola (Venture) 33MW | 24 | 13 | 20 | 19 | 19 | 14 | 12 | 11 | 12 | 14 | 16 | 16 | 16 | 16 | 17 | 17 | 17 | 18 |  | 25 | 27 | 25 | 31 | 30 | 29 | 29 | 447913
140 | Bangla Trak Noapara | [17 empty] | 0 |  | 19 | 40 | 40 | 40 | 40 |  |  | 149760
141 | Noapara (KZA) 40MW | 40 | 40 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 33 | 8 | 8 |  | 40 | 40 | 40 | 40 | 33 |  | 24 | 398625
142 | Gopalganj Peaking | 32 | 32 | 31 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 15 | 22 | 25 | 25 | 35 |  | 45 | 55 | 76 | 72 | 66 | 66 | 65 | 682368
143 | Bheramara GT-1,2,3
144
145 | Bheramara HVDC | 478 | 478 | 478 | 478 | 478 | 478 | 478 | 478 | 478 | 477 | 478 | 478 | 477 | 477 | 478 | 478 | 478 | 478 |  | 478 | 477 | 477 | 478 | 477 | 473 | 473 | 11577455
146 | Bheramara 360 MW | 274 | 274 | 274 | 274 | 278 | 215 | 140 | 290 | 120 | 120 | 0 |  | 0 | 140 | 140 | 125 | 120 | 110 |  | 110 | 100 | 110 | 150 | 150 | 150 | 150 | 3856896
147
148
149 | Barapukuria Unit-1
150 | Barapukuria Unit-2 | 70 | 71 | 70 | 70 | 71 | 71 | 67 | 63 | 63 | 67 | 62 | 64 | 66 | 67 | 69 | 69 | 68 | 68 |  | 67 | 67 | 68 | 59 | 69 | 71 | 70 | 1625890
151 | Barapukuria Unit-3 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 158 | 158 | 159 | 158 | 159 | 159 | 159 | 160 | 160 | 160 | 160 |  | 160 | 160 | 160 | 160 | 160 | 159 | 160 | 3895700
152 | Baghabari GT 71MW
153 | Baghabari GT 100MW
156 | Baghabari Peaking 50MW | [17 empty] | 0 |  | 43 | 43 | 43 | 43 | 43 | 43 | 0 | 224520
| Sirajgonj Unit-1 225MW (Gas) | 183 | 181 | 183 | 182 | 178 | 175 | 190 | 197 | 196 | 196 | 190 | 193 | 198 | 183 | 196 | 182 | 169 | 169 |  | 181 | 183 | 176 | 182 | 182 | 172 | 185 | 4664409
157 | Sirajgonj Unit-1 225MW (Oil)
158 | Sirajgonj Unit-2 225MW (Gas)
| Sirajgonj Unit-2 225MW (Oil) | 174 | 173 | 175 | 173 | 170 | 168 | 182 | 189 | 188 | 187 | 183 | 179 | 186 | 175 | 188 | 174 | 168 | 168 |  | 180 | 180 | 174 | 180 | 180 | 171 | 186 | 4463972
Sirajgonj Unit-3 225 MW(Gas)
159 | Sirajgonj Unit-3 225 MW(Oil)
160 | Bera Peaking | 37 | 37 | 37 | 37 | 0 | [11 empty] | 0 | 9 |  | 37 | 37 | 37 | 38 | 38 | 0 |  | 331228
161 | Bogra (GBB) | 22 | 22 | 22 | 22 | 22 | 14 | 18 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 21 | 22 | 22 | 498000
162 | Bogra (EPL) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 11 | 11 | 12 | 12 | 12 | 12 | 251928
163 | Ullapara (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0 | 5 | 5 | 5 | 5 | 5 | 8 | 8 |  | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 150174
164 | Amnura 50MW | 40 | 35 | 40 | 40 | 40 | 12 | 12 | 12 | 12 | 25 | 25 | 35 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 842640
165 | Katakhali (Northern) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 929888
166 | Katakhali Peaking | [17 empty] | 0 |  | 36 | 45 | 47 | 46 | 46 | 45 | 45 | 252041
167 | Santahar Peaking | 42 | 0 | [15 empty] | 0 |  | 30 | 43 | 43 | 43 | 43 | 42 | 42 | 268159
168 | Rajlanka 52 MW | 43 | 43 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 43 | 43 | 43 | 43 | 43 | 43 | 454560
169 | Chapainawabganj-100 MW | 100 | 100 | 100 | 68 | 68 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 51 | 51 | 51 |  | 51 | 100 | 101 | 101 | 102 | 66 | 63 | 1340012
170
171
172 | Rangpur GT | [17 empty] | 0 |  | 17 | 17 | 16 | 16 | 16 | 0 |  | 64000
173 | Saidpur GT | 18 | 18 | 0 | [14 empty] | 0 |  | 17 | 17 | 18 | 18 | 18 | 19 | 19 | 139000
175
176
177
178 | Western Zone Total | 2451 | 2260 | 2142 | 2091 | 2019 | 1822 | 1735 | 1896 | 1725 | 1783 | 1639 | 1655 | 1712 | 1834 | 1872 | 1880 | 1788 | 1814 | 0 | 2389 | 2599 | 2633 | 2658 | 2649 | 2413 | 2365 | 49938728
177
178 | Western Zone Total | 1739 | 1733 | 1361 | 1359 | 1275 | 1200 | 1113 | 1104 | 1237 | 1525 | 1361 | 1364 | 1267 | 1221 | 1288 | 1290 | 1492 | 1587 | 0 | 2291 | 2149 | 2113 | 2138 | 2057 | 2047 | 2028 | 37879953