## Schedule B1
Schedule B1: Plant & Equipment supplied from abroad
New 230/132/33 kV Substation at KACHUA
Item No. | Description of Equipment Requirement |  | Unit | Quantity | Code | Foreign Currency (in……….)
[6 empty] | Unit Price | Total Price
[6 empty] | CIP | CIP
|  |  |  | (1) |  | (2) | (3) = (1) x (2)
A | 230 kV switchgear, equipment connection and steel structures
1A1 | 245kV GIS Line Feeder Bays, each comprising: |  | Set | 8
| i. | 245kV, 4000A, 50kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 245kV, 3150A, 50kA/3s, three phase, single pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 245kV, 3150A, 50kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 245kV, 50kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 245kV, 3150A, 50kA/3s three phase line disconnector integral with high speed earth switch complete with motor operating mechanism | sets | 1
| vi | 245kV, 50kA/3s single phase, 5-core, current transformer | No. | 3
| vii. | 245kV single phase, 3 core, Class 0.2, 10VA for Metering and Class 3P,15VA for Protection, voltage transformer | No. | 3
| viii. | 245kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Cubicle | set | 1
| x | Offline PD Monitoring facility in compartments | Lot | 1
| xi | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
1A2 | 245kV GIS Auto Transformer Feeder Bays, each comprising: |  | Set | 2
| i. | 245kV, 4000A, 50kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 245kV, 3150A, 50kA/3s, three phase, Gang pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 245kV, 3150A, 50kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 245kV, 50kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 245kV, 3150A, 50kA/3s, three phase line side disconnector with earth switch complete with motor operating mechanism | sets | 1
| vi | 245kV, 50kA/3s, single phase, 5-core, current transformer | No. | 3
| vii. | 245kV single phase, 3 core, Class 0.2,10VA for Metering and Class 3P,15VA for Protection, voltage transformer | No. | 3
| viii. | 245kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Cubicle | No. | 1
| x | Offline PD Monitoring facility in compartments | Lot | 1
| xi. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for single-core cables, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
1A3 | 245kV Bus Coupler Bays , each comprising: |  | set | 1
| i. | 245kV, 4000A, 50kA/3s, three phase double busbar | Lot | 1
| ii. | 245kV, 50kA/3s, three phase, gang pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| ii. | 245kV, 50kA/3s, three phase busbar disconnector complete with motor operating mechanism | Set | 2
| iv. | 245kV, 50kA/3s, three phase, three position earth switch complete with motor operating mechanism, on either side of circuit breaker. | Set | 2
| v. | 245kV, 50kA/3s, single phase, 3-core, current transformer | No. | 3
| vi. | 245kV, 50kA/3s, single phase, 2-core, current transformers | No. | 3
| vii. | Local Control Cubicle | set | 1
| viii. | Offline PD Monitoring facility in compartments | Lot | 1
| ix. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, sepecial equipment as per specification etc. as appropriate | Lot | 1
1A4 | 245kV GIS Double Busbar with VT/ES, each comprising: |  | Set | 1
| i. | 245kV, 4000A, 50kV/3s, three phase double busbars | Lot | 1
| ii. | 245kV single phase, 2 core, Class 0.2, 10VA for Metering and Class 3P, 15VA for Protection, voltage transformer | No. | 6
| iii. | 245kV, 50kA/3s, three phase, three position earth switches complete with motor operating Mechanism | set | 2
| iv. | Offline PD Monitoring facility in compartments | Lot | 1
| v. | Local Control Cubicle | No. | 1
1A5 | 216kV rated voltage, 192kV(rms) continuous operating voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase surge arresters |  | No. | 30
1A6 | Rigid tubular conductor and/or stranded conductors including accessories for each connection as required for completing 230kV GIS Switchyard
| i. | Tubular Conductor | Lot | 1
| ii | Flexible Conductor | Lot | 1
1A7 | Insulator and fittings including all necessary clamps and connectors as required for completing 230kV GIS Switchyard
| i | Insulator | Lot | 1
| ii | Fittings & Clamps_Connector | Lot | 1
| ii | Nut-bolt | Lot | 1
| iv. | Cable trench including fitting, fixing accessories | Lot | 1
1A8 | Steel gantry, having double tier for each double circuit of 230kV Transmission Line & Equipment support Structure including all necessary accessories required for completing 230kV GIS Switchyard
| a) | Steel Structure
| i. | Gantry Column | No. | 10
| ii. | Beam | No. | 8
| iii. | Nut & Bolts | Lot | 1
| b) | Equipment Structure
| i. | LA | No. | 30
| ii. | CVT |  | Deleted
1B | 145 kV Indoor Type Gas Insulated Switchgear (GIS), equipment connection and steel structures
145 kV Indoor Type Gas Insulated Switchgear (GIS),
Deleted
145 kV Outdoor Type Air Insulated Switchgear (AIS)
1B1 | SF6 Circuit breaker,1600A,40kA/1s, live tank, single pole operating for Line Bay |  | set | 2
1B2 | SF6 Circuit breaker,2500A, 40kA/1s,live tank, gang operating for Transformer Bay |  | set | 2
1B3 | Disconnector switch without E/S, 1600A,40kA/1s for Line bay |  |  | 4
1B4 | Disconnector switch with E/S, 1600A,40kA/1s for Line Bay |  |  | 2
1B5 | Disconnector switch without E/S, 2500A,40kA/1s for Transformer Bay |  | set | 4
1B6 | Disconnector switch with E/S, 2500A,40kA/1s for Transformer Bay |  | set | 2
1B7 | Single phase current transformer,1600-3200/1, 5-core,40kA/1s for Line Bay |  | nos. | 6
1B8 | Single phase current transformer,2000-3200/1, 5-core,40kA/1s for tansformer bay |  | nos. | 6
1B9 | Single phase voltage transformer (VT), 3-core |  | nos. | 12
1B10 | 120kV rated voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase surge arresters |  | No. | 12
1B11 | Rigid tubular bus and/or stranded conductors including accessories for each connection as required for completing 145kV GIS Switchyard
| i. | Tubular Conductor | Lot | 1
| ii | Flexible Conductor | Lot | 1
1B12 | insulator and fittings including all necessary clamps and connectors as required for completing 145kV GIS Switchyard
| i | Insulator | Lot | 1
| ii | Fittings & Clamps_Connector | Lot | 1
| ii | Nut-bolt | Lot | 1
| iv. | Cable trench including fitting, fixing accessories | Lot | 1
1B13 | steel gantry, having double tier for each double circuit of 145kV Transmission Line including all necessary accessories required for completing 145kV GIS Switchyard
| a) | Steel Structure
| i. | _Gantry Column | No. | 8
| ii. | Beam
| 1) | at Bus Height | No. | 3
| 2) | at Jack-Bus Height | No. | 6
| iii. | Nut & Bolts | Lot | 1
| b) | Equipment Structure
| i. | CB | set | 4
| ii. | DS without ES | set | 8
| ii. | DS with ES | set | 4
| iv. | Bus ES | Deleted
| v. | CT | nos. | 12
| vi. | CVT/IVT | nos. | 12
| vii. | LA | nos. | 12
1C | 33 kV Switchgear, equipment connection and steel structures
One (1) set of complete equipment for switchgear 33 kV shall be designed, supplied, delivered, installed, tested and commissioned, under this contract, comprise the following:
1C1 | Circuit Breaker 36 kV, 630 A, 31.5kA/1s, 50 Hz, 170/70 kV BIL, three pole, vacuum type, for outdoor installation with one spring-stored energy operating mechanism |  | Set | 2
1C2 | Disconnector 36 kV, 630 A, 31.5kA/1s, 50 Hz, 170/70 kV BIL, three pole, single vertical break, post type, motor operated
| i) | DS without ES | set | 2
| ii) | DS with ES | set | 2
1C3 | Current transformer 36 kV, 31.5kA/1s, 50Hz, 170/70 kV BIL, single phase, 10/1, 630-1250/1 , 2-core, post type |  | nos. | 6
1C4 | Voltage transformer 36kV, 50Hz, 170/70 kV BIL, single phase, 33/V3 / 110/V3 / 110/V3 kV/V/V, 2 secondary windings, inductive type |  | nos. | 6
1C5 | Surge arrester 36 kV, 30 kV continuous operating voltage, 10 kA nominal discharge current, 50 Hz, single phase, gapless, metal oxide type |  | nos. | 6
1C6 | Gantry steel structures for Bus & Equipment, Conductor for 36kV Bus bar & equipment, 36kV XLPE cable for Tertiary side connection from power trans-former, Insulator and fittings including all necessary clamps and connectors, cable trench required to complete 33kV switchyard.
| i. | Flexible conductor for Bus & Equipment connection | Lot | 1
| ii. | Insulators and fittings incl. all necessary clamps and connectors,Nut-Bolt required for completing 33 kV switchyard | Lot | 1
| iii. | Gantry steel structures for Bus
| a) | Beam | No | 4
| b) | Column | No | 6
| iv. | steel structures for equipment supports required for completing 33 kV switchgear
| a) | CB,DS; CT,PT & LA ( 3 no.'s= 1set) | set | 12
| v. | XLPE Cable | m | 120
| vi. | Cable Sealing End | No | 12
| vii. | Cable trench | Lot | 1
1D |  | Transformers
1D1 |  | Autotransformer 230/135/34.5 kV three phase ONAF 350/350/100 MVA, ONAN 250/250/70 MVA, YNa0d1, with On-load tap changer, with tertiary winding (brought out to terminal bushings) | Set | 2
1D2 |  | Deleted
1D3 |  | On-line Dissolved Gas Analyzer & Moisture monitoring system for 230/135/34.5kV auto transformers | Set | 2
1D4 |  | Earthing / Auxiliary Power Transformer 33/0.415 kV, three phase 350 kVA, ZNyn11, ONAN, with Off-load tap changer, associated outdoor neutral CTs and steel support structures including all necessary connections. | Set | 2
1D5 |  | Complete Fire Fighting system for GIS Hall & Control Room
| i) | 230kV GIS Hall | lot | 1
| ii) | 132kV GIS Hall | Deleted
| iii) | Panel & Control Room | Lot | 1
1D6 | a) | Fast Depressurization system for three phase outdoor type auto transformer | Set | 2
| b) | Water Spray system for three phase outdoor type auto transformer | Set | 2
1E | Control, Protection, SAS and Metering
245kV Circuits
1E1 | Control, Protection,monitoring & SAS Function for overhead line circuits |  | set | 8
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | set | 1
| b) | Protection main relays, Main-1 & Main-2 | set | 2
| c) | Auxiliary relays (TCS, Lockout etc) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
1E2 |  | Control, monitoring, Protection, monitoring & SAS Function for Auto transformer circuits | set | 2
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | set | 1
| b) | Protection main relay (Main-1, Main-2) | set | 2
| c) | Auxiliary relays (TCS, Lockout etc) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
1E3 |  | Control, Protection,monitoring & SAS Function for Bus Coupler circuits | set | 1
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | set | 1
| b) | Protection main relay | set | 1
| c) | Auxiliary relays (TCS, Lockout etc) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
1E4 |  | Busbar Protection | set | 1
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | NA
| b) | Protection main relay | set | 1
| i. | Bay unit with HMI | set | 11
| ii. | Central unit with HMI | set | 1
| c) | Selector Switch for Enabling/Disabling BBP,BFP, all function | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
1E5 |  | Tarif metering
| a) | Meters (Main & Check) | No. | 20
| b) | Panel including wiring, lighting,humidity controller, heater & other accessories | lot | 1
145kV Circuits
1E6 |  | Control, Protection,monitoring & SAS for overhead line circuits | set | 2
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | set | 1
| b) | Protection main relay (Main-1, Main-2) | set | 2
| c) | Auxiliary relays (TCS, Lockout etc) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
1E7 |  | Control, Protection,monitoring & SAS for Auto transformer circuits | set | 2
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | set | 1
| b) | Protection main relay (as Backup: 67,67N,50,50N,51,51N) | set | 1
| c) | Auxiliary relays (TCS, Lockout etc) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
1E8 |  | Deleted
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | set | 1
| b) | Protection main relay | set | 1
| c) | Auxiliary relays (TCS, Lockout etc) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
1E9 |  | Busbar Protection | set | 1
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | NA
| b) | Protection main relay
| i. | Bay unit with HMI | set | 4
| ii. | Central unit HMI | set | 1
| c) | Selector Switch for Enabling/Disabling BBP,BFP, all function | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
1E10 |  | Tariff metering
| a) | Meters | No. | 8
| b) | Panel including wiring, lighting,humidity controller, heater & other accessories | lot | 1
36kV Circuit
1E11 |  | Control, Monitoring, Protection & SAS function for 33kV station power system | Set | 2
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | Set | 2
| b) | Protection main relay ( as backup: 67,67N,50,50N,51,51N) | Set | 2
| c) | Auxiliary relays (TCS, Lockout etc) | Set | 2
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | Set | 2
1E12 |  | Tariff metering
| a) | Meters (Main & Check) | No. | 4
| b) | Panel including wiring, lighting,humidity controller, heater & other accessories | lot | 1
1E13 | Substation Automation system
| i. | BCU
| a) | for 245kV Circuits | No. | 11
| b) | for 145kV Circuits | No. | 4
| c) | 33kV Circuits | No. | 2
| ii. | Industrial Server PC ( Intel XEON Silver- 4116 processor, ECC memory) cum Operator workstation with SAS & Enginering Software | Set | 2
| iii. | Ethernet Switch for SAS | Lot | 1
| iv. | GPS system | Set | 1
| v. | Common alarm unit with hooter/buzzer for annunciation | Set | 1
| vi. | LCD Monitor, 55" or Large | Set | 1
| vii. | Printer, A4 Laser (One black & White, Other Color) | Set | 2
| viii. | Engineering PC: core i7-9800X series processor, 1TB HDD, 16GB RAM, 22'' display for SAS & SCADA | No. | 1
| ix. | Cable (Fiber Optic, Ethernet, Copper etc.) | Lot | 1
| x. | Panel including wiring, lighting,heater & other accessories | Lot | 1
| xi. | Other Accessories (if any) | Lot | 1
1F | SCADA system for Telecontrol and Telemetering
| a) | Equipment at Substation
| i. | Gateway (server, engineering software) | Set | 2
| ii. | Ethernet Switch | Set | 2
| iii. | Hardware Firewall | Set | 1
| iv. | Additional 33kV Feeder BCU | set | 5
| v. | Panel including wiring, lighting,humidity controller, heater & other accessories | lot | 1
| vi. | Cables | lot | 1
| vii. | Other Accessories (if any) | lot | 1
1E13 |  | Substation Automation system
| i. | BCU
| a) | for 245kV Circuits | No. | 11
| b) | for 145kV Circuits | No. | 4
| ii. | CPU
| a) | Industrial Server PC | Set | 2
| b) | HMI PC | Set | 2
| iii. | Softwares
| a) | Operating System | set | 1
| b) | SAS Enginering Software/tool | set | 1
| c) | SAS Software | set | 1
| iv. | Ethernet Switch | Lot | 1
| v. | GPS system | Set | 1
| vi. | Modem | Set | 1
| vii. | PC small Monitor & Keyboard | Set | 2
| viii. | LCD Monitor, 55" or Large | Set | 1
| ix. | Gateway | Set | 2
| x. | Printer, A4 Laser (One black & White, Other Color) | Set | 2
| xi. | Laptop: core i7, 500GB HDD, 8GB RAM, 17'' display | No. | 1
| xii. | Cable | Lot | 1
| a) | Fiber Optic Cable
| b) | Ehternet/LAN Cable | Lot | 1
| c) | Copper Cable | Lot | 1
| xiii. | Panel including wiring, lighting,heater & other accessories | Lot | 1
| xiv. | Other Accessories | Lot | 1
| b) | Integration work with Master & Backup NLDC including Engineering & Commissioning | refere to Schedule B4
1G | Digital Fault & Disturbance Recorder
1G1 | i. | DFDR processor | Set | 1
| ii. | Card for each bay including A/D Converter, Digital & Analog data acquisition system
| a) | for 245kV Circuits | set | 11
| b) | for 145kV Circuits | set | 4
| iii. | Ethernet Switch | set | 1
| iv | GPS system | set | 1
| v. | Panel including wiring, lighting, heater, humidity sensor & other accessories | Lot | 1
| vi. | Engineering PC: core i7-9700K, 1 TB HDD, 16GB RAM, 17'' display | set | 1
1H | GIL & Power Cable
1H1 | 132kV, 2000A GIL for connection between secondary side of Power transformer & 132kV switchgear near existing 132kV AIS Bus
| i) | GIL | m | 240
| ii) | SF6-Air Bushing | No. | 12
1H2 | 132kV, 2000A rated in Buried Soil XLPE power cable for con-nection between secondary side of Power transformer & 132kV switchgear near existing 132kV AIS Bus
| i) | Cable | m | 720
| ii) | Cable sealing End | No. | 12
1H3 | 36kV, 300 mm2 XLPE power cable for connection between tertiary side of Power transformer & 33/0.4kV Auxiliary transformer.
| i) | Cable | m | 120
| ii) | Cable sealing End | No. | 12
1I | Multicore Cables
Multicore Cables for control, protection, metering & power circuits
| i. | _LV Control Cable | lot | 1
| ii. | _LV Power Cable | lot | 1
1J | Earthing and Lightning Protection system and Portable Eathing Equipment
1J1 | Earthing and Lightning Protection system
| i. | _Earthing system for complete substation | lot | 1
| ii. | _Lighting Protection System for complete substation | lot | 1
1J2 | Portable(maintenance) earthing equipment device |  | set | 2
1K | Batteries, chargers & DC distribution
1K1 | 110V Ni-cad Batteries with chargers & distribution board (including 2 sets 5kVA Inverter) |  | lot | 1
| i. | _110V Battery Banks, 600Ah | set | 2
| ii. | _Charger 220A | set | 2
| iii. | _5kVA Inverter | set | 2
| iv. | _110V DC Distribution panel, MCC type | lot | 1
1K2 |  | 48V Ni-cad Batteries with chargers & distribution board
| i. | _48V battery Banks,150Ah | set | 2
| ii. | _Charger 70A | set | 2
| iii. | _48V DC Disatribution Panel | lot | 1
1L | LVAC Distribution
1L1 | _AC 415V or 240V distribution panels (MCC type) |  | lot | 1
1L2 | _Tariff metering at LV side(Main & Check) |  | No | 4
1M | Civil Works, Building and Foundation
1M1 | Complete civil items required for outdoor works including boundary wall and slope protection |  | Refer to Schedule B4
1M2 | Complete civil works for GIS Hall, Operation & Panel Room
| i) | _Foundation works | Refer to Schedule B4
| ii) | _Super structures | Refer to Schedule B4
| iii) | _All finish works | Refer to Schedule B4
| iv) | _10 ton EOT Crane | No. | 1
| v) | 6 person lift | No | 1
1M3 | Testing of Foundation |  | Refer to Schedule B4
1M4 | Fire Fighting system for GIS Hall & Control Room
| i) | Fire Fighting system For GIS Room | Lot | 1
| ii) | Fire Fighting system For Operation & Panel Room | Lot | 1
1M5 | Complete transformer Protector system for transformers including Nitrogen Injection system : reservoir, pipe network and pump etc. |  | Refer to Schedule B4
1N | Lighting, small power, air conditioning and Ventilation
1N1 | Indoor Lighting (LED type), small power, air conditioning and Ventilation and emergency DC lighting for control building and local control houses |  | lot | 1
1N2 | Lighting (LED type) for ouside building for security, roadway, switchyard |  | lot | 1
1N3 | Complete solar system (1kW solar panel) including 12V VRLA maintenace free battery and other accessories for Substation emergency DC Lighting |  | Set | 1
1O | Fibre Optic Multiplexer Equipment and PLC Equipment for Communication and Protection
1O1 | Indoor Fibre Optic Multipexer Equipment |  | lot | 1
1O2 | PABX Card & tele-phone set |  | lot | 1
1O3 | under ground optical fiber cable, armoured, 48/24 core including Outdoor termination box,indoor MDF & pigtail cables |  | lot | 1
1O4 | PDH & SDH and 48/24 Core ODF with necessary connection work and testing shall be installed. |  | lot | 1
Total Price( for New Kochua 230/132/33kV SS) carried to Summary of Price Schedule
Total Price in words ( for New Kochua 230/132/33kV SS)...........................................................................................................................................................................
New 132/33 kV Substation at Laksham
Item No. | Description of Equipment Requirement |  | Unit | Quantity |  | Foreign Currency (in……….)
[6 empty] | Unit Price | Total Price
[6 empty] | CIP | CIP
|  |  |  | (1) |  | (2) | (3) = (1) x (2)
2A.A | 230 kV switchgear, equipment connection and steel structures
Deleted
2A.B | 145 kV Indoor Type Gas Insulated Switchgear (GIS), equipment connection and steel structures
2A.B1 | 145kV GIS Line Feeder Bays
| a) | For Laksham SS | set | 2
Each Line bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1600A, 40kA/3s, three phase, single pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1600A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1600A, 40kA/3s three phase line disconnector integral with high speed earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer | sets | 3
| vii. | 145kV single phase voltage transformer 2 core, Class 0.2 for Metering and Class 3P for Protection, | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Cubicle | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2A.B2 | 145kV GIS Transformer Feeder Bays: |  | Set | 2
| a) | For Laksham SS | set | 2
Each transformer bay shall comprise of the following equipment:
| i. | 145kV,2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1600A, 40kA/3s, three phase, gang pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1600A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1600A, 40kA/3s three phase line side disconnector integral with earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer | sets | 3
| vii. | 145kV single phase voltage transformer 2 core, Class 0.2 for Metering and Class 3P for Protection, | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Cubicle | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2A.B3 | 145kV Bus Coupler Bays :
| a) | For Laksham SS | set | 1
Each Bus Coupler Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase double busbar | lot | 1
| ii. | 145kV, 2500A, 40kA/3s, three phase, gang pole operation circuit breaker complete with spring-stored energy operating mechanism | No. | 1
| iii. | 145kV, 2500A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Sets | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism, on either side of circuit breaker. | sets | 2
| v. | 145kV, 2500A,40kA/3s, single phase, 2-core, current transformer | No. | 3
| vi. | 145kV, 2500A, 40kA/3s, single phase, 3-core, current transformers | No. | 3
| vii. | Local Control Cubicle | set | 1
| viii. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, sepecial equipment as per specification etc. as appropriate | Lot | 1
2A.B4 | 145kV GIS Double Busbar with VT/ES :
| a) | For Laksham SS | Set | 1
Each GIS Double Busbar with VT/ES Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase double busbars | Lot | 1
| ii. | 145kV, single phase, 2 cores voltage transformer | No. | 6
| iii. | 145kV, 40kA/3s, three phase, three position earth switches complete with motor operating Mechanism | Sets | 2
| iv. | Local Control Cubicle | Set | 1
132kV Air I nsulated Switchgear
2A.B5 | 120kV rated voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase surge arrester
| a) | For Laksham SS | No. | 12
2A.B6 | Rigid tubular conductor and/or stranded conductors including accessories for each connection as required for completing 145kV GIS Switchyard for all five (05) substations
| i. | Tubular Conductor | Lot | 1
| ii | Flexible Conductor | Lot | 1
2A.B7 | insulator and fittings including all necessary clamps and connectors as required for completing 145kV GIS Switchyard for all five (05) substations
| i | _Insulator | Lot | 1
| ii | Fittings & Clamps_Connector | Lot | 1
| ii | Nut-bolt | Lot | 1
| iv. | _Cable trench including fitting, fixing accessories | Lot | 1
2A.B8 | Steel gantry, having double tier for each double circuit of 145kV Transmission Line including all necessary accessories required for completing 145kV GIS Switchyard
| a) | Steel Structure
| i. | _Gantry Column | No. | 3
| ii. | Beam | No. | 2
| iii. | Nut & Bolts | Lot | 1
| b) | Equipment Structure
| i. | LA | No. | 12
2A.C 33 kV Switchgear, equipment connection and steel structures
One (1) set of complete equipment for switchgear 33 kV shall be designed, supplied, delivered, installed, tested and commissioned, under this contract, comprise the following:
2A.C1 | Circuit Breaker 36 kV, 2500 A, 31.5kA/1s, 50 Hz, 170/70 kV BIL, three pole, vacuum type, for outdoor installation with one spring-stored energy operating mechanism |  | Set | 2
2A.C2 | Disconnector 36 kV, 2500 A, 31.5 kA/1s, 50 Hz, 170/70 kV BIL, three pole, single vertical break, post type, motor operated
| i) | DS without ES | set | 2
| ii) | DS with ES | set | 2
2A.C3 | Current transformer 36 kV, 31.5 kA/1s, 50Hz, 170/70 kV BIL, single phase, 2500/1 , 3-core, post type with double secondary box |  | nos. | 6
2A.C4 | Voltage transformer 36kV, 50Hz, 170/70 kV BIL, single phase, 33/V3 / 0.110/V3 / 0.110/V3 kV, 3 secondary windings, inductive type with double secondary box |  | No. | 6
2A.C5 | Surge arrester 36 kV, 30 kV continuous operating voltage, 10 kA nominal discharge current, 50 Hz, single phase, gapless, metal oxide type for all five (05) substations |  | No. | 6
2A.C6 | DS with load break fuse (10A) etc. for Connection between 36kV busbar & 02 sets of 33/0.415kV Earthing/Auxiliary transformer. |  | Set | 2
2A.C7 | Gantry steel structures for Bus & Equipment, Conductor for 36kV,3000A Bus bar, Insulator and fittings including all necessary clamps and connectors required to complete 33kV switchyard
| i. | Flexible conductor for Bus & Equipment connection | Lot | 1
| ii. | Insulators and fittings incl. all necessary clamps and connectors,Nut-Bolt required for completing 33 kV switchyard | Lot | 1
| iii. | Gantry steel structures for Bus
| a) | Beam | No | 4
| b) | Column | No | 6
| iv. | Gantry steel structures for Transformer
| a) | Beam | No | 2
| b) | Column | No | 3
| v. | steel structures for equipment supports required for completing 33 kV switchgear
| a) | CB,DS; CT,PT & LA ( 3 No.s= 1set) | set | 11
| vi. | XLPE Cable | Deleted
| vii. | Cable Sealing End | Deleted
| viii. | Cable trench | Lot | 1
2A.D | Transformers
2A.D1 |  | Deleted
2A.D2 | Three phase outdoor type two-winding power transformer, 132/34.5kV, 80/120MVA (ONAN/ONAF) |  | Set | 2
2A.D3 | On-line Dissolved Gas monitoring system for 132/34.5kV transformers |  | Deleted
2A.D4 | Earthing / Auxiliary Power Transformer 33/0.415 kV, three phase 250 kVA, Dyn11, ONAN , associated outdoor neutral CTs and steel support structures including all necessary connections. |  | Set | 2
2A.D5 |  | Complete Fire Fighting system for GIS Hall & Control Room
| i) | 230kV GIS Hall | Deleted
| ii) | 132kV GIS Hall | Lot | 1
| iii) | Panel & Control Room | Lot | 1
2A.D6 | Transformer Fire-Fighting system (water Spray type) for three phase outdoor type power transformer |  | Deleted
2A.E | Control, Protection, SAS and Metering
245kV Circuits
Deleted
145kV Circuits
2A.E1 |  | Control, Protection,monitoring & SAS function for overhead line circuits | set | 2
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main & Backup) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2E2 |  | Control, Protection,monitoring & SAS function for Power transformer circuits | set | 2
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main-1, Main-2) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2A.E3 |  | Control, Protection,monitoring & SAS function for Bus Coupler circuits | set | 1
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay | set | 1
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2A.E3 |  | Busbar Protection | set | 1
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | NA
| b) | Protection main relay
| i. | Bay unit with HMI | set | 5
| ii. | Central unit HMI | set | 1
| c) | Selector Switch for Enabling/Disabling BBP,BFP, all function | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2A.E4 |  | Tariff metering
| a) | Meters (Main & Check) | No. | 8
| b) | Complete Panel including wiring, lighting,humidity controller, heater & other accessories | lot | 1
36kV Circuit
2A.E5 |  | Control, Monitoring, Protection & SAS for 33kV station power system | Set | 2
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | Set | 1
| b) | Protection main relay (67,67N,50,50N,51,51N etc) | Set | 1
| c) | Auxiliary relays (TCS, Lockout etc) | Set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | Set | 1
2A.E6 | Tariff metering
| a) | Meters (Main & Check) | No. | 4
| b) | Panel including wiring, lighting,humidity controller, heater & other accessories | lot | 1
2A.E7 |  | Substation Automation system
| i. | BCU
| a) | for 245kV Circuits | No. | NA
| b) | for 145kV Circuits | No. | 2
| c) | 33kV Circuits | No. | 2
| ii. | Industrial Server PC ( Intel XEON Silver- 4116 processor, ECC memory) cum Operator workstation with SAS & Enginering Software | Set | 2
| iii. | Ethernet Switch for SAS | Lot | 1
| iv. | GPS system | Set | 1
| v. | Common alarm unit with hooter/buzzer for annunciation | Set | 2
| vi. | LCD Monitor, 55" or Large | Set | 1
| vii. | Printer, A4 Laser (One black & White, Other Color) | Set | 2
| viii. | Engineering PC: core i7-9800X series processor, 1TB HDD, 16GB RAM, 22'' display for SAS & SCADA | No. | 1
| ix. | Cable (Fiber Optic, Ethernet, Copper etc.)
| x. | Panel including wiring, lighting,heater & other accessories | Lot | 1
| xi. | Other Accessories (if any) | Lot | 1
2A.F | SCADA system for Telecontrol and Telemetering
| a) | Equipment at Substation
| i. | Gateway (server, engineering software) | Set | 2
| ii. | Ethernet Switch | Set | 2
| iii. | Hardware Firewall | Set | 1
| iv. | Additional 33kV Feeder BCU | set | 5
| v. | Panel including wiring, lighting,heater & other accessories | lot | 1
| vi. | Cables | lot | 1
| vii. | Other Accessories (if any) | lot | 1
| b) | Integration work with Master & Backup NLDC including Engineering & Commissioning | refere to Schedule B4
2A.G | Digital Fault & Disturbance Recorder
Deleted
2A.H |  | GIL & Power Cable
Deleted
2A.I |  | Multicore Cables
Multicore Cables for control, protection, metering & power circuits
| i. | _LV Control Cable | lot | 1
| ii. | _LV Power Cable | lot | 1
2A.J |  | Earthing and Lightning Protection system and Portable Eathing Equipment
2A.J1 |  | Earthing and Lightning Protection system
| i. | _Earthing system for complete substation | lot | 1
| ii. | _Lightning Protection System for complete substation | lot | 1
2A.I2 |  | Portable(maintenance) earthing equipment device | set | 1
2A.K |  | Batteries, chargers & DC distribution
2A.K1 |  | 110V Ni-cad Batteries with chargers & distribution board (including 2 sets 3kVA Inverter) | lot | 1
| i. | _110V Battery Banks, 500Ah | set | 2
| ii. | _Charger 170A | set | 2
| iii. | _3kVA Inverter | set | 1
| iv. | _110V DC Distribution panel, MCC type | lot | 1
2A.K2 |  | 48V Ni-cad Batteries with chargers & distribution board
| i. | _48V battery Banks,150Ah | set | 2
| ii. | _Charger, 70A | set | 2
| iii. | _48V DC Disatribution Panel | lot | 1
2A.L | LVAC Distribution
2A.L1 | _AC 415V or 240V distribution panels (MCC type) |  | lot | 1
2A.L2 | _Tariff metering at LV side(Main & Check) |  | No. | 4
2A.M | Civil Works, Building and Foundation
2A.M1 | Complete civil items required for outdoor works including boundary wall and slope protection |  | Refer to Schedule B4
2A.M2 | Complete civil works for GIS Hall, Operation & Panel Room
| i) | _Foundation works | Refer to Schedule B4
| ii) | _Super structures | Refer to Schedule B4
| iii) | _All finish works | Refer to Schedule B4
| iv) | _10 ton EOT Crane | No. | 1
| v) | 6 person lift | No | 1
2A.M3 | Testing of Foundation |  | Refer to Schedule B4
2A.M4 | Fire Fighting system for GIS Hall & Control Room
| i) | Fire Fighting system For GIS Room | Lot | 1
| ii) | Fire Fighting system For Operation & Panel Room | Lot | 1
2A.M5 | Complete Water spray system for transformers fire-fighting including reservoir, pipe network and pump etc. |  | Deleted
2A.N | Lighting, small power, air conditioning and Ventilation
2A.N1 | Indoor Lighting (LED type), small power, air conditioning and Ventilation and emergency DC lighting for control building and local control houses |  | lot | 1
2A.N2 | Lighting (LED type) for ouside building area for security, roadway, switchyard and emergency DC lighting |  | lot | 1
2A.N3 | Complete solar system (1kW solar panel) including 12V VRLA maintenace free battery and other accessories for Substation emergency DC Lighting |  | Set | 1
2A.O | Fibre Optic Multiplexer Equipment for Communication and Protection
2A.O1 | Indoor Fibre Optic Multipexer Equipment |  | lot | 1
2A.O2 | PABX Card & telephone set |  | lot | 1
2A.O3 | Under ground optical fiber cable, armoured, 48/24 core including Outdoor termination box,indoor MDF & pigtail cables |  | lot | 1
2A.O4 | PDH & SDH and 48/24 Core ODF with necessary connection work and testing shall be installed. |  | lot | 1
Total Price ( for New Laksham 132/33kV SS) carried to Summary of Price Schedule
Total Price in words ( for New Laksham 132/33kV SS) ............................................................................................................................................................................
New132/33 kV Substation at Muradnagar
Item No. | Description of Equipment Requirement |  | Unit | Quantity |  | Foreign Currency (in……….)
[6 empty] | Unit Price | Total Price
[6 empty] | CIP | CIP
|  |  |  | (1) |  | (2) | (3) = (1) x (2)
2B.A | 230 kV switchgear, equipment connection and steel structures
Deleted
2B.B | 145 kV Indoor Type Gas Insulated Switchgear (GIS), equipment connection and steel structures
2B.B1 | 145kV GIS Line Feeder Bays
| b) | For Muradnagr SS | set | 6
Each Line bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1600A, 40kA/3s, three phase, single pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1600A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1600A, 40kA/3s three phase line disconnector integral with high speed earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer | sets | 3
| vii. | 145kV single phase voltage transformer 2 core, Class 0.2 for Metering and Class 3P for Protection, | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Cubicle | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2B.B2 | 145kV GIS Transformer Feeder Bays:
| b) | For Muradnagr SS | set | 2
Each transformer bay shall comprise of the following equipment:
| i. | 145kV,2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1600A, 40kA/3s, three phase, gang pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1600A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1600A, 40kA/3s three phase line side disconnector integral with earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer | sets | 3
| vii. | 145kV single phase voltage transformer 2 core, Class 0.2 for Metering and Class 3P for Protection, | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Cubicle | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2B.B3 | 145kV Bus Coupler Bays :
| b) | For Muradnagr SS | set | 1
Each Bus Coupler Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase double busbar | lot | 1
| ii. | 145kV, 2500A, 40kA/3s, three phase, Gang pole operation circuit breaker complete with spring-stored energy operating mechanism | No. | 1
| iii. | 145kV, 2500A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Sets | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism, on either side of circuit breaker. | sets | 2
| v. | 145kV, 40kA/3s, single phase, 2-core, current transformer | No. | 3
| vi. | 145kV, 2500A, 40kA/3s, single phase, 3-core, current transformers | No. | 3
| vii. | Local Control Cubicle | set | 1
| viii. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, sepecial equipment as per specification etc. as appropriate | Lot | 1
2B.B4 | 145kV GIS Double Busbar with VT/ES :
| a) | For Muradnagar SS | Set | 1
Each GIS Double Busbar with VT/ES Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kV/3s, three phase double busbars | Lot | 1
| ii. | 145kV, single phase, 2 cores voltage transformer | No. | 6
| iii. | 145kV, 40kA/3s, three phase, three position earth switches complete with motor operating Mechanism | Sets | 2
| iv. | Local Control Cubicle | Set | 1
132kV Air I nsulated Switchgear
2B.B5 | 120kV rated voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase surge arresters
| b) | For Muradnagr SS | No. | 24
2B.B6 | Rigid tubular bus and/or stranded conductors including accessories for each connection as required for completing 145kV GIS Switchyard for all five (05) substations
| i. | Tubular Conductor | Lot | 1
| ii | Flexible Conductor | Lot | 1
2B.B7 | insulator and fittings including all necessary clamps and connectors as required for completing 145kV GIS Switchyard
| i | _Insulator | Lot | 1
| ii | Fittings & Clamps_Connector | Lot | 1
| ii | Nut-bolt | Lot | 1
| iv. | _Cable trench including fitting, fixing accessories | Lot | 1
2B.B8 | Steel gantry, having double tier for each double circuit of 145kV Transmission Line including all necessary accessories required for completing 145kV GIS Switchyard
| a) | Steel Structure
| i. | _Gantry Column | No. | 9
| ii. | Beam | No. | 8
| iii. | Nut & Bolts | Lot | 1
| b) | Equipment Structure
| i. | LA | No. | 24
2B.C 33 kV Switchgear, equipment connection and steel structures
One (1) set of complete equipment for switchgear 33 kV shall be designed, supplied, delivered, installed, tested and commissioned, under this contract, comprise the following:
2B.C1 | Circuit Breaker 36 kV, 2500 A, 31.5kA/1s, 50 Hz, 170/70 kV BIL, three pole, vacuum type, for outdoor installation with one spring-stored energy operating mechanism |  | Set | 2
2B.C2 | Disconnector 36 kV, 2500 A, 31.5 kA/1s, 50 Hz, 170/70 kV BIL, three pole, single vertical break, post type, motor operated
| i) | DS without ES | set | 2
| ii) | DS with ES | set | 2
2B.C3 | Current transformer 36 kV, 31.5 kA/1s, 50Hz, 170/70 kV BIL, single phase, 2500/1 , 3-core, post type with double secondary box |  | nos. | 6
2B.C4 | Voltage transformer 36kV, 50Hz, 170/70 kV BIL, single phase, 33/V3 / 0.110/V3 / 0.110/V3 kV, 3 secondary windings, inductive type with double secondary box |  | No. | 6
2B.C5 | Surge arrester 36 kV, 30 kV continuous operating voltage, 10 kA nominal discharge current, 50 Hz, single phase, gapless, metal oxide type for all five (05) substations |  | No. | 6
2B.C6 | DS with load break fuse (10A) etc. for Connection between 36kV busbar & 02 sets of 33/0.415kV Earthing/Auxiliary transformer. |  | Set | 2
2B.C7 | Gantry steel structures for Bus & Equipment, Conductor for 36kV,3000A Bus bar, Insulator and fittings including all necessary clamps and connectors required to complete 33kV switchyard
| i. | Flexible conductor for Bus & Equipment connection | Lot | 1
| ii. | Insulators and fittings incl. all necessary clamps and connectors,Nut-Bolt required for completing 33 kV switchyard | Lot | 1
| iii. | Gantry steel structures for Bus
| a) | Beam | No | 4
| b) | Column | No | 6
| iv. | Gantry steel structures for Transformer
| a) | Beam | No | 2
| b) | Column | No | 3
| v. | steel structures for equipment supports required for completing 33 kV switchgear
| a) | CB,DS; CT,PT & LA ( 3 No.s= 1set) | set | 11
| vi. | XLPE Cable | Deleted
| vii. | Cable Sealing End | Deleted
| viii. | Cable trench | Lot | 1
2B.D | Transformers
2B.D1 |  | Deleted
2B.D2 |  | Three phase outdoor type two-winding power transformer, 132/34.5kV, 80/120MVA (ONAN/ONAF) | Set | 2
2B.D3 |  | On-line Dissolved Gas monitoring system for 230/138/33kV auto transformers | Deleted
2B.D4 |  | Earthing / Auxiliary Power Transformer 33/0.415 kV, three phase 250 kVA, Dyn11, ONAN , associated outdoor neutral CTs and steel support structures including all necessary connections. | Set | 2
2B.D5 |  | Complete Fire Fighting system for GIS Hall & Control Room
| i) | 230kV GIS Hall | Deleted
| ii) | 132kV GIS Hall | Lot | 1
| iii) | Panel & Control Room | Lot | 1
2B.D6 |  | Transformer Fire-Fighting system (water Spray type) for three phase outdoor type power transformer | Set | 2
2B.E | Control, Protection, SAS and Metering
245kV Circuits
Deleted
145kV Circuits
2B.E1 |  | Control, Protection,monitoring & SAS function for overhead line circuits | set | 6
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main-1, Main-2) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2B.E2 |  | Control, Protection,monitoring & SAS function for Auto transformer circuits | set | 2
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main-1, Main-2) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2B.E3 |  | Control, Protection,monitoring & SAS function for Bus Coupler circuits | set | 1
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main-1, Main-2) | set | 1
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2B.E3 |  | Busbar Protection | set | 1
Each Comprising
| a) | Control panel with all accessories including monitoring | set | 1
| b) | Protection main relay
| i. | Bay unit with HMI | set | 5
| ii. | Central unit with HMI | set | 1
| c) | Selector Switch for Enabling/Disabling BBP,BFP, all function | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2B.E4 |  | Tariff metering
| a) | Meters (Main & Check) | No. | 16
| b) | Panel including wiring, lighting,heater & other accessories | lot | 1
36kV Circuit
2B.E5 |  | Control, Monitoring, Protection & SAS for 33kV station power system | set | 2
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | set | 1
| b) | Protection main relay (67,67N,50,50N,51,51N etc) | Set | 1
| c) | Auxiliary relays (TCS, Lockout etc) | Set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2B.E6 |  | Tariff metering
| a) | Meters (Main & Check) | No. | 4
| b) | Panel including wiring, lighting,heater, humidity sensor & other accessories | lot | 1
2B.E7 |  | Substation Automation system
| i. | BCU
| a) | for 245kV Circuits | No. | NA
| b) | for 145kV Circuits | No. | 9
| c) | 33kV Circuits | No. | 2
| ii. | Industrial Server PC ( Intel XEON Silver- 4116 processor, ECC memory) cum Operator workstation with SAS & Enginering Software | Set | 2
| iii. | Ethernet Switch for SAS | Lot | 1
| iv. | GPS system | Set | 1
| v. | Common alarm unit with hooter/buzzer for annunciation | Set | 2
| vi. | LCD Monitor, 55" or Large | Set | 1
| vii. | Printer, A4 Laser (One black & White, Other Color) | Set | 2
| viii. | Engineering PC: core i7-9800X series processor, 1TB HDD, 8GB RAM, 22'' display for SAS & SCADA | No. | 1
| ix. | Cable (Fiber Optic, Ethernet, Copper etc.)
| x. | Panel including wiring, lighting,heater & other accessories | Lot | 1
| xi. | Other Accessories (if any) | Lot | 1
2B.F | SCADA system for Telecontrol and Telemetering
| a) | Equipment at Substation
| i. | Gateway (server, engineering software) | Set | 2
| ii. | Ethernet Switch | Set | 2
| iii. | Hardware Firewall | Set | 1
| iv. | Additional 33kV Feeder BCU | set | 5
| v. | Panel including wiring, lighting,heater, humidity sensor & other accessories | lot | 1
| vi. | Cables | lot | 1
| vii. | Other Accessories (if any) | lot | 1
| b) | Integration work with Master & Backup NLDC including Engineering & Commissioning | refere to Schedule B4
2B.G | Digital Fault & Disturbance Recorder
Deleted
2B.H |  | GIL & Power Cable
Deleted
2B.I |  | Multicore Cables
Multicore Cables for control, protection, metering & power circuits
| i. | _LV Control Cable | lot | 1
| ii. | _LV Power Cable | lot | 1
2B.J |  | Earthing and Lightning Protection system and Portable Eathing Equipment
2B.J1 |  | Earthing and Lightning Protection system
| i. | _Earthing system for complete substation | lot | 1
| ii. | _Lighting Protection System for complete substation | lot | 1
2B.J2 |  | Portable(maintenance) earthing equipment device | set | 1
2B.K |  | Batteries, chargers & DC distribution
2B.K1 |  | 110V Ni-cad Batteries with chargers & distribution board (including 2 sets 4kVA UPS, 30 mins) | lot | 1
| i. | _110V Battery Banks, 500Ah | set | 2
| ii. | _Charger 170A | set | 2
| iii. | _5kVA Inverter | set | 1
| iv. | _110V DC Distribution panel, MCC type | lot | 1
2B.K2 |  | 48V Ni-cad Batteries with chargers & distribution board
| i. | _48V battery Banks,150Ah | set | 2
| ii. | _Charger, 70A | set | 2
| iii. | _48V DC Disatribution Panel | lot | 1
2B.L | LVAC Distribution
2B.L1 | _AC 415V or 240V distribution panels (MCC type) |  | lot | 1
2B.L2 | _Tariff metering at LV side(Main & Check) |  | No. | 4
2B.M | Civil Works, Building and Foundation |  | Refer to Schedule B4
2B.M1 | Complete civil items required for outdoor works including boundary wall and slope protection |  | Refer to Schedule B4
2B.M2 | Complete civil works for GIS Hall, Operation & Panel Room
| i) | _Foundation works | Refer to Schedule B4
| ii) | _Super structures | Refer to Schedule B4
| iii) | _All finish works | Refer to Schedule B4
| iv) | _10 ton EOT Crane | No. | 1
| v) | 6 person lift | No | 1
2B.M3 | Testing of Foundation |  | Refer to Schedule B4
2B.M4 | Fire Fighting system for GIS Hall & Control Room
| i) | Fire Fighting system For GIS Room | Lot | 1
| ii) | Fire Fighting system For Operation & Panel Room | Lot | 1
2B.M5 | Complete Water spray system for transformers fire-fighting including reservoir, pipe network and pump etc. |  | set | 2
2B.N | Lighting, small power, air conditioning and Ventilation
2B.N1 | Indoor Lighting (LED type), small power, air conditioning and Ventilation and emergency DC lighting for control building and local control houses |  | lot | 1
2B.N2 | Lighting (LED type) for ouside building area for security, roadway, switchyard and emergency DC lighting |  | lot | 1
2B.N3 | Complete solar system (1kW solar panel) including 12V VRLA maintenace free battery and other accessories for Substation emergency DC Lighting |  | Set | 1
2B.O | Fibre Optic Multiplexer Equipment for Communication and Protection
2B.O1 | Indoor Fibre Optic Multipexer Equipment |  | lot | 1
2B.O2 | PABX card & telephone set |  | lot | 1
2B.O3 | Under ground optical fiber cable, armoured, 48/24 core including Outdoor termination box,indoor MDF & pigtail cables |  | lot | 1
2B.O4 | PDH & SDH and 48/24 Core ODF with necessary connection work and testing shall be installed. |  | lot | 1
Total Price ( for New Muradnagar 132/33kV SS) carried to Summary of Price Schedule
Total Price in words ( for New Muradnagar 132/33kV SS)............................................................................................................................................................................
New 132/33 kV Substation at Chandina
Item No. | Description of Equipment Requirement |  | Unit | Quantity |  | Foreign Currency (in……….)
[6 empty] | Unit Price | Total Price
[6 empty] | CIP | CIP
|  |  |  | (1) |  | (2) | (3) = (1) x (2)
2C.A | 230 kV switchgear, equipment connection and steel structures
Deleted
2C.B | 145 kV Indoor Type Gas Insulated Switchgear (GIS), equipment connection and steel structures
2C.B1 | 145kV GIS Line Feeder Bays
| c) | For Chandina SS | set | 2
Each Line bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1600A, 40kA/3s, three phase, single pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1600A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | set | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1600A, 40kA/3s three phase line disconnector integral with high speed earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer | No. | 3
| vii. | 145kV single phase voltage transformer 2 core, Class 0.2 for Metering and Class 3P for Protection, | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | m | 50
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Cubicle | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2C.B2 | 145kV GIS Transformer Feeder Bays:
| c) | For Chandina SS | set | 2
Each transformer bay shall comprise of the following equipment:
| i. | 145kV,2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1600A, 40kA/3s, three phase, gang pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1600A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1600A, 40kA/3s three phase line side disconnector integral with earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer | No. | 3
| vii. | 145kV single phase voltage transformer 2 core, Class 0.2 for Metering and Class 3P for Protection, | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | m | 50
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Cubicle | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2C.B3 | 145kV Bus Coupler Bays :
| c) | For Chandina SS | set | 1
Each Bus Coupler Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase double busbar | lot | 1
| ii. | 145kV, 2500A, 40kA/3s, three phase, gang pole operation circuit breaker complete with spring-stored energy operating mechanism | No. | 1
| iii. | 145kV, 2500A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Sets | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism, on either side of circuit breaker. | sets | 2
| v. | 145kV, 40kA/3s, single phase, 2-core, current transformer with cores as follows: | No. | 3
| vi. | 145kV, 2500A, 40kA/3s, single phase, 3-core, current transformers with cores as follows: | No. | 3
| vii. | Local Control Cubicle | set | 1
| viii. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, sepecial equipment as per specification etc. as appropriate | Lot | 1
2C.B4 | 145kV GIS Double Busbar with VT/ES :
| c) | For Chandina SS | Set | 1
Each GIS Double Busbar with VT/ES Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 450kA/3s, three phase double busbars | Lot | 1
| ii. | 145kV single phase, 2 cores voltage transformer | No. | 6
| iii. | 145kV, 40kA/3s, three phase, three position earth switches complete with motor operating Mechanism | Sets | 2
| iv. | Local Control Panel | Set | 1
2C.B5 | 120kV rated voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase surge arresters
| c) | For Chandina SS | No. | 12
2C.B6 | Rigid tubular bus and/or stranded conductors including accessories for each connection as required for completing 145kV GIS Switchyard for all five (05) substations
| i. | Tubular Conductor | Lot | 1
| ii | Flexible Conductor | Lot | 1
2C.B7 | insulator and fittings including all necessary clamps and connectors as required for completing 145kV GIS Switchyard for all five (05) substations
| i | _Insulator | Lot | 1
| ii | Fittings & Clamps_Connector | Lot | 1
| ii | Nut-bolt | Lot | 1
| iv. | _Cable trench including fitting, fixing accessories | Lot | 1
2C.B8 | Steel gantry, having double tier for each double circuit of 145kV Transmission Line including all necessary accessories required for completing 145kV GIS Switchyard
| a) | Steel Structure
| i. | _Gantry Column | No. | 4
| ii. | Beam | No. | 4
| iii. | Nut & Bolts | Lot | 1
| b) | Equipment Structure
| i. | LA | No. | 12
2C.C 33 kV Switchgear, equipment connection and steel structures
One (1) set of complete equipment for switchgear 33 kV shall be designed, supplied, delivered, installed, tested and commissioned, under this contract, comprise the following:
2C.C1 | Circuit Breaker 36 kV, 2500 A, 31.5kA/1s, 50 Hz, 170/70 kV BIL, three pole, vacuum type, for outdoor installation with one spring-stored energy operating mechanism |  | Set | 2
2C.C2 | Disconnector 36 kV, 2500 A, 31.5 kA/1s, 50 Hz, 170/70 kV BIL, three pole, single vertical break, post type, motor operated
| i) | DS without ES | set | 2
| ii) | DS with ES | set | 2
2C.C3 | Current transformer 36 kV, 31.5 kA/1s, 50Hz, 170/70 kV BIL, single phase, 2500/1 , 3-core, post type with double secondary box |  | nos. | 6
2C.C4 | Voltage transformer 36kV, 50Hz, 170/70 kV BIL, single phase, 33/V3 / 0.110/V3 / 0.110/V3 kV, 3 secondary windings, inductive type with double secondary box |  | No. | 6
2C.C5 | Surge arrester 36 kV, 30 kV continuous operating voltage, 10 kA nominal discharge current, 50 Hz, single phase, gapless, metal oxide type for all five (05) substations |  | No. | 6
2C.C6 | DS with load break fuse (10A) etc. for Connection between 36kV busbar & 02 sets of 33/0.415kV Earthing/Auxiliary transformer. |  | Set | 2
2C.C7 | Gantry steel structures for Bus & Equipment, Conductor for 36kV,3000A Bus bar, Insulator and fittings including all necessary clamps and connectors required to complete 33kV switchyard
| i. | Flexible conductor for Bus & Equipment connection | Lot | 1
| ii. | Insulators and fittings incl. all necessary clamps and connectors,Nut-Bolt required for completing 33 kV switchyard | Lot | 1
| iii. | Gantry steel structures for Bus
| a) | Beam | No | 4
| b) | Column | No | 6
| iv. | Gantry steel structures for Transformer
| a) | Beam | No | 2
| b) | Column | No | 3
| v. | steel structures for equipment supports required for completing 33 kV switchgear
| a) | CB,DS; CT,PT & LA ( 3 No.s= 1set) | set | 11
| vi. | XLPE Cable | Deleted
| vii. | Cable Sealing End | Deleted
| viii. | Cable trench | Lot | 1
2C.D | Transformers
2C.D1 |  | Deleted
2C.D2 |  | Three phase outdoor type two-winding power transformer, 132/36kV, 80/120MVA (ONAN/ONAF) | Set | 2
2C.D3 |  | On-line Dissolved Gas monitoring system for 230/138/33kV auto transformers | Deleted
2C.D4 |  | Earthing / Auxiliary Power Transformer 33/0.415 kV, three phase 250 kVA, Dyn11, ONAN , associated outdoor neutral CTs and steel support structures including all necessary connections. | Set | 2
2C.D5 |  | Complete Fire Fighting system for GIS Hall & Control Room
| i) | 230kV GIS Hall | Deleted
| ii) | 132kV GIS Hall | Lot | 1
| iii) | Panel & Control Room | Lot | 1
2C.D6 |  | Transformer Fire-Fighting system (water Spray type) for three phase outdoor type power transformer | Deleted
2C.E | Control, Protection, SAS and Metering
245kV Circuits
Deleted
145kV Circuits
2C.E1 |  | Control, Protection,monitoring & SAS function for overhead line circuits | set | 2
| a) | Control panel with Mimic & all accessories including monitoring | set | 2
| b) | Protection main relay (Main-1, Main-2) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 2
| d) | Protection Panel including wiring, lighting,heater & other accessories | set | 2
2C.E2 |  | Control, Protection,monitoring & SAS function for Power transformer circuits | set | 2
| a) | Control panel with Mimic & all accessories including monitoring | set | 2
| b) | Protection main relay (Main-1, Main-2) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 2
| d) | Protection Panel including wiring, lighting,heater & other accessories | set | 1
2C.E3 |  | Control, Protection,monitoring & SAS function for Bus Coupler circuits | set | 1
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay | set | 1
| c) | Auxiliary relays (TCS, Lockout etc) | set | 1
| d) | Protecttion Panel including wiring, lighting,heater & other accessories | set | 1
2C.E3 |  | Busbar Protection | set | 1
| a) | Control panel with Mimic & all accessories including monitoring | NA
| b) | Protection main relay | set | 1
| i. | Bay unit with HMI | set | 5
| ii. | Central unit with HMI | set | 1
| c) | Protection Auxiliary relay | set | 1
| d) | Protecttion Panel including wiring, lighting,heater & other accessories | set | 1
2C.E4 |  | Tariff metering | lot | 1
| a) | Meters | lot | 1
| b) | Panel including wiring, lighting,humidity controller, heater & other accessories | lot | 1
36kV Circuit
2C.E5 |  | Control, Monitoring, Protection & SAS for 33kV station power system | Set | 2
| a) | Control Mimic panel with all accessories including monitoring | Set | 2
| b) | Protection main relay (67,67N,50,50N,51,51N etc) | Set | 2
| c) | Auxiliary relays (TCS, Lockout etc) | Set | 2
| d) | Protecttion Panel including wiring, lighting,heater, humidity sensor & other accessories | Set | 2
2C.E6 |  | Tariff metering
| a) | Meters (Main & Check) | No. | 4
| b) | Panel including wiring, lighting,heater & other accessories | lot | 1
2C.E7 | Substation Automation system
| i. | BCU
| a) | for 245kV Circuits | No. | NA
| b) | for 145kV Circuits | No. | 3
| c) | 33kV Circuits | No. | 2
| ii. | Industrial Server PC ( Intel XEON Silver- 4116 processor, ECC memory) cum Operator workstation with SAS & Enginering Software | Set | 2
| iii. | Ethernet Switch for SAS | Lot | 1
| iv. | GPS system | Set | 1
| v. | Common alarm unit with hooter/buzzer for annunciation | Set | 2
| vi. | LCD Monitor, 55" or Large | Set | 1
| vii. | Printer, A4 Laser (One black & White, Other Color) | Set | 2
| viii. | Engineering PC: core i7-9800X series processor, 1TB HDD, 16GB RAM, 22'' display for SAS & SCADA | No. | 1
| ix. | Cable (Fiber Optic, Ethernet, Copper etc.) | lot | 1
| x. | Panel including wiring, lighting,heater & other accessories | Lot | 1
| xi. | Other Accessories (if any) | Lot | 1
2C.F | SCADA system for Telecontrol and Telemetering
| a) | Equipment at Substation
| i. | Gateway (server, engineering software) | Set | 2
| ii. | Ethernet Switch | Set | 2
| iii. | Hardware Firewall | Set | 1
| iv. | Additional 33kV Feeder BCU | set | 5
| v. | Panel including wiring, lighting,heater & other accessories | lot | 1
| vi. | Cables | lot | 1
| vii. | Other Accessories (if any) | lot | 1
| b) | Integration work with Master & Backup NLDC including Engineering & Commissioning | refere to Schedule B4
2C.G | Digital Fault & Disturbance Recorder
Deleted
2C.H |  | GIL & Power Cable
Deleted
2C.I |  | Multicore Cables
Multicore Cables for control, protection, metering & power circuits
| i. | _LV Control Cable | lot | 1
| ii. | _LV Power Cable | lot | 1
2C.J |  | Earthing and Lightning Protection system and Portable Eathing Equipment
2C.J1 |  | Earthing and Lightning Protection system
| i. | _Earthing system for complete substation | lot | 1
| ii. | _Lighting Protection System for complete substation | lot | 1
2C.J2 |  | Portable(maintenance) earthing equipment device | set | 1
2C.K |  | Batteries, chargers & DC distribution
2C.K1 |  | 110V Ni-cad Batteries with chargers & distribution board (including 2 sets 4kVA Inverter) | lot | 1
| i. | _110V Battery Banks, 500Ah | set | 2
| ii. | _Charger 170A | set | 2
| iii. | _4kVA Inverter | set | 1
| iv. | _110V DC Distribution panel, MCC type | lot | 1
2C.K2 |  | 48V Ni-cad Batteries with chargers & distribution board
| i. | _48V battery Banks,150Ah | set | 2
| ii. | _Charger, 70A | set | 2
| iii. | _48V DC Disatribution Panel | lot | 1
2C.L | LVAC Distribution
2C.L1 | _AC 415V or 240V distribution panels (MCC type) |  | lot | 1
2C.L2 | _Tariff metering at LV side(Main & Check) |  | No. | 4
2C.M | Civil Works, Building and Foundation |  | Refer to Schedule B4
2C.M1 | Complete civil items required for outdoor works including boundary wall and slope protection |  | Refer to Schedule B4
2C.M2 | Complete civil works for GIS Hall, Operation & Panel Room
| i) | _Foundation works | Refer to Schedule B4
| ii) | _Super structures | Refer to Schedule B4
| iii) | _All finish works | Refer to Schedule B4
| iv) | _10 ton EOT Crane | No. | 1
| v) | 6 person lift | No | 1
2C.M3 | Testing of Foundation |  | Refer to Schedule B4
2C.M4 | Fire Fighting system for GIS Hall & Control Room
| i) | Fire Fighting system For GIS Room | Lot | 1
| ii) | Fire Fighting system For Operation & Panel Room | Lot | 1
2C.M5 | Complete Water spray system for transformers fire-fighting including reservoir, pipe network and pump etc. |  | Deleted
2C.N | Lighting, small power, air conditioning and Ventilation
2C.N1 | Indoor Lighting (LED type), small power, air conditioning and Ventilation and emergency DC lighting for control building and local control houses |  | lot | 1
2C.N2 | Lighting (LED type) for ouside building area for security, roadway, switchyard and emergency DC lighting |  | lot | 1
2C.N3 | Complete solar system (1kW solar panel) including 12V VRLA maintenace free battery and other accessories for Substation emergency DC Lighting |  | Set | 1
2C.O | Fibre Optic Multiplexer Equipment for Communication and Protection
2C.O1 | Indoor Fibre Optic Multipexer Equipment |  | lot | 1
2C.O2 | PABX Card & telephone set |  | lot | 1
2C.O3 | Under ground optical fiber cable, armoured, 48/24 core including Outdoor termination box,indoor MDF & pigtail cables |  | lot | 1
2C.O4 | PDH & SDH and 48/24 Core ODF with necessary connection work and testing shall be installed. |  | lot | 1
Total Price ( for New Chandina 132/33kV SS) carried to Summary of Price Schedule
Total Price in words ( for New Chandina 132/33kV SS)............................................................................................................................................................................
New 132/33 kV Substation at Laxmipur
Item No. | Description of Equipment Requirement |  | Unit | Quantity |  | Foreign Currency (in……….)
[6 empty] | Unit Price | Total Price
[6 empty] | CIP | CIP
|  |  |  | (1) |  | (2) | (3) = (1) x (2)
2D.A | 230 kV switchgear, equipment connection and steel structures
Deleted
2D.B | 145 kV Indoor Type Gas Insulated Switchgear (GIS), equipment connection and steel structures
2D.B1 | 145kV GIS Line Feeder Bays
| d) | For Laxmipur SS | set | 2
Each Line bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1600A, 40kA/3s, three phase, single pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1600A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1600A, 40kA/3s three phase line disconnector integral with high speed earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer with cores as follows | No. | 3
| vii. | 145kV single phase voltage transformer 2 core, Class 0.2,10VA for Metering and Class 3P,15VA for Protection | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Panel | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2D.B2 | 145kV GIS Transformer Feeder Bays:
| d) | For Laxmipur SS | Set | 2
Each Line bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1600A, 40kA/3s, three phase, Gang pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1600A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1600A, 40kA/3s three phase line disconnector integral with earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer with cores as follows | No. | 3
| vii. | 145kV single phase voltage transformer 2 core, Class 0.2 for Metering and Class 3P for Protection, | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Panel | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2D.B3 | 145kV Bus Coupler Bays :
| d) | For Laxmipur SS | set | 1
Each Bus Coupler Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase double busbar | lot | 1
| ii. | 145kV, 2500A, 40kA/3s, three phase, Gang pole operation circuit breaker complete with spring-stored energy operating mechanism | No. | 1
| iii. | 145kV, 2500A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Sets | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism, on either side of circuit breaker. | sets | 2
| v. | 145kV, 40kA/3s, single phase, 2-core, current transformer with cores as follows: | No. | 3
| vi. | 145kV, 2500A, 40kA/3s, single phase, 2-core, current transformers with cores as follows: | No. | 3
| vii. | Local Control Panel | set | 1
| viii. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, sepecial equipment as per specification etc. as appropriate | Lot | 1
2D.B4 | 145kV GIS Double Busbar with VT/ES :
| d) | For Laxmipur SS | Set | 1
Each GIS Double Busbar with VT/ES Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase double busbars | Lot | 1
| ii. | 145kV single phase, 2 core, voltage transformer | No. | 6
| iii. | 145kV, 40kA/3s, three phase, three position earth switches complete with motor operating Mechanism | Sets | 2
| iv. | Local Control Panel | Set | 1
2D.B5 | 120kV rated voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase surge arresters
| d) | For Laxmipur SS | No. | 12
2D.B6 | Rigid tubular bus and/or stranded conductors including accessories for each connection as required for completing 145kV GIS Switchyard for all five (05) substations
| i. | Tubular Conductor | Lot | 1
| ii | Flexible Conductor | Lot | 1
2D.B7 | Insulator and fittings including all necessary clamps and connectors as required for completing 145kV GIS Switchyard
| i | _Insulator | Lot | 1
| ii | Fittings & Clamps_Connector | Lot | 1
| ii | Nut-bolt | Lot | 1
| iv. | _Cable trench including fitting, fixing accessories | Lot | 1
2D.B8 | Steel gantry, having double tier for each double circuit of 145kV Transmission Line including all necessary accessories required for completing 145kV GIS Switchyard
| a) | Steel Structure
| i. | _Gantry Column | No. | 6
| ii. | Beam | No. | 4
| iii. | Nut & Bolts | Lot | 1
| b) | Equipment Structure
| i. | LA | No. | 12
2D.C 33 kV Switchgear, equipment connection and steel structures
One (1) set of complete equipment for switchgear 33 kV shall be designed, supplied, delivered, installed, tested and commissioned, under this contract, comprise the following:
2D.C1 | Circuit Breaker 36 kV, 2500 A, 31.5kA/1s, 50 Hz, 170/70 kV BIL, three pole, vacuum type, for outdoor installation with one spring-stored energy operating mechanism |  | Set | 2
2D.C2 | Disconnector 36 kV, 2500 A, 31.5 kA/1s, 50 Hz, 170/70 kV BIL, three pole, single vertical break, post type, motor operated
| i) | DS without ES | set | 2
| ii) | DS with ES | set | 2
2D.C3 | Current transformer 36 kV, 31.5 kA/1s, 50Hz, 170/70 kV BIL, single phase, 630-1250/1/1 , 2-core, post type |  | nos. | 6
2D.C4 | Voltage transformer 36kV, 50Hz, 170/70 kV BIL, single phase, 2 secondary windings, inductive type |  | No. | 6
2D.C5 | Surge arrester 36 kV, 30 kV continuous operating voltage, 10 kA nominal discharge current, 50 Hz, single phase, gapless, metal oxide type for all five (05) substations |  | No. | 6
2D.C6 | DS with load break fuse (6A) etc. for Connection between 36kV busbar & 02 sets of 33/0.415kV Earthing/Auxiliary transformer. |  | Set | 2
2D.C7 | Gantry steel structures for Bus & Equipment, Conductor for 36kV,3000A Bus bar, Insulator and fittings including all necessary clamps and connectors required to complete 33kV switchyard
| i. | Flexible conductor for Bus & Equipment connection | Lot | 1
| ii. | Insulators and fittings incl. all necessary clamps and connectors,Nut-Bolt required for completing 33 kV switchyard | Lot | 1
| iii. | Gantry steel structures for Bus
| a) | Beam | No | 4
| b) | Column | No | 6
| iv. | Gantry steel structures for Transformer
| a) | Beam | No | 2
| b) | Column | No | 3
| v. | steel structures for equipment supports required for completing 33 kV switchgear
| a) | CB,DS; CT,PT & LA ( 3 No.s= 1set) | set | 11
| vi. | XLPE Cable | Deleted
| vii. | Cable Sealing End | Deleted
| viii. | Cable trench | Lot | 1
2D.D |  | Transformers
2D.D1 |  | Deleted
2D.D2 |  | Three phase outdoor type two-winding power transformer, 132/36kV, 80/120MVA (ONAN/ONAF) | Set | 2
2D.D3 |  | On-line Dissolved Gas monitoring system for 230/138/33kV auto transformers | Deleted
2D.D4 |  | Earthing / Auxiliary Power Transformer 33/0.415 kV, three phase 250 kVA, Dyn11, ONAN , associated outdoor neutral CTs and steel support structures including all necessary connections. | set | 2
2D.D5 |  | Complete Fire Fighting system for GIS Hall & Control Room
| i) | 230kV GIS Hall | Deleted
| ii) | 132kV GIS Hall | Lot | 1
| iii) | Panel & Control Room | Lot | 1
2D.D6 |  | Transformer Fire-Fighting system (water Spray type) for three phase outdoor type power transformer | Deleted
2D.E | Control, Protection, SAS and Metering
245kV Circuits
Deleted
145kV Circuits
2D.E1 |  | Control, Protection,monitoring & SAS function for overhead line circuits | set | 2
| a) | Control panel with Mimic & all accessories including monitoring | set | 2
| b) | Protection main relay (Main-1, Main-2) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 2
| d) | Protecttion Panel including wiring, lighting,heater & other accessories | set
2D.2E2 |  | Control, Protection,monitoring & SAS function for Auto transformer circuits | set | 2
| a) | Control panel with Mimic & all accessories including monitoring | set | 2
| b) | Protection main relay (Main-1, Main-2) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 2
| d) | Protecttion Panel including wiring, lighting,heater & other accessories | set | 2
2D.E3 |  | Control, Protection,monitoring & SAS function for Bus Coupler circuits | set | 1
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main-1, Main-2) | set | 1
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Protecttion Panel including wiring, lighting,heater & other accessories | set | 1
2D.E3 |  | Busbar Protection | set | 1
| a) | Control panel with Mimic & all accessories including monitoring | NA
| b) | Protection main relay
| i. | Bay Unit | set | 5
| ii. | Central Unit | set | 1
| c) | Protection Auxiliary relay | set | 1
| d) | Protecttion Panel including wiring, lighting,heater & other accessories | set | 1
2D.E4 |  | Tariff metering | lot | 1
| a) | Meters (Main & Check) | No. | 8
| b) | Panel including wiring, lighting,heater & other accessories | lot | 1
36kV Circuit
2D.E5 |  | Control, Monitoring, Protection & SAS for 33kV station power system | Set | 2
| a) | Control Mimic panel with all accessories including monitoring | Lot | 1
| b) | Protection main relay (67,67N,50,50N,51,51N etc) | Set | 2
| c) | Auxiliary relays (TCS, Lockout etc) | Set | 2
| d) | Protecttion Panel including wiring, lighting,heater & other accessories | Set | 2
2D.E6 |  | Tariff metering
| a) | Meters (Main & Check) | No. | 4
| b) | Panel including wiring, lighting,heater & other accessories | lot | 1
2D.E7 | Substation Automation system
| i. | BCU/BCPU
| a) | for 245kV Circuits | No. | NA
| b) | for 145kV Circuits | No. | 5
| c) | 33kV Circuits | No. | 2
| ii. | Industrial Server PC cum Operator workstation with SAS & Enginering Software | Set | 2
| iii. | Ethernet Switch for SAS | Lot | 1
| iv. | GPS system | Set | 1
| v. | Common alarm unit with hooter/buzzer for annunciation | Set | 2
| vi. | LCD Monitor, 55" or Large | Set | 1
| vii. | Printer, A4 Laser (One black & White, Other Color) | Set | 2
| viii. | Engineering PC: core i7, 1TB HDD, 8GB RAM, 22'' display for SAS & SCADA | No. | 1
| ix. | Cable (Fiber Optic, Ethernet, Copper etc.)
| x. | Panel including wiring, lighting,heater & other accessories | Lot | 1
| xi. | Other Accessories (if any) | Lot | 1
2D.F | SCADA system for Telecontrol and Telemetering
| a) | Equipment at Substation
| i. | Gateway (server, engineering software) | Set | 2
| ii. | Ethernet Switch | Set | 2
| iii. | Hardware Firewall | Set | 1
| iv. | Additional 33kV Feeder BCU | set | 5
| v. | Panel including wiring, lighting,heater & other accessories | lot | 1
| vi. | Cables | lot | 1
| vii. | Other Accessories (if any) | lot | 1
| b) | Integration work with Master & Backup NLDC including Engineering & Commissioning | refere to Schedule B4
2D.G | Digital Fault & Disturbance Recorder
Deleted
2D.H |  | GIL & Power Cable
Deleted
2D.I |  | Multicore Cables
Multicore Cables for control, protection, metering & power circuits
| i. | _LV Control Cable | lot | 1
| ii. | _LV Power Cable | lot | 1
2D.J |  | Earthing and Lightning Protection system and Portable Eathing Equipment
2D.J1 |  | Earthing and Lightning Protection system
| i. | _Earthing system for complete substation | lot | 1
| ii. | _Lighting Protection System for complete substation | lot | 1
2D.J2 |  | Portable(maintenance) earthing equipment device | set | 1
2D.K |  | Batteries, chargers & DC distribution
2D.K1 |  | 110V Ni-cad Batteries with chargers & distribution board (including 2 sets 4kVA UPS, 30 mins) | lot | 1
| i. | _110V Battery Banks, 350Ah | set | 2
| ii. | _Charger 120A | set | 2
| iii. | _5kVA,30 mins Inverter | set | 1
| iv. | _110V DC Distribution panel, MCC type | lot | 1
2D.K2 |  | 48V Ni-cad Batteries with chargers & distribution board
| i. | _48V battery Banks,125Ah | set | 2
| ii. | _Charger, 50A | set | 2
| iii. | _48V DC Disatribution Panel | lot | 1
2D.L | LVAC Distribution
2D.L1 | _AC 415V or 240V distribution panels (MCC type) |  | lot | 1
2D.L2 | _Tariff metering at LV side(Main & Check) |  | No. | 4
2D.M | Civil Works, Building and Foundation |  | Refer to Schedule B4
2D.M1 | Complete civil items required for outdoor works including boundary wall and slope protection |  | Refer to Schedule B4
2D.M2 | Complete civil works for GIS Hall, Operation & Panel Room
| i) | _Foundation works | Refer to Schedule B4
| ii) | _Super structures | Refer to Schedule B4
| iii) | _All finish works | Refer to Schedule B4
| iv) | _10 ton EOT Crane | No. | 1
| v) | 6 person lift | No | 1
2D.M3 | Testing of Foundation |  | Refer to Schedule B4
2D.M4 | Fire Fighting system for GIS Hall & Control Room
| i) | Fire Fighting system For GIS Room | Lot | 1
| ii) | Fire Fighting system For Operation & Panel Room | Lot | 1
2D.M5 | Complete Water spray system for transformers fire-fighting including reservoir, pipe network and pump etc. |  | Deleted
2D.N | Lighting, small power, air conditioning and Ventilation
2D.N1 | Indoor Lighting (LED type), small power, air conditioning and Ventilation and emergency DC lighting for control building and local control houses |  | lot | 1
2D.N2 | Lighting (LED type) for ouside building area for security, roadway, switchyard and emergency DC lighting |  | lot | 1
2D.N3 | Complete solar system (1kW solar panel) including 12V VRLA maintenace free battery and other accessories for Substation emergency DC Lighting |  | Set | 1
2D.O | Fibre Optic Multiplexer Equipment for Communication and Protection
2D.O1 | Indoor Fibre Optic Multipexer Equipment |  | lot | 1
2D.O2 | PABX Card & telephone set |  | lot | 1
2D.O3 | Under ground optical fiber cable, armoured, 48/24 core including Outdoor termination box,indoor MDF & pigtail cables |  | lot | 1
2D.O4 | PDH & SDH and 48/24 Core ODF with necessary connection work and testing shall be installed. |  | lot | 1
Total Price ( for New Laxmipur 132/33kV SS) carried to Summary of Price Schedule
Total Price in words ( for New Laxmipur 132/33kV SS)............................................................................................................................................................................
New 132/33 kV Substation at Kosba
Item No. | Description of Equipment Requirement |  | Unit | Quantity |  | Foreign Currency (in……….)
[6 empty] | Unit Price | Total Price
[6 empty] | CIP | CIP
|  |  |  | (1) |  | (2) | (3) = (1) x (2)
2E.A | 230 kV switchgear, equipment connection and steel structures
Deleted
2E.B | 145 kV Indoor Type Gas Insulated Switchgear (GIS), equipment connection and steel structures
2E.B1 | 145kV GIS Line Feeder Bays
| e) | For Kosba SS | set | 2
Each Line bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1600A, 40kA/3s, three phase, single pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1600A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1600A, 40kA/3s three phase line disconnector integral with high speed earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer with cores as follows | sets | 3
| vii. | 145kV single phase voltage transformer 2 core, Class 0.2 for Metering and Class 3P for Protection | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Panel | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2E.B2 | 145kV GIS Transformer Feeder Bays:
| e) | For Kosba SS | set | 2
Each transformer bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1600A, 40kA/3s, three phase, Gang pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1600A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1600A, 40kA/3s three phase line disconnector integral with earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer with cores as follows | No. | 3
| vii. | 145kV single phase voltage transformer 2 core, Class 0.2,10VA for Metering and Class 3P,15VA for Protection, | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Panel | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2E.B3 | 145kV Bus Coupler Bays :
| e) | For Kosba SS | set | 1
Each Bus Coupler Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase double busbar | lot | 1
| ii. | 145kV, 2500A, 40kA/3s, three phase, Gang pole operation circuit breaker complete with spring-stored energy operating mechanism | No. | 1
| iii. | 145kV, 2500A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Sets | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism, on either side of circuit breaker. | sets | 2
| v. | 145kV, 40kA/3s, single phase, 2-core, current transformer with cores as follows: | No. | 3
| vi. | 145kV, 2500A, 40kA/3s, single phase, 2-core, current transformers with cores as follows: | No. | 3
| vii. | Local Control Panel | set | 1
| viii. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, sepecial equipment as per specification etc. as appropriate | Lot | 1
2E.B4 | 145kV GIS Double Busbar with VT/ES :
| e) | For Kosba SS | Set | 1
Each GIS Double Busbar with VT/ES Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase double busbars | Lot | 1
| ii. | 145kV single phase, 2 core, voltage transformer | No. | 6
| iii. | 145kV, 40kA/3s, three phase, three position earth switches complete with motor operating Mechanism | Sets | 2
| iv. | Local Control Panel | Set | 1
2E.B5 | 120kV rated voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase surge arresters
| e) | For Kosba SS | No. | 12
2E.B6 | Rigid tubular bus and/or stranded conductors including accessories for each connection as required for completing 145kV GIS Switchyard
| i. | Tubular Conductor | Lot | 1
| ii | Flexible Conductor | Lot | 1
2E.B7 | insulator and fittings including all necessary clamps and connectors as required for completing 145kV GIS Switchyard
| i | _Insulator | Lot | 1
| ii | Fittings & Clamps_Connector | Lot | 1
| ii | Nut-bolt | Lot | 1
| iv. | _Cable trench including fitting, fixing accessories | Lot | 1
2E.B8 | Steel gantry, having double tier for each double circuit of 145kV Transmission Line including all necessary accessories required for completing 145kV GIS Switchyard
| a) | Steel Structure
| i. | _Gantry Column | No. | 4
| ii. | Beam | No. | 2
| iii. | Nut & Bolts | Lot | 1
| b) | Equipment Structure
| i. | LA | No. | 12
2E.C 33 kV Switchgear, equipment connection and steel structures
One (1) set of complete equipment for switchgear 33 kV shall be designed, supplied, delivered, installed, tested and commissioned, under this contract, comprise the following:
2E.C1 | Circuit Breaker 36 kV, 2500 A, 31.5kA/1s, 50 Hz, 170/70 kV BIL, three pole, vacuum type, for outdoor installation with one spring-stored energy operating mechanism |  | Set | 2
2E.C2 | Disconnector 36 kV, 2500 A, 31.5 kA/1s, 50 Hz, 170/70 kV BIL, three pole, single vertical break, post type, motor operated
| i) | DS without ES | set | 2
| ii) | DS with ES | set | 2
2E.C3 | Current transformer 36 kV, 31.5 kA/1s, 50Hz, 170/70 kV BIL, single phase, 630-1250/1/1 , 2-core, post type |  | nos. | 6
2E.C4 | Voltage transformer 36kV, 50Hz, 170/70 kV BIL, single phase, 33/V3 / 110/V3 / 110/V3 kV/V/V, 2 secondary windings, inductive type |  | No. | 6
2E.C5 | Surge arrester 36 kV, 30 kV continuous operating voltage, 10 kA nominal discharge current, 50 Hz, single phase, gapless, metal oxide type for all five (05) substations |  | No. | 6
2E.C6 | DS with load break fuse (6A) etc. for Connection between 36kV busbar & 02 sets of 33/0.415kV Earthing/Auxiliary transformer. |  | Set | 2
2E.C7 | Gantry steel structures for Bus & Equipment, Conductor for 36kV,3000A Bus bar, Insulator and fittings including all necessary clamps and connectors required to complete 33kV switchyard
| i. | Flexible conductor for Bus & Equipment connection | Lot | 1
| ii. | Insulators and fittings incl. all necessary clamps and connectors,Nut-Bolt required for completing 33 kV switchyard | Lot | 1
| iii. | Gantry steel structures for Bus
| a) | Beam | No | 4
| b) | Column | No | 6
| iv. | Gantry steel structures for Transformer
| a) | Beam | No | 2
| b) | Column | No | 3
| v. | steel structures for equipment supports required for completing 33 kV switchgear
| a) | CB,DS; CT,PT & LA ( 3 No.s= 1set) | set | 11
| vi. | XLPE Cable | Deleted
| vii. | Cable Sealing End | Deleted
| viii. | Cable trench | Lot | 1
2E.D |  | Transformers
2E.D1 |  | Deleted
2E.D2 |  | Three phase outdoor type two-winding power transformer, 132/36kV, 80/120MVA (ONAN/ONAF) | Set | 2
2E.D3 |  | On-line Dissolved Gas monitoring system for 230/138/33kV auto transformers | Deleted
2E.D4 |  | Earthing / Auxiliary Power Transformer 33/0.415 kV, three phase 250 kVA, Dyn11, ONAN , associated outdoor neutral CTs and steel support structures including all necessary connections. | Set | 2
2E.D5 |  | Complete Fire Fighting system for GIS Hall & Control Room
| i) | 230kV GIS Hall | Deleted
| ii) | 132kV GIS Hall | Lot | 1
| iii) | Panel & Control Room | Lot | 1
2E.D6 |  | Transformer Fire-Fighting system (water Spray type) for three phase outdoor type power transformer | Deleted
2E.E | Control, Protection, SAS and Metering
245kV Circuits
Deleted
145kV Circuits
2E.E1 |  | Control, Protection,monitoring & SAS function for overhead line circuits | set | 2
| a) | Control panel with Mimic & all accessories including monitoring | set | 2
| b) | Protection main relay (Main-1, Main-2) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 2
| d) | Protecttion Panel including wiring, lighting,heater & other accessories | set
2E2 |  | Control, Protection,monitoring & SAS function for Auto transformer circuits | set | 2
| a) | Control panel with Mimic & all accessories including monitoring | set | 2
| b) | Protection main relay (Main-1, Main-2) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 2
| d) | Protecttion Panel including wiring, lighting,heater & other accessories | set | 2
2E.E3 |  | Control, Protection,monitoring & SAS function for Bus Coupler circuits | set | 1
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main-1, Main-2) | set | 1
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Protecttion Panel including wiring, lighting,heater & other accessories | set | 1
2E.E3 |  | Busbar Protection | set | 1
| a) | Control panel with Mimic & all accessories including monitoring | NA
| b) | Protection main relay
| i. | Bay Unit | set | 5
| ii. | Central Unit | set | 1
| c) | Protection Auxiliary relay | set | 1
| d) | Protecttion Panel including wiring, lighting,heater & other accessories | set | 1
2E.E4 |  | Tariff metering
| a) | Meters (Main & Check) | No. | 8
| b) | Panel including wiring, lighting,heater & other accessories | lot | 1
36kV Circuit
2E.E5 |  | Control, Monitoring, Protection & SAS for 33kV station power system | Set | 2
| a) | Control Mimic panel with all accessories including monitoring | Lot | 1
| b) | Protection main relay (67,67N,50,50N,51,51N etc) | Set | 2
| c) | Auxiliary relays (TCS, Lockout etc) | Set | 2
| d) | Protecttion Panel including wiring, lighting,heater & other accessories | Lot | 1
2E.E6 |  | Tariff metering | lot | 1
| a) | Meters | No. | 4
| b) | Panel including wiring, lighting,heater & other accessories | lot | 1
2E.E7 | Substation Automation system
| i. | BCU/BCPU
| a) | for 245kV Circuits | No. | NA
| b) | for 145kV Circuits | No. | 5
| c) | 33kV Circuits | No. | 2
| ii. | Industrial Server PC cum Operator workstation with SAS & Enginering Software | Set | 2
| iii. | Ethernet Switch for SAS | Lot | 1
| iv. | GPS system | Set | 1
| v. | Common alarm unit with hooter/buzzer for annunciation | Set | 2
| vi. | LCD Monitor, 55" or Large | Set | 1
| vii. | Printer, A4 Laser (One black & White, Other Color) | Set | 2
| viii. | Engineering PC: core i7, 1TB HDD, 8GB RAM, 22'' display for SAS & SCADA | No. | 1
| ix. | Cable (Fiber Optic, Ethernet, Copper etc.)
| x. | Panel including wiring, lighting,heater & other accessories | Lot | 1
| xi. | Other Accessories (if any) | Lot | 1
2E.F | SCADA system for Telecontrol and Telemetering
| a) | Equipment at Substation
| i. | Gateway (server, engineering software) | Set | 2
| ii. | Ethernet Switch | Set | 2
| iii. | Hardware Firewall | Set | 1
| iv. | Additional 33kV Feeder BCU | set | 5
| v. | Panel including wiring, lighting,heater & other accessories | lot | 1
| vi. | Cables | lot | 1
| vii. | Other Accessories (if any) | lot | 1
| b) | Integration work with Master & Backup NLDC including Engineering & Commissioning | refere to Schedule B4
2E.G | Digital Fault & Disturbance Recorder
Deleted
2E.H |  | GIL & Power Cable
Deleted
2E.I |  | Multicore Cables
Multicore Cables for control, protection, metering & power circuits
| i. | _LV Control Cable | lot | 1
| ii. | _LV Power Cable | lot | 1
2E.J |  | Earthing and Lightning Protection system and Portable Eathing Equipment
2E.J1 |  | Earthing and Lightning Protection system
| i. | _Earthing system for complete substation | lot | 1
| ii. | _Lighting Protection System for complete substation | lot | 1
2E.J2 |  | Portable(maintenance) earthing equipment device | set | 1
2E.K |  | Batteries, chargers & DC distribution
2E.K1 |  | 110V Ni-cad Batteries with chargers & distribution board (including 2 sets 4kVA UPS, 30 mins) | lot | 1
| i. | _110V Battery Banks, 350Ah | set | 2
| ii. | _Charger 120A | set | 2
| iii. | _5kVA,30 mins Inverter | set | 1
| iv. | _110V DC Distribution panel, MCC type | lot | 1
2E.K2 |  | 48V Ni-cad Batteries with chargers & distribution board
| i. | _48V battery Banks,125Ah | set | 2
| ii. | _Charger, 50A | set | 2
| iii. | _48V DC Disatribution Panel | lot | 1
2E.L | LVAC Distribution
2E.L1 | _AC 415V or 240V distribution panels (MCC type) |  | lot | 1
2E.L2 | _Tariff metering at LV side(Main & Check) |  | No. | 4
2E.M | Civil Works, Building and Foundation
2E.M1 | Complete civil items required for outdoor works including boundary wall and slope protection |  | Refer to Schedule B4
2E.M2 | Complete civil works for GIS Hall, Operation & Panel Room
| i) | _Foundation works | Refer to Schedule B4
| ii) | _Super structures | Refer to Schedule B4
| iii) | _All finish works | Refer to Schedule B4
| iv) | _10 ton EOT Crane | No. | 1
| v) | 6 person lift | No | 1
2E.M3 | Testing of Foundation |  | Refer to Schedule B4
2E.M4 | Fire Fighting system for GIS Hall & Control Room
| i) | Fire Fighting system For GIS Room | Lot | 1
| ii) | Fire Fighting system For Operation & Panel Room | Lot | 1
2E.M5 | Complete Water spray system for transformers fire-fighting including reservoir, pipe network and pump etc. |  | Deleted
2E.N | Lighting, small power, air conditioning and Ventilation
2E.N1 | Indoor Lighting (LED type), small power, air conditioning and Ventilation and emergency DC lighting for control building and local control houses |  | lot | 1
2E.N2 | Lighting (LED type) for ouside building area for security, roadway, switchyard and emergency DC lighting |  | lot | 1
2E.N3 | Complete solar system (1kW solar panel) including 12V VRLA maintenace free battery and other accessories for Substation emergency DC Lighting |  | Set | 1
2E.O | Fibre Optic Multiplexer Equipment for Communication and Protection
2E.O1 | Indoor Fibre Optic Multipexer Equipment |  | lot | 1
2E.O2 | PABX Card & telephone set |  | lot | 1
2E.O3 | Under ground optical fiber cable, armoured, 48/24 core including Outdoor termination box,indoor MDF & pigtail cables |  | lot | 1
2E.O4 | PDH & SDH and 48/24 Core ODF with necessary connection work and testing shall be installed. |  | lot | 1
Total Price (for New Kosba 132/33kV SS) carried to Summary of Price Schedule
Total Price in words(for New Kosba 132/33kV SS)............................................................................................................................................................................
Extension of 230kV bays at 230/132 kV GIS GAZARIA Substation
Item No. | Description of Equipment Requirement |  | Unit | Quantity |  | Foreign Currency (in……….)
[6 empty] | Unit Price | Total Price
[6 empty] | CIP | CIP
|  |  |  | (1) |  | (2) | (3) = (1) x (2)
3A | 230 kV switchgear, equipment connection and steel structures
3A1 | 245kV GIS Line Feeder Bays, each comprising: |  | Set | 4
| i. | 245kV, 3150A, 50kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 245kV, 3150A, 50kA/3s, three phase, single pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 245kV, 3150A, 50kA/3s, three phase busbar disconnector complete with motor operating mechanism | sets | 2
| iv. | 245kV, 50kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 245kV, 3150A, 50kA/3s three phase line disconnector integral with high speed earth switch complete with motor operating mechanism | sets | 1
| vi | 245kV, 3150A, 50kA/3s single phase, 6-core, current transformer with cores as follows: | No. | 3
| vii. | 245kV single phase, 2 core, Class 0.2,10VA for Metering and Class 3P,15VA for Protection, voltage transformer | No. | 3
| viii. | 245kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Panel | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
3A2 | 245kV GIS Auto Transformer Feeder Bays, each comprising: |  | Deleted
3A3 | 245kV Bus Coupler Bays , each comprising: |  | Deleted
3A4 | 245kV GIS Double Busbar with VT/ES, each comprising: |  | Deleted
3A5 | 216kV rated voltage, 192kV(rms) continuous operating voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase surge arresters |  | No. | 12
3A6 | Rigid tubular bus and/or stranded conductors including accessories for each connection as required for completing 230kV GIS Switchyard
| i. | Tubular Conductor | Lot | 1
| ii | Flexible Conductor | Lot | 1
3A7 | Insulator and fittings including all necessary clamps and connectors as required for completing 230kV GIS Switchyard
| i | _Insulator | Lot | 1
| ii | Fittings & Clamps_Connector | Lot | 1
| ii | Nut-bolt | Lot | 1
| iv. | _Cable trench including fitting, fixing accessories | Lot | 1
3A8 | Steel gantry, having double tier for each double circuit of 230kV Transmission Line & Equipment support Structure including all necessary accessories required for completing 230kV GIS Switchyard
| a) | Steel Structure
| i. | _Gantry Column | No. | 5
| ii. | Beam | No. | 4
| iii. | Nut & Bolts | Lot | 1
| b) | Equipment Structure
| i. | LA | No. | 12
| ii. | CVT |  | Deleted
3B | 145 kV Indoor Type Gas Insulated Switchgear (GIS), equipment connection and steel structures
Deleted
3C | 36 kV Switchgear, equipment connection and steel structures
Deleted
3D |  | Transformers
Deleted
3E | Control, Protection, SAS and Metering
245kV Circuits
3E1 |  | Control, Protection,monitoring & SAS Function for overhead line circuits | set | 4
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | set | 1
| b) | Protection main relay (Main-1, Main-2) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
3E2 |  | Deleted
3E3 |  | Deleted
3E4 |  | Extension of Busbar Protection | lot | 1
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | NA
| b) | Protection main relay ( Bay Unit )
| i) | Central Unit extension card | set | 1
| ii) | Bay Unit with HMI | set | 4
| c) | Selector Switch for Enabling/Disabling BBP,BFP, all function | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | lot | 1
3E5 |  | Tarif metering
| a) | Meters | No. | 8
| b) | Panel including wiring, lighting,humidity controller, heater & other accessories | lot | 1
145kV Circuits
Deleted
36kV Circuit
Deleted
3E5 | Substation Automation system
| i. | BCU
| a) | for 245kV Circuits | No. | 4
| b) | for 145kV Circuits | No. | Deleted
| c) | 33kV Circuits | No. | Deleted
| ii. | Industrial Server PC cum Operator workstation with SAS & Enginering Software | Set | Deleted
| iii. | Ethernet Switch for SAS | Lot | 1
| iv. | GPS system | Set | Deleted
| v. | Common alarm unit with hooter/buzzer for annunciation | Set | Deleted
| vi. | LCD Monitor, 55" or Large | Set | Deleted
| vii. | Printer, A4 Laser (One black & White, Other Color) | Set | Deleted
| viii. | Engineering PC: core i7, 1TB HDD, 8GB RAM, 22'' display for SAS & SCADA | No. | Deleted
| ix. | Cable (Fiber Optic, Ethernet, Copper etc.) | Lot | 1
| x. | Panel including wiring, lighting,heater & other accessories | Lot | 1
| xi. | Other Accessories (if any) | Lot | 1
3F | Extension of SCADA system for Telecontrol and Telemetering
| a) | Equipment at Substation
| i. | Modification of Gateway (server, engineering software) | Set | 2
| ii. | Ethernet Switch | Set | Deleted
| iii. | Hardware Firewall | Set | Deleted
| iv. | Additional 33kV Feeder BCU | set | Deleted
| v. | Panel including wiring, lighting,heater & other accessories | lot | Deleted
| vi. | Cables | lot | Deleted
| vii. | Other Accessories (if any) | lot | Deleted
| b) | Integration work with Master & Backup NLDC including Engineering & Commissioning | refere to Schedule B4
3G | Digital Fault & Disturbance Recorder (Extension)
3G1 | i. | DFDR processor | Set | 1
| ii. | Card for each bay including A/D Converter, Digital & Analog data acquisition system
| a) | for 245kV Circuits | set | 4
| b) | for 145kV Circuits | Deleted
| iii. | Ethernet Switch | Deleted
| iv | GPS system | Deleted
| v. | Panel including wiring, lighting,heater & other accessories | Lot | 1
| vi. | Engineering PC: core i7, 500GB HDD, 8GB RAM, 17'' display | set | Deleted
3H |  | GIL & Power Cable
Deleted
3I |  | Multicore Cables
Multicore Cables for control, protection, metering & power circuits
| i. | _LV Control Cable | lot | 1
| ii. | _LV Power Cable | lot | 1
3J |  | Earthing and Lightning Protection system and Portable Eathing Equipment
3J1 |  | Earthing and Lightning Protection system
| i. | _Extension of Earthing system for bay extension work | lot | 1
| ii. | _Extension of Lighting Protection System for bay extension work | lot | 1
3J2 |  | Portable(maintenance) earthing equipment device | set | 1
3K |  | Batteries, chargers & DC distribution
3K1 |  | 110V Ni-cad Batteries with chargers & distribution board (including 2 sets 4kVA Inverter)
| i. | _110V Battery Banks, 600Ah | Deleted
| ii. | _Charger 600A | Deleted
| iii. | _4kVA Inverter | Deleted
| iv. | _ Extension of 110V DC Distribution panel, MCC type | lot | 1
3K2 |  | 48V Ni-cad Batteries with chargers & distribution board
| i. | _48V battery Banks,150Ah | Deleted
| ii. | _Charger 70A | Deleted
| iii. | _Extension of 48V DC Disatribution Panel | lot | 1
3L | LVAC Distribution
3K1 | _Extension of AC 415V or 240V distribution panels (MCC type) |  | lot | 1
3K2 | _Tariff metering at LV side(Main & Check) |  | Deleted
3M | Civil Works, Building and Foundation |  | Refer to Schedule B4
3N | Lighting, small power, air conditioning and Ventilation
3N1 | Indoor Lighting (LED type), small power, air conditioning and Ventilation and emergency DC lighting required for bay extension work for control building and local control houses |  | lot | 1
3N2 | Lighting (LED type) for ouside building required for bay extension work for security, roadway, switchyard and emergency DC lighting |  | lot | 1
3O | Fibre Optic Multiplexer Equipment for Communication and Protection
3O1 | Extension of Indoor Fibre Optic Multipexer Equipment |  | lot | 1
3O2 | PABX Card & telephone set |  | Deleted
3O3 | Under ground optical fiber cable, armoured, 48 core including Outdoor termination box,indoor MDF & pigtail cables |  | lot | 1
3O4 | Extension of PDH & SDH and 48 Core ODF with necessary connection work and testing shall be installed. |  | lot | 1
Total Price (for Extension works at GAZARIA SS) carried to Summary of Price Schedule
Total Price in words (for Extension works at GAZARIA SS)............................................................................................................................................................................
Extension of 132kV AIS bays at 230/132 kV Comilla (North) AIS Substation
Item No. | Description of Equipment Requirement |  | Unit | Quantity |  | Foreign Currency (in……….)
[6 empty] | Unit Price | Total Price
[6 empty] | CIP | CIP
|  |  |  | (1) |  | (2) | (3) = (1) x (2)
4A | 230 kV switchgear, equipment connection and steel structures
Deleted
4B | 145 kV Indoor Type Gas Insulated Switchgear (GIS), equipment connection and steel structures
Deleted
145 kV Indoor Type Air Insulated Switchgear (AIS), equipment connection and steel structures
4B1 |  | SF6 Circuit breaker,1600A, 40kA/1s,live tank, single pole operating for Line Bay | Set | 2
4B2 |  | Disconnector switch without E/S, 1600A,40kA/1s for Line bay | Set | 4
4B3 |  | Disconnector switch with E/S, 1600A,40kA/1s | Set | 2
4B4 |  | Disconnector switch without E/S, 1600A,40kA/1s | Set | 2
4B5 |  | Single phase current transformer, 5-core,40kA/1s | No. | 6
4B6 |  | Single phase Inductive voltage transformer (VT), 2-core, | No. | 6
4B7 |  | Single phase surge arrester, 120kV rated,10kA | No. | 6
4B8 |  | Flexible conductorsfor bus and jumper, insulators, fittings including all necessary clamps and connectors for extension work
| i. | _Flexible Conductor for Bus, jumper, equipment connections | Lot | 1
| ii. | _Insulator | Lot | 1
| iii. | _Fittings | Lot | 1
4B9 |  | Steel Structures for gantry and equipment supports required for this extension work
| a) | _Gantry Column including nut & bolts
| i) | For Main Bus | nos. | 2
| ii) | For Jack-Bus | nos. | 2
| b) | _Gantry beam at Main Bus & Jack-Bus height including nut & bolts | nos. | 4
| c) | _Equipment support structures including nut & bolts
| i) | CB | set | 2
| ii) | DS without ES | set | 6
| iii) | DS with ES | set | 2
| iv) | Bus ES | Deleted
| v) | CT | nos. | 6
| vi) | CVT/IVT | nos. | 6
| vii) | LA | nos. | 6
| ix) | PI | Deleted
| d) | _Cable tray including fitting, fixing accessories | lot | 1
4C | 33 kV Switchgear, equipment connection and steel structures
Deleted
4D |  | Transformers
Deleted
4E | Control, Protection, SAS and Metering
245kV Circuits
Deleted
145kV Circuits
4E1 |  | Control, Protection,monitoring & SAS Function for overhead line circuits | set | 2
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main-1, Main-2) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
4E2 |  | Deleted
4E3 |  | Deleted
4E4 |  | Extension of Busbar Protection | lot | 1
| a) | Control Mimic panel with all accessories including monitoring | NA
| b) | Protection main relay
| i) | Central Unit extension card | lot | 1
| ii) | Bay Unit with HMI | lot | 1
| c) | Selector Switch for Enabling/Disabling BBP,BFP, all function | lot | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories
4E5 |  | Tarif metering | lot | 1
| a) | Meters | No. | 4
| b) | Panel including wiring, lighting,heater, humidity sensor & other accessories | lot | 1
36kV Circuit
Deleted
4E6 | Substation Automation system |  | Deleted
| i. | BCU
| a) | for 245kV Circuits | No. | #REF!
| b) | for 145kV Circuits | No. | #REF!
| c) | 33kV Circuits | No. | #REF!
| ii. | Industrial Server PC ( and/ HMI) with SAS & Enginering Software | Set | 2
| iii. | Ethernet Switch for SAS | Lot | 1
| iv. | GPS system | Set | 1
| v. | Operator workstation | Set | 2
| vi. | LCD Monitor, 55" or Large | Set | 1
| vii. | Printer, A4 Laser (One black & White, Other Color) | Set | 2
| viii. | Engineering PC: core i7, 1TB HDD, 8GB RAM, 22'' display for SAS & SCADA | No. | 1
| ix. | Cable (Fiber Optic, Ethernet, Copper etc.) | Lot | 1
| x. | Panel including wiring, lighting,heater & other accessories | Lot | 1
| xi. | Other Accessories (if any) | Lot | 1
4F | SCADA system for Telecontrol and Telemetering |  |  | 1
| a) | Extension of SCADA system including hardwire & software modification in existing RTU/gateway, Supply of IED/transducer, sub-rack with I/O card, CPU, necessary wiring required for MiCOM264 RTU | lot | 1
| b) | Integration work with Master & Backup NLDC including Engineering & Commissioning | refere to Schedule B4
4G | Digital Fault & Disturbance Recorder |  | Deleted
4H |  | GIL & Power Cable | Deleted
4I |  | Multicore Cables
Multicore Cables for control, protection, metering & power circuits
| i. | _LV Control Cable | lot | 1
| ii. | _LV Power Cable | lot | 1
4J |  | Earthing and Lightning Protection system and Portable Eathing Equipment
1J1 |  | Earthing and Lightning Protection system
| i. | _Extension of Earthing system for bay extension work | lot | 1
| ii. | _Extension of Lighting Protection System for bay extension work | lot | 1
4J2 |  | Portable(maintenance) earthing equipment device | set | 1
4K |  | Batteries, chargers & DC distribution
4K1 |  | 110V Ni-cad Batteries with chargers & distribution board (including 2 sets 4kVA UPS, 30 mins)
| i. | _110V Battery Banks, 500Ah | Deleted
| ii. | _Charger 170A | Deleted
| iii. | _4kVA Inverter | Deleted
| iv. | _ Extension of 110V DC Distribution panel, MCC type | lot | 1
4K2 |  | 48V Ni-cad Batteries with chargers & distribution board
| i. | _48V battery Banks,150Ah | Deleted
| ii. | _Charger 70A | Deleted
| iii. | _Extension of 48V DC Disatribution Panel | lot | 1
4L | LVAC Distribution
4L1 | _Extension of AC 415V or 240V distribution panels (MCC type) |  | lot | 1
4L2 | _Tariff metering at LV side(Main & Check) |  | Deleted
4M | Civil Works, Building and Foundation |  | Refer to Schedule B4
4N | Lighting, small power, air conditioning and Ventilation
4N1 | Indoor Lighting (LED type), small power, air conditioning and Ventilation and emergency DC lighting required for bay extension work for control building and local control houses |  | Deleted
4N2 | Lighting (LED type) for ouside building required for bay extension work for security, roadway, switchyard and emergency DC lighting |  | lot | 1
4O | Fibre Optic Multiplexer Equipment and PLC Equipment for Communication and Protection
4O1 | Extension of Indoor Fibre Optic Multipexer Equipment |  | lot | 1
4O2 | PABX Card & telephone set |  | Deleted
4O3 | Under ground optical fiber cable, armoured, 48 core including Outdoor termination box,indoor MDF & pigtail cables |  | lot | 1
4O4 | Extension of PDH & SDH and 48 Core ODF with necessary connection work and testing shall be installed. |  | lot | 1
Total Price (for Extension works at Comilla(N) SS) carried to Summary of Price Schedule
Total Price in words (for Extension works at Comilla(N) SS)............................................................................................................................................................................
Schedule B1: Mandatory Spare, Maintanence & Test Equipement Supplied from Outside the Employer's Country
| Item | Description | Unit | Qty | Country | Unit Price1 | Total Price1
of origin
[6 empty] | CIP | CIP
|  |  |  | 1 |  | 2 | 3=1x2
230 kV GIS
| 1 | Complete three position ES module | set | 6
| 2 | Complete HES module | sets | 6
| 3 | Set of interrupting chamber including insulators, fixed and moving contacts for offered type circuit breaklers | sets | 2
| 4 | surge arrester | nos. | 6
| 5 | voltage transformer module | nos. | 10
| 6 | Closing coils | nos. | 10
| 7 | Tripping coils | nos. | 10
| 8 | Motor for circuit breaker operating mechanism | nos. | 2
| 9 | Motor for disconnector drive | nos. | 2
| 10 | Coils for Blocking magnet in disconnector drive | nos. | 3
| 13 | Gas pressure monitor | No | 5
| 14 | Gas pressure switch | No | 5
| 15 | Gas pressure gauge | No | 5
| 16 | Pressure Relief Device | No | 5
| 17 | Supporting insulator with barrier | No | 5
132kV GIS
| 13 | Complete three position ES module | set | 6
| 14 | Complete HES module | sets | 6
| 15 | Set of interrupting chamber including insulators, fixed and moving contacts for offered type circuit breaklers | sets | 2
| 16 | surge arrester | nos. | 20
| 17 | Voltage transformer module | nos. | 30
| 18 | Closing coils | nos. | 10
| 19 | Tripping coils | nos. | 10
| 20 | Motor for circuit breaker operating mechanism | nos. | 2
| 21 | Motor for disconnector drive | nos. | 2
| 22 | Coils for Blocking magnet in disconnector drive | nos. | 3
| 23 | Gas pressure monitor | No | 15
| 24 | Gas pressure switch | No | 15
| 25 | Gas pressure gauge | No | 15
| 26 | Pressure Relief Device | No | 15
| 27 | Supporting insulator with barrier | No | 15
TRANSFORMERS
| 28 | Auto-transformer 245kV bushings | nos. | 1
| 29 | transformer 145 kV bushings | nos. | 12
| 30 | Neutral Bushing | No | 6
| 31 | 36kV Bushing | no. | 10
| 32 | WTI | No. | 30
| 33 | OTI | No. | 30
| 34 | Gas pressure relief device | No | 14
| 35 | Earthing transformer 36 kV bushings | nos. | 1
| 36 | Sets of auto transformer gaskets | sets | 1
| 37 | Sets of earthing transformer gaskets | sets | 1
| 38 | Sets of tap changer spares | sets | 1
| 39 | Set of special tools, gauges and spanners (Bidders to give details) | set | 1
| 40 | Spare transformer oil | kg/substation | 32000
| 41 | Silica gel with breather 100% spare | lot | 1
| 42 | Transformer oil treatment plant, 8000litre/hr (Clause 4.13.2) | set | 3
Transformer Protector SYSTEM
| 43 | Nitrogen Cylinder set per Substation | set | 1
| 44 | Rupture disk as per number of TP’s in a substation | lot | 1
| 45 | Electrical Actuator as per number of TP’s in a substation; | lot | 1
| 46 | Isolation valve sensors | set | 2
| 47 | LHD set | set | 1
Water Spray system
| 48 | Warter spray nozzles | nos. | 10
| 49 | Release sprinklers | nos. | 5
| 50 | Set of internal parts of deluge valve | set | 1
| 51 | Set of sealings for deluge valves of each type | set | 1
| 52 | Set of sealings for pipes and flanges | set | 1
| 53 | Set of spare parts for jockey pump | set | 1
| 54 | Set of spare parts for control panel and automatic level indicator | set | 1
| 55 | Set of spare parts for the air supply and reducing devices | set | 1
| 56 | Fire fighting pump complete with coupling | set | 1
Miscellaneous
| 57 | SF6 evacuation and filling plant | set | 6
| 58 | XLPE termination kits | set | 6
| 59 | All types of control valves for SF6 gas | lot/substation | 6
| 60 | Rubber gaskets “O” rings and seals for SF6 gas | lot/substation | 6
PROTECTION, CONTROL, METERING
| 61 | Distance relay | set | 7
| 62 | Current differential relay | set | 2
| 63 | Biased different relay (3-phase) | set | 7
| 64 | Two pole overcurrent and earth fault relay | sets | 14
| 65 | Tripping relay (electrical reset) | sets | 15
| 66 | Trip circuit supervision relay | sets | 15
| 67 | Relay Test Block & socket | sets | 15
| 68 | BCU | No. | 10
| 69 | BCPU | No. | 10
| 70 | Heater | No | 150
| 71 | Humidity Sensors | No. | 150
| 72 | Humidity stat and thermostat | No. | 150
| 73 | Ammeter | nos. | 20
| 74 | Voltmeter | nos. | 20
| 75 | Annunciator bulbs | nos. | 200
| 76 | Bulbs for discrepancy switches | nos. | 100
| 77 | kWh & kVarh meter | nos. | 15
POWER & CONTROL CABLES
Spare cable comprising:
| 78 | control cable, 7 core | meter | 1000
| 79 | control cable, 12 core | meter | 1000
| 80 | Batteries, Chargers, & DC Distribution
| 81 | Battery fuses | nos. | 40
| 82 | Set DC board incoming MCCB | sets | 15
| 83 | Sets outgoing MCBs | sets | 20
LV AC SWITCHGEAR
| 84 | 3-phase set LVAC board incoming MCCB | no. | 15
| 85 | 3-phase sets outgoing MCCBs | nos. | 30
| 86 | 1-phase sets outgoing MCBs | nos. | 30
Fiber Optic Multiplexer Equipment
| 87 | Set of spare modules of necessary function | lot | 1
TEST and O&M EQUIPMENT
| 88 | Set of gas filling/handling equipment with all accessories | sets | 6
| 89 | 1 cylinder of SF6 gas with valve | sets | 7
| 90 | SF6 gas sniffer | sets | 14
| 91 | SF6 density monitoring device | sets | 12
| 92 | SF6 pressure monitring device | sets | 12
| 93 | Offline Partial Discharge monitoring Device for GIS | set | 7
| 94 | Portable vacuum pump suitable for SF6 circuit breaker | set | 2
| 95 | circuit breaker operational analyzer with accessories including connecting lead | set | 24
| 96 | Contact resistance measurement test set (suitable for measurement down to 1 µ ohm at 10A d.c.) | set | 7
| 97 | 5 kV insulation resistance test set (range 0.5 –1.0 - 2.5 - 5 kV) | sets | 7
| 98 | Earth resistance test set (range 10-100-1000 ohm: min scale division 0.1 ohm) | sets | 7
| 99 | Clip-on mA meter (for spill current) | nos. | 7
| 100 | set of Tools for each substation ( as per table 01 of clause 1.4.4 of volume 02) | set | 6
| 101 | set of Tools (Gas leakage detector, oxygen analyzer, moisture meter ) for GIS at each substation as per clause 3.4.5 of volume 02 | set | 6
Total Price carried to Summary of Price Schedule (Spare Parts)
Total Price in words............................................................................................................................................................................

## Schedule B2
Schedule B2: Plant & Equipment supplied from within Employer's Country
New 230/132/33 kV Substation at KACHUA
Item No. | Description of Equipment Requirement |  | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
[5 empty] | Unit Price | Total Price | Unit Price | Total Price
[5 empty] | CIP | CIP | EXW | EXW
|  |  |  | (1) | (2) | (3) = (1) x (2) | (4) | (5)=(1)x(4)
1A | 230 kV switchgear, equipment connection and steel structures
1A1 | 245kV GIS Line Feeder Bays, each comprising: |  | Set | 8
| i. | 245kV, 4000A, 50kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 245kV, 3150A, 50kA/3s, three phase, single pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 245kV,3150A, 50kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 245kV, 50kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 245kV, 2000A, 50kA/3s three phase line disconnector integral with high speed earth switch complete with motor operating mechanism | sets | 1
| vi | 245kV,50kA/3s single phase, 5-core, current transformer | No. | 3
| vii. | 245kV single phase, 2 core, Class 0.2, 10VA for Metering and Class 3P,15VA for Protection, voltage transformer | No. | 3
| viii. | 245kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Cubicle | set | 1
| x | Offline PD Monitoring facility in compartments | Lot | 1
| xi. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
1A2 | 245kV GIS Auto Transformer Feeder Bays, each comprising: |  | Set | 2
| i. | 245kV, 4000A, 50kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 245kV, 3150A, 50kA/3s, three phase, Gang pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 245kV, 3150A, 50kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 245kV, 50kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 245kV, 3150A, 50kA/3s, three phase line side disconnector with earth switch complete with motor operating mechanism | sets | 1
| vi | 245kV, 3200A, 50kA/3s, single phase, 5-core, current transformer | No. | 3
| vii. | 245kV single phase, 2 core, Class 0.2,10VA for Metering and Class 3P,15VA for Protection, voltage transformer | No. | 3
| viii. | 245kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Cubicle | No. | 1
| x | Offline PD Monitoring facility in compartments | Lot | 1
| xi. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for single-core cables, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
1A3 | 245kV Bus Coupler Bays , each comprising: |  | set | 1
| i. | 245kV, 4000A, 50kA/3s, three phase double busbar | Lot | 1
| ii. | 245kV, 50kA/3s, three phase, gang pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| ii. | 245kV, 50kA/3s, three phase busbar disconnector complete with motor operating mechanism | Set | 2
| iv. | 245kV, 50kA/3s, three phase, three position earth switch complete with motor operating mechanism, on either side of circuit breaker. | Set | 2
| v. | 245kV, 50kA/3s, single phase, 3-core, current transformer | No. | 3
| vi. | 245kV, 50kA/3s, single phase, 2-core, current transformers | No. | 3
| vii. | Local Control Cubicle | set | 1
| viii. | Offline PD Monitoring facility in compartments | Lot | 1
| ix. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
1A4 | 245kV GIS Double Busbar with VT/ES, each comprising: |  | Set | 1
| i. | 245kV, 4000A, 50kV/3s, three phase double busbars | Lot | 1
| ii. | 245kV single phase, 2 core, Class 0.2, 10VA for Metering and Class 3P, 15VA for Protection, voltage transformer | No. | 6
| iii. | 245kV, 50kA/3s, three phase, three position earth switches complete with motor operating Mechanism | set | 2
| iv. | Offline PD Monitoring facility in compartments | Lot | 1
| v. | Local Control Cubicle | No. | 1
1A5 | 216kV rated voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase surge arresters |  | No. | 30
1A6 | Rigid tubular conductor and/or stranded conductors including accessories for each connection as required for completing 230kV GIS Switchyard
| i. | Tubular Conductor | Lot | 1
| ii | Flexible Conductor | Lot | 1
1A7 | Insulator and fittings including all necessary clamps and connectors as required for completing 230kV GIS Switchyard
| i | Insulator | Lot | 1
| ii | Fittings & Clamps_Connector | Lot | 1
| ii | Nut-bolt | Lot | 1
| iv. | Cable trench including fitting, fixing accessories | Lot | 1
1A8 | Steel gantry, having double tier for each double circuit of 230kV Transmission Line & Equipment support Structure including all necessary accessories required for completing 230kV GIS Switchyard
| a) | Steel Structure
| i. | Gantry Column | No. | 10
| ii. | Beam | No. | 8
| iii. | Nut & Bolts | Lot | 1
| b) | Equipment Structure
| i. | LA | No. | 30
| ii. | CVT |  | Deleted
1B | 145 kV Indoor Type Gas Insulated Switchgear (GIS), equipment connection and steel structures
145 kV Indoor Type Gas Insulated Switchgear (GIS),
Deleted
145 kV Outdoor Type Air Insulated Switchgear (AIS)
1B1 | SF6 Circuit breaker,1600A,40kA/1s, live tank, single pole operating for Line Bay |  | set | 2
1B2 | SF6 Circuit breaker,2500A, 40kA/1s,live tank, gang operating for Transformer Bay |  | set | 2
1B3 | Disconnector switch without E/S, 1600A,40kA/1s for Line bay |  | set | 4
1B4 | Disconnector switch with E/S, 1600A,40kA/1s for Line Bay |  | set | 2
1B5 | Disconnector switch without E/S, 2500A,40kA/1s for Transformer Bay |  | set | 4
1B6 | Disconnector switch with E/S, 2500A,40kA/1s for Transformer Bay |  | set | 2
1B7 | Single phase current transformer,1600-3200/1, 5-core,40kA/1s for Line Bay |  | nos. | 6
1B8 | Single phase current transformer,2000-3200/1, 5-core,40kA/1s for tansformer bay |  | nos. | 6
1B9 | Single phase voltage transformer (VT), 3-core |  | nos. | 12
1B10 | 120kV rated voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase surge arresters |  | No. | 12
1B11 | Rigid tubular bus and/or stranded conductors including accessories for each connection as required for completing 145kV GIS Switchyard
| i. | Tubular Conductor | Lot | 1
| ii | Flexible Conductor | Lot | 1
1B12 | insulator and fittings including all necessary clamps and connectors as required for completing 145kV GIS Switchyard
| i | Insulator | Lot | 1
| ii | Fittings & Clamps_Connector | Lot | 1
| ii | Nut-bolt | Lot | 1
| iv. | Cable trench including fitting, fixing accessories | Lot | 1
1B13 | steel gantry, having double tier for each double circuit of 145kV Transmission Line including all necessary accessories required for completing 145kV GIS Switchyard
| a) | Steel Structure
| i. | _Gantry Column | No. | 5
| ii. | Beam
| 1) | at Bus Height | No. | 2
| 2) | at Jack-Bus Height | No. | 2
| iii. | Nut & Bolts | Lot | 1
| b) | Equipment Structure
| i. | CB | set | 4
| ii. | DS without ES | set | 8
| ii. | DS with ES | set | 4
| iv. | Bus ES | Deleted
| v. | CT | nos. | 12
| vi. | CVT/IVT | nos. | 12
| vii. | LA | nos. | 12
1C | 33 kV Switchgear, equipment connection and steel structures
One (1) set of complete equipment for switchgear 33 kV shall be designed, supplied, delivered, installed, tested and commissioned, under this contract, comprise the following:
1C1 | Circuit Breaker 36 kV, 630 A, 31.5kA/1s, 50 Hz, 170/70 kV BIL, three pole, vacuum type, for outdoor installation with one spring-stored energy operating mechanism |  | Set | 2
1C2 | Disconnector 36 kV, 630 A, 31.5kA/1s, 50 Hz, 170/70 kV BIL, three pole, single vertical break, post type, motor operated
| i) | DS without ES | set | 2
| ii) | DS with ES | set | 2
1C3 | Current transformer 36 kV, 31.5kA/1s, 50Hz, 170/70 kV BIL, single phase, 630-1250/1/1 , 2-core, post type |  | nos. | 6
1C4 | Voltage transformer 36kV, 50Hz, 170/70 kV BIL, single phase, 33/V3 / 110/V3 / 110/V3 kV/V/V, 2 secondary windings, inductive type |  | nos. | 6
1C5 | Surge arrester 36 kV, 30 kV continuous operating voltage, 10 kA nominal discharge current, 50 Hz, single phase, gapless, metal oxide type |  | nos. | 6
1C6 | Gantry steel structures for Bus & Equipment, Conductor for 36kV Bus bar & equipment, 36kV XLPE cable for Tertiary side connection from power trans-former, Insulator and fittings including all necessary clamps and connectors, cable trench required to complete 33kV switchyard.
| i. | Flexible conductor for Bus & Equipment connection | Lot | 1
| ii. | Insulators and fittings incl. all necessary clamps and connectors,Nut-Bolt required for completing 33 kV switchyard | Lot | 1
| iii. | Gantry steel structures for Bus
| a) | Beam | No | 4
| b) | Column | No | 6
| iv. | steel structures for equipment supports required for completing 33 kV switchgear
| a) | CB,DS; CT,PT & LA ( 3 no.'s= 1set) | set | 12
| v. | XLPE Cable | m | 120
| vi. | Cable Sealing End | No | 12
| vii. | Cable trench | Lot | 1
1D |  | Transformers
1D1 |  | Autotransformer 230/135/34.5 kV three phase ONAF 350/350/100 MVA, ONAN 250/250/70 MVA, YNa0d1, with On-load tap changer, with tertiary winding (brought out to terminal bushings) | Set | 2
1D2 |  | Deleted
1D3 |  | On-line Dissolved Gas Analyzer & Moisture monitoring system for 230/135/34.5kV auto transformers | Set | 2
1D4 |  | Earthing / Auxiliary Power Transformer 33/0.415 kV, three phase 350 kVA, ZNyn11, ONAN, with Off-load tap changer, associated outdoor neutral CTs and steel support structures including all necessary connections. | Set | 2
1D5 |  | Complete Fire Fighting system for GIS Hall & Control Room
| i) | 230kV GIS Hall | lot | 1
| ii) | 132kV GIS Hall | Deleted
| iii) | Panel & Control Room | Lot | 1
1D6 | a) | Fast Depressurization system for three phase outdoor type auto transformer | Set | 2
| b) | Water Spray system for three phase outdoor type auto transformer | Set | 2
1E | Control, Protection, SAS and Metering
245kV Circuits
1E1 | Control, Protection,monitoring & SAS Function for overhead line circuits |  | set | 8
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | set | 1
| b) | Protection main relays, Main-1 & Main-2 | set | 2
| c) | Auxiliary relays (TCS, Lockout etc) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
1E2 |  | Control, monitoring, Protection, monitoring & SAS Function for Auto transformer circuits | set | 2
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | set | 1
| b) | Protection main relay (Main-1, Main-2) | set | 2
| c) | Auxiliary relays (TCS, Lockout etc) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
1E3 |  | Control, Protection,monitoring & SAS Function for Bus Coupler circuits | set | 1
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | set | 1
| b) | Protection main relay | set | 1
| c) | Auxiliary relays (TCS, Lockout etc) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
1E4 |  | Busbar Protection | set | 1
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | NA
| b) | Protection main relay
| i. | Bay unit with HMI | set | 11
| ii. | Central unit with HMI | set | 1
| c) | Selector Switch for Enabling/Disabling BBP,BFP, all function | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
1E5 |  | Tarif metering
| a) | Meters (Main & Check) | No. | 20
| b) | Panel including wiring, lighting,humidity controller, heater & other accessories | lot | 1
145kV Circuits
1E6 |  | Control, Protection,monitoring & SAS for overhead line circuits | set | 2
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | set | 1
| b) | Protection main relay (Main-1, Main-2) | set | 2
| c) | Auxiliary relays (TCS, Lockout etc) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
1E7 |  | Control, Protection,monitoring & SAS for Auto transformer circuits | set | 2
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | set | 1
| b) | Protection main relay (as Backup: 67,67N,50,50N,51,51N) | set | 2
| c) | Auxiliary relays (TCS, Lockout etc) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
1E8 |  | Deleted
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | set | 1
| b) | Protection main relay | set | 1
| c) | Auxiliary relays (TCS, Lockout etc) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
1E9 |  | Busbar Protection | set | 1
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | NA
| b) | Protection main relay
| i. | Bay unit with HMI | set | 4
| ii. | Central unit HMI | set | 1
| c) | Selector Switch for Enabling/Disabling BBP,BFP, all function | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
1E10 |  | Tariff metering
| a) | Meters | No. | 8
| b) | Panel including wiring, lighting,heater, humidity controller & other accessories | lot | 1
36kV Circuit
1E11 |  | Control, Monitoring, Protection & SAS function for 33kV station power system | Set | 2
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | Set | 1
| b) | Protection main relay ( as backup: 67,67N,50,50N,51,51N) | Set | 1
| c) | Auxiliary relays (TCS, Lockout etc) | Set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | Set | 1
1E12 |  | Tariff metering
| a) | Meters (Main & Check) | No. | 4
| b) | Panel including wiring, lighting,heater, humidity sensor & other accessories | set | 1
1E13 | Substation Automation system
| i. | BCU
| a) | for 245kV Circuits | No. | 11
| b) | for 145kV Circuits | No. | 4
| c) | 33kV Circuits | No. | 2
| ii. | Industrial Server PC ( Intel XEON Silver- 4116 processor, ECC memory) cum Operator workstation with SAS & Enginering Software | Set | 2
| iii. | Ethernet Switch for SAS | Lot | 1
| iv. | GPS system | Set | 1
| v. | Common alarm unit with hooter/buzzer for annunciation | Set | 1
| vi. | LCD Monitor, 55" or Large | Set | 1
| vii. | Printer, A4 Laser (One black & White, Other Color) | Set | 2
| viii. | Engineering PC: core i7-9800X series processor, 1TB HDD, 16GB RAM, 22'' display for SAS & SCADA | No. | 1
| ix. | Cable (Fiber Optic, Ethernet, Copper etc.) | Lot | 1
| x. | Panel including wiring, lighting,heater & other accessories | Lot | 1
| xi. | Other Accessories (if any) | Lot | 1
1F | SCADA system for Telecontrol and Telemetering
| a) | Equipment at Substation
| i. | Gateway (server, engineering software) | Set | 2
| ii. | Ethernet Switch | Set | 2
| iii. | Hardware Firewall | Set | 1
| iv. | Additional 33kV Feeder BCU | set | 5
| v. | Panel including wiring, lighting,heater, humidity controller & other accessories | lot | 1
| vi. | Cables | lot | 1
| vii. | Other Accessories (if any) | lot | 1
1E13 |  | Substation Automation system
| i. | BCU
| a) | for 245kV Circuits | No. | 11
| b) | for 145kV Circuits | No. | 4
| ii. | CPU
| a) | Industrial Server PC | Set | 2
| b) | HMI PC | Set | 2
| iii. | Softwares
| a) | Operating System | set | 1
| b) | SAS Enginering Software/tool | set | 1
| c) | SAS Software | set | 1
| iv. | Ethernet Switch | Lot | 1
| v. | GPS system | Set | 1
| vi. | Modem | Set | 1
| vii. | PC small Monitor & Keyboard | Set | 2
| viii. | LCD Monitor, 55" or Large | Set | 1
| ix. | Gateway | Set | 2
| x. | Printer, A4 Laser (One black & White, Other Color) | Set | 2
| xi. | Laptop: core i7, 500GB HDD, 8GB RAM, 17'' display | No. | 1
| xii. | Cable | Lot | 1
| a) | Fiber Optic Cable
| b) | Ehternet/LAN Cable | Lot | 1
| c) | Copper Cable | Lot | 1
| xiii. | Panel including wiring, lighting,heater & other accessories | Lot | 1
| xiv. | Other Accessories | Lot | 1
| b) | Integration work with Master & Backup NLDC including Engineering & Commissioning | refer to Schedule B4
1G | Digital Fault & Disturbance Recorder
1G1 | i. | DFDR processor | Set | 1
| ii. | Card for each bay including A/D Converter, Digital & Analog data acquisition system
| a) | for 245kV Circuits | set | 11
| b) | for 145kV Circuits | set | 4
| iii. | Ethernet Switch | set | 1
| iv | GPS system | set | 1
| v. | Panel including wiring, lighting, heater, humidity sensor & other accessories | Lot | 1
| vi. | Engineering PC: core i7-9700K, 1 TB HDD, 16GB RAM, 17'' display | set | 1
1H | GIL & Power Cable
1H1 | 132kV, 2000A GIL for connection between secondary side of Power transformer & 132kV switchgear near existing 132kV AIS Bus
| i) | GIL | m | 240
| ii) | SF6-Air Bushing | No. | 12
1H2 | 132kV, 2000A rated in Buried Soil XLPE power cable for con-nection between secondary side of Power transformer & 132kV switchgear near existing 132kV AIS Bus
| i) | Cable | m | 720
| ii) | Cable sealing End | No. | 12
1H3 | 36kV, 300 mm2 XLPE power cable for connection between tertiary side of Power transformer & 33/0.415kV Auxiliary transformer.
| i) | Cable | m | 120
| ii) | Cable sealing End | No. | 12
1I | Multicore Cables
Multicore Cables for control, protection, metering & power circuits
| i. | _LV Control Cable | lot | 1
| ii. | _LV Power Cable | lot | 1
1J | Earthing and Lightning Protection system and Portable Eathing Equipment
1J1 | Earthing and Lightning Protection system
| i. | _Earthing system for complete substation | lot | 1
| ii. | _Lighting Protection System for complete substation | lot | 1
1J2 | Portable(maintenance) earthing equipment device |  | set | 2
1K | Batteries, chargers & DC distribution
1K1 | 110V Ni-cad Batteries with chargers & distribution board (including 2 sets 5kVA Inverter) |  | lot | 1
| i. | _110V Battery Banks, 600Ah | set | 2
| ii. | _Charger 220A | set | 2
| iii. | _5kVA Inverter | set | 2
| iv. | _110V DC Distribution panel, MCC type | lot | 1
1K2 |  | 48V Ni-cad Batteries with chargers & distribution board
| i. | _48V battery Banks,150Ah | set | 2
| ii. | _Charger 70A | set | 2
| iii. | _48V DC Disatribution Panel | lot | 1
1L | LVAC Distribution
1L1 | _AC 415V or 240V distribution panels (MCC type) |  | lot | 1
1L2 | _Tariff metering at LV side(Main & Check) |  | No | 4
1M | Civil Works, Building and Foundation
1M1 | Complete civil items required for outdoor works including boundary wall and slope protection |  | Refer to Schedule B4
1M2 | Complete civil works for GIS Hall, Operation & Panel Room
| i) | _Foundation works | Refer to Schedule B4
| ii) | _Super structures | Refer to Schedule B4
| iii) | _All finish works | Refer to Schedule B4
| iv) | _10 ton EOT Crane | No. | 1
| v) | 6 person lift | No | 1
1M3 | Testing of Foundation |  | Refer to Schedule B4
1M4 | Fire Fighting system for GIS Hall & Control Room
| i) | Fire Fighting system For GIS Room | Lot | 1
| ii) | Fire Fighting system For Operation & Panel Room | Lot | 1
1M5 | Complete transformer Protector system for transformers including Nitrogen Injection system : reservoir, pipe network and pump etc. |  | Refer to Schedule B4
1N | Lighting, small power, air conditioning and Ventilation
1N1 | Indoor Lighting (LED type), small power, air conditioning and Ventilation and emergency DC lighting for control building and local control houses |  | lot | 1
1N2 | Lighting (LED type) for ouside building for security, roadway, switchyard |  | lot | 1
1N3 | Complete solar system (1kW solar panel) including 12V VRLA maintenace free battery and other accessories for Substation emergency DC Lighting |  | Set | 1
1O | Fibre Optic Multiplexer Equipment and PLC Equipment for Communication and Protection
1O1 | Indoor Fibre Optic Multipexer Equipment |  | lot | 1
1O2 | PABX Card & tele-phone set |  | lot | 1
1O3 | under ground optical fiber cable, armoured, 48/24 core including Outdoor termination box,indoor MDF & pigtail cables |  | lot | 1
1O4 | PDH & SDH and 48/24 Core ODF with necessary connection work and testing shall be installed. |  | lot | 1
Total Price( for New Kochua 230/132/33kV SS) carried to Summary of Price Schedule
Total Price in words ( for New Kochua 230/132/33kV SS)...........................................................................................................................................................................
New 132/33 kV Substation at Laksham
Item No. | Description of Equipment Requirement |  | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
[5 empty] | Unit Price | Total Price | Unit Price | Total Price
[5 empty] | CIP | CIP | EXW | EXW
|  |  |  | (1) | (2) | (3) = (1) x (2) | (4) | (5)=(1)x(4)
2A.A | 230 kV switchgear, equipment connection and steel structures
Deleted
2A.B | 145 kV Indoor Type Gas Insulated Switchgear (GIS), equipment connection and steel structures
2A.B1 | 145kV GIS Line Feeder Bays
| a) | For Laksham SS | set | 2
Each Line bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1600A, 40kA/3s, three phase, single pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1600A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1600A, 40kA/3s three phase line disconnector integral with high speed earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer | sets | 3
| vii. | 145kV single phase voltage transformer 2 core, Class 0.2 for Metering and Class 3P for Protection, | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Cubicle | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2A.B2 | 145kV GIS Transformer Feeder Bays: |  | Set | 2
| a) | For Laksham SS | set | 2
Each transformer bay shall comprise of the following equipment:
| i. | 145kV,2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1600A, 40kA/3s, three phase, Gang pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1600A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1600A, 40kA/3s three phase line side disconnector integral with earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer | sets | 3
| vii. | 145kV single phase voltage transformer 2 core, Class 0.2 for Metering and Class 3P for Protection, | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Cubicle | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2A.B3 | 145kV Bus Coupler Bays :
| a) | For Laksham SS | set | 1
Each Bus Coupler Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase double busbar | lot | 1
| ii. | 145kV, 2500A, 40kA/3s, three phase, Gang pole operation circuit breaker complete with spring-stored energy operating mechanism | No. | 1
| iii. | 145kV, 2500A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Sets | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism, on either side of circuit breaker. | sets | 2
| v. | 145kV, 2500A,40kA/3s, single phase, 2-core, current transformer | No. | 3
| vi. | 145kV, 2500A, 40kA/3s, single phase, 3-core, current transformers | No. | 3
| vii. | Local Control Cubicle | set | 1
| viii. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2A.B4 | 145kV GIS Double Busbar with VT/ES :
| a) | For Laksham SS | Set | 1
Each GIS Double Busbar with VT/ES Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase double busbars | Lot | 1
| ii. | 145kV, single phase, 2 cores voltage transformer | No. | 6
| iii. | 145kV, 40kA/3s, three phase, three position earth switches complete with motor operating Mechanism | Sets | 2
| iv. | Local Control Cubicle | Set | 1
132kV Air I nsulated Switchgear
2A.B5 | 120kV rated voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase surge arrester
| a) | For Laksham SS | No. | 12
2A.B6 | Rigid tubular conductor and/or stranded conductors including accessories for each connection as required for completing 145kV GIS Switchyard for all five (05) substations
| i. | Tubular Conductor | Lot | 1
| ii | Flexible Conductor | Lot | 1
2A.B7 | insulator and fittings including all necessary clamps and connectors as required for completing 145kV GIS Switchyard for all five (05) substations
| i | _Insulator | Lot | 1
| ii | Fittings & Clamps_Connector | Lot | 1
| ii | Nut-bolt | Lot | 1
| iv. | _Cable trench including fitting, fixing accessories | Lot | 1
2A.B8 | Steel gantry, having double tier for each double circuit of 145kV Transmission Line including all necessary accessories required for completing 145kV GIS Switchyard
| a) | Steel Structure
| i. | _Gantry Column | No. | 3
| ii. | Beam | No. | 2
| iii. | Nut & Bolts | Lot | 1
| b) | Equipment Structure
| i. | LA | No. | 12
2A.C 33 kV Switchgear, equipment connection and steel structures
One (1) set of complete equipment for switchgear 33 kV shall be designed, supplied, delivered, installed, tested and commissioned, under this contract, comprise the following:
2A.C1 | Circuit Breaker 36 kV, 2500 A, 31.5kA/1s, 50 Hz, 170/70 kV BIL, three pole, vacuum type, for outdoor installation with one spring-stored energy operating mechanism |  | Set | 2
2A.C2 | Disconnector 36 kV, 2500 A, 31.5 kA/1s, 50 Hz, 170/70 kV BIL, three pole, single vertical break, post type, motor operated
| i) | DS without ES | set | 2
| ii) | DS with ES | set | 2
2A.C3 | Current transformer 36 kV, 31.5 kA/1s, 50Hz, 170/70 kV BIL, single phase, 2500/1 , 3-core, post type |  | nos. | 6
2A.C4 | Voltage transformer 36kV, 50Hz, 170/70 kV BIL, single phase, 33/V3 / 0.110/V3 / 0.110/V3 kV, 3 secondary windings, inductive type |  | No. | 6
2A.C5 | Surge arrester 36 kV, 30 kV continuous operating voltage, 10 kA nominal discharge current, 50 Hz, single phase, gapless, metal oxide type for all five (05) substations |  | No. | 6
2A.C6 | DS with load break fuse (10A) etc. for Connection between 36kV busbar & 02 sets of 33/0.415kV Earthing/Auxiliary transformer. |  | Set | 2
2A.C7 | Gantry steel structures for Bus & Equipment, Conductor for 36kV,3000A Bus bar, Insulator and fittings including all necessary clamps and connectors required to complete 33kV switchyard
| i. | Flexible conductor for Bus & Equipment connection | Lot | 1
| ii. | Insulators and fittings incl. all necessary clamps and connectors,Nut-Bolt required for completing 33 kV switchyard | Lot | 1
| iii. | Gantry steel structures for Bus
| a) | Beam | No | 4
| b) | Column | No | 6
| iv. | Gantry steel structures for Transformer
| a) | Beam | No | 2
| b) | Column | No | 3
| v. | steel structures for equipment supports required for completing 33 kV switchgear
| a) | CB,DS; CT,PT & LA ( 3 No.s= 1set) | set | 11
| vi. | XLPE Cable | Deleted
| vii. | Cable Sealing End | Deleted
| viii. | Cable trench | Lot | 1
2A.D |  | Transformers
2A.D1 |  | Deleted
2A.D2 | Three phase outdoor type two-winding power transformer, 132/34.5kV, 80/120MVA (ONAN/ONAF) |  | Set | 2
2A.D3 | On-line Dissolved Gas monitoring system for 132/34.5kV transformers |  | Deleted
2A.D4 | Earthing / Auxiliary Power Transformer 33/0.415 kV, three phase 250 kVA, Dyn11, ONAN , associated outdoor neutral CTs and steel support structures including all necessary connections. |  | Set | 2
2A.D5 |  | Complete Fire Fighting system for GIS Hall & Control Room
| i) | 230kV GIS Hall | Deleted
| ii) | 132kV GIS Hall | Lot | 1
| iii) | Panel & Control Room | Lot | 1
2A.D6 | Transformer Fire-Fighting system (water Spray type) for three phase outdoor type power transformer |  | Deleted
2A.E | Control, Protection, SAS and Metering
245kV Circuits
Deleted
145kV Circuits
2A.E1 |  | Control, Protection,monitoring & SAS function for overhead line circuits | set | 2
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main & Backup) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2E2 |  | Control, Protection,monitoring & SAS function for Power transformer circuits | set | 2
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main-1, Main-2) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2A.E3 |  | Control, Protection,monitoring & SAS function for Bus Coupler circuits | set | 1
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay | set | 1
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Protecttion Panel including wiring, lighting,heater & other accessories | set | 1
2A.E3 |  | Busbar Protection | set | 1
| a) | Control panel with Mimic & all accessories including monitoring | NA
| b) | Protection main relay
| i. | Bay unit with HMI | set | 5
| ii. | Central unit HMI | set | 1
| c) | Selector Switch for Enabling/Disabling BBP,BFP, all function | set | 1
| d) | Protecttion Panel including wiring, lighting,heater, humidity sensor & other accessories | set | 1
2A.E4 |  | Tariff metering
| a) | Meters (Main & Check) | No. | 8
| b) | Panel including wiring, lighting,humidity controller, heater & other accessories | lot | 1
36kV Circuit
2A.E5 |  | Control, Monitoring, Protection & SAS for 33kV station power system | Set | 2
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | Set | 1
| b) | Protection main relay (67,67N,50,50N,51,51N etc) | Set | 1
| c) | Auxiliary relays (TCS, Lockout etc) | Set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | Set | 1
2A.E6 |  | Tariff metering
| a) | Meters (Main & Check) | No. | 4
| b) | Panel including wiring, lighting,heater & other accessories | set | 1
2A.E7 |  | Substation Automation system
| i. | BCU
| a) | for 245kV Circuits | No. | NA
| b) | for 145kV Circuits | No. | 2
| c) | 33kV Circuits | No. | 2
| ii. | Industrial Server PC ( Intel XEON Silver- 4116 processor, ECC memory) cum Operator workstation with SAS & Enginering Software | Set | 2
| iii. | Ethernet Switch for SAS | Lot | 1
| iv. | GPS system | Set | 1
| v. | Common alarm unit with hooter/buzzer for annunciation | Set | 2
| vi. | LCD Monitor, 55" or Large | Set | 1
| vii. | Printer, A4 Laser (One black & White, Other Color) | Set | 2
| viii. | Engineering PC: core i7-9800X series processor, 1TB HDD, 16GB RAM, 22'' display for SAS & SCADA | No. | 1
| ix. | Cable (Fiber Optic, Ethernet, Copper etc.)
| x. | Panel including wiring, lighting,heater & other accessories | Lot | 1
| xi. | Other Accessories (if any) | Lot | 1
2A.F | SCADA system for Telecontrol and Telemetering
| a) | Equipment at Substation
| i. | Gateway (server, engineering software) | Set | 2
| ii. | Ethernet Switch | Set | 2
| iii. | Hardware Firewall | Set | 1
| iv. | Additional 33kV Feeder BCU | set | 5
| v. | Panel including wiring, lighting,heater & other accessories | lot | 1
| vi. | Cables | lot | 1
| vii. | Other Accessories (if any) | lot | 1
| b) | Integration work with Master & Backup NLDC including Engineering & Commissioning | refere to Schedule B4
2A.G | Digital Fault & Disturbance Recorder
Deleted
2A.H |  | GIL & Power Cable
Deleted
2A.I |  | Multicore Cables
Multicore Cables for control, protection, metering & power circuits
| i. | _LV Control Cable | lot | 1
| ii. | _LV Power Cable | lot | 1
2A.J |  | Earthing and Lightning Protection system and Portable Eathing Equipment
2A.J1 |  | Earthing and Lightning Protection system
| i. | _Earthing system for complete substation | lot | 1
| ii. | _Lighting Protection System for complete substation | lot | 1
2A.I2 |  | Portable(maintenance) earthing equipment device | set | 1
2A.K |  | Batteries, chargers & DC distribution
2A.K1 |  | 110V Ni-cad Batteries with chargers & distribution board (including 2 sets 3kVA Inverter) | lot | 1
| i. | _110V Battery Banks, 500Ah | set | 2
| ii. | _Charger 170A | set | 2
| iii. | _3kVA Inverter | set | 1
| iv. | _110V DC Distribution panel, MCC type | lot | 1
2A.K2 |  | 48V Ni-cad Batteries with chargers & distribution board
| i. | _48V battery Banks,150Ah | set | 2
| ii. | _Charger, 70A | set | 2
| iii. | _48V DC Disatribution Panel | lot | 1
2A.L | LVAC Distribution
2A.L1 | _AC 415V or 240V distribution panels (MCC type) |  | lot | 1
2A.L2 | _Tariff metering at LV side(Main & Check) |  | No. | 4
2A.M | Civil Works, Building and Foundation
2A.M1 | Complete civil items required for outdoor works including boundary wall and slope protection |  | Refer to Schedule B4
2A.M2 | Complete civil works for GIS Hall, Operation & Panel Room
| i) | _Foundation works | Refer to Schedule B4
| ii) | _Super structures | Refer to Schedule B4
| iii) | _All finish works | Refer to Schedule B4
| iv) | _10 ton EOT Crane | No. | 1
| v) | 6 person lift | No | 1
2A.M3 | Testing of Foundation |  | Refer to Schedule B4
2A.M4 | Fire Fighting system for GIS Hall & Control Room
| i) | Fire Fighting system For GIS Room | Lot | 1
| ii) | Fire Fighting system For Operation & Panel Room | Lot | 1
2A.M5 | Complete Water spray system for transformers fire-fighting including reservoir, pipe network and pump etc. |  | Deleted
2A.N | Lighting, small power, air conditioning and Ventilation
2A.N1 | Indoor Lighting (LED type), small power, air conditioning and Ventilation and emergency DC lighting for control building and local control houses |  | lot | 1
2A.N2 | Lighting (LED type) for ouside building area for security, roadway, switchyard and emergency DC lighting |  | lot | 1
2A.N3 | Complete solar system (ikW solar panel) including 12V VRLA maintenace free battery and other accessories for Substation emergency DC Lighting |  | Set | 1
2A.O | Fibre Optic Multiplexer Equipment for Communication and Protection
2A.O1 | Indoor Fibre Optic Multipexer Equipment |  | lot | 1
2A.O2 | PABX Card & telephone set |  | lot | 1
2A.O3 | Under ground optical fiber cable, armoured, 48/24 core including Outdoor termination box,indoor MDF & pigtail cables |  | lot | 1
2A.O4 | PDH / SDH and 48/24 Core ODF with necessary connection work and testing shall be installed. |  | lot | 1
Total Price ( for New Laksham 132/33kV SS) carried to Summary of Price Schedule
Total Price in words ( for New Laksham 132/33kV SS) ............................................................................................................................................................................
New132/33 kV Substation at Muradnagar
Item No. | Description of Equipment Requirement |  | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
[5 empty] | Unit Price | Total Price | Unit Price | Total Price
[5 empty] | CIP | CIP | EXW | EXW
|  |  |  | (1) | (2) | (3) = (1) x (2) | (4) | (5)=(1)x(4)
2B.A | 230 kV switchgear, equipment connection and steel structures
Deleted
2B.B | 145 kV Indoor Type Gas Insulated Switchgear (GIS), equipment connection and steel structures
2B.B1 | 145kV GIS Line Feeder Bays
| b) | For Muradnagr SS | set | 6
Each Line bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1600A, 40kA/3s, three phase, single pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1600A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1600A, 40kA/3s three phase line disconnector integral with high speed earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer | sets | 3
| vii. | 145kV single phase voltage transformer 2 core, Class 0.2 for Metering and Class 3P for Protection, | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Cubicle | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2B.B2 | 145kV GIS Transformer Feeder Bays:
| b) | For Muradnagr SS | set | 2
Each transformer bay shall comprise of the following equipment:
| i. | 145kV,2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1600A, 40kA/3s, three phase, Gang pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1600A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1600A, 40kA/3s three phase line side disconnector integral with earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer | sets | 3
| vii. | 145kV single phase voltage transformer 2 core, Class 0.2 for Metering and Class 3P for Protection, | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Cubicle | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2B.B3 | 145kV Bus Coupler Bays :
| b) | For Muradnagr SS | set | 1
Each Bus Coupler Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase double busbar | lot | 1
| ii. | 145kV, 2500A, 40kA/3s, three phase, Gang pole operation circuit breaker complete with spring-stored energy operating mechanism | No. | 1
| iii. | 145kV, 2500A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Sets | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism, on either side of circuit breaker. | sets | 2
| v. | 145kV, 40kA/3s, single phase, 2-core, current transformer with cores as follows: | No. | 3
| vi. | 145kV, 2500A, 40kA/3s, single phase, 3-core, current transformers with cores as follows: | No. | 3
| vii. | Local Control Cubicle | set | 1
| viii. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2B.B4 | 145kV GIS Double Busbar with VT/ES :
| a) | For Muradnagar SS | Set | 1
Each GIS Double Busbar with VT/ES Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kV/3s, three phase double busbars | Lot | 1
| ii. | 145kV, single phase, 2 cores voltage transformer | No. | 6
| iii. | 145kV, 40kA/3s, three phase, three position earth switches complete with motor operating Mechanism | Sets | 2
| iv. | Local Control Cubicle | Set | 1
132kV Air I nsulated Switchgear
2A.B5 | 120kV rated voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase surge arresters
| b) | For Muradnagr SS | No. | 24
2B.B6 | Rigid tubular bus and/or stranded conductors including accessories for each connection as required for completing 145kV GIS Switchyard for all five (05) substations
| i. | Tubular Conductor | Lot | 1
| ii | Flexible Conductor | Lot | 1
2B.B7 | insulator and fittings including all necessary clamps and connectors as required for completing 145kV GIS Switchyard
| i | _Insulator | Lot | 1
| ii | Fittings & Clamps_Connector | Lot | 1
| ii | Nut-bolt | Lot | 1
| iv. | _Cable trench including fitting, fixing accessories | Lot | 1
2B.B8 | Steel gantry, having double tier for each double circuit of 145kV Transmission Line including all necessary accessories required for completing 145kV GIS Switchyard
| a) | Steel Structure
| i. | _Gantry Column | No. | 9
| ii. | Beam | No. | 8
| iii. | Nut & Bolts | Lot | 1
| b) | Equipment Structure
| i. | LA | No. | 24
2B.C 33 kV Switchgear, equipment connection and steel structures
One (1) set of complete equipment for switchgear 33 kV shall be designed, supplied, delivered, installed, tested and commissioned, under this contract, comprise the following:
2B.C1 | Circuit Breaker 36 kV, 2500 A, 31.5kA/1s, 50 Hz, 170/70 kV BIL, three pole, vacuum type, for outdoor installation with one spring-stored energy operating mechanism |  | Set | 2
2B.C2 | Disconnector 36 kV, 2500 A, 31.5 kA/1s, 50 Hz, 170/70 kV BIL, three pole, single vertical break, post type, motor operated
| i) | DS without ES | set | 2
| ii) | DS with ES | set | 2
2B.C3 | Current transformer 36 kV, 31.5 kA/1s, 50Hz, 170/70 kV BIL, single phase, 2500/1 , 3-core, post type |  | nos. | 6
2B.C4 | Voltage transformer 36kV, 50Hz, 170/70 kV BIL, single phase, 33/V3 / 0.110/V3 / 0.110/V3 kV, 3 secondary windings, inductive type |  | No. | 6
2B.C5 | Surge arrester 36 kV, 30 kV continuous operating voltage, 10 kA nominal discharge current, 50 Hz, single phase, gapless, metal oxide type for all five (05) substations |  | No. | 6
2B.C6 | DS with load break fuse (10A) etc. for Connection between 36kV busbar & 02 sets of 33/0.415kV Earthing/Auxiliary transformer. |  | Set | 2
2B.C7 | Gantry steel structures for Bus & Equipment, Conductor for 36kV,3000A Bus bar, Insulator and fittings including all necessary clamps and connectors required to complete 33kV switchyard
| i. | Flexible conductor for Bus & Equipment connection | Lot | 1
| ii. | Insulators and fittings incl. all necessary clamps and connectors,Nut-Bolt required for completing 33 kV switchyard | Lot | 1
| iii. | Gantry steel structures for Bus
| a) | Beam | No | 4
| b) | Column | No | 6
| iv. | Gantry steel structures for Transformer
| a) | Beam | No | 2
| b) | Column | No | 3
| v. | steel structures for equipment supports required for completing 33 kV switchgear
| a) | CB,DS; CT,PT & LA ( 3 No.s= 1set) | set | 11
| vi. | XLPE Cable | Deleted
| vii. | Cable Sealing End | Deleted
| viii. | Cable trench | Lot | 1
2B.D | Transformers
2B.D1 |  | Deleted
2B.D2 |  | Three phase outdoor type two-winding power transformer, 132/34.5kV, 80/120MVA (ONAN/ONAF) | Set | 2
2B.D3 |  | On-line Dissolved Gas monitoring system for 230/138/33kV auto transformers | Deleted
2B.D4 |  | Earthing / Auxiliary Power Transformer 33/0.415 kV, three phase 250 kVA, Dyn11, ONAN , associated outdoor neutral CTs and steel support structures including all necessary connections. | Set | 2
2B.D5 |  | Complete Fire Fighting system for GIS Hall & Control Room
| i) | 230kV GIS Hall | Deleted
| ii) | 132kV GIS Hall | Lot | 1
| iii) | Panel & Control Room | Lot | 1
2B.D6 |  | Transformer Protector system for three phase outdoor type auto transformer as | Deleted
2B.E | Control, Protection, SAS and Metering
245kV Circuits
Deleted
145kV Circuits
2B.E1 |  | Control, Protection,monitoring & SAS function for overhead line circuits | set | 6
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main & Backup) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2B.E2 |  | Control, Protection,monitoring & SAS function for Auto transformer circuits | set | 2
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main & Backup) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2B.E3 |  | Control, Protection,monitoring & SAS function for Bus Coupler circuits | set | 1
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main-1, Main-2) | set | 1
| c) | Auxiliary relay (TCS, Lockout etc.)
| d) | Protecttion Panel including wiring, lighting,heater, humidity sensor & other accessories | set | 1
2B.E3 |  | Busbar Protection | set | 1
| a) | Control panel with all accessories including monitoring | set | 1
| b) | Protection main relay
| i. | Bay unit with HMI | set | 5
| ii. | Central unit with HMI | set | 1
| c) | Selector Switch for Enabling/Disabling BBP,BFP, all function | set | 1
| d) | Protecttion Panel including wiring, lighting,heater & other accessories | set | 1
2B.E4 |  | Tariff metering
| a) | Meters (Main & Check) | No. | 16
| b) | Panel including wiring, lighting,heater & other accessories | set | 1
36kV Circuit
2B.E5 |  | Control, Monitoring, Protection & SAS for 33kV station power system | set | 2
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | set | 1
| b) | Protection main relay (67,67N,50,50N,51,51N etc) | Set | 1
| c) | Auxiliary relays (TCS, Lockout etc) | Set | 1
| d) | Protecttion Panel including wiring, lighting,heater, humidity sensor & other accessories | set | 1
2B.E6 |  | Tariff metering
| a) | Meters (Main & Check) | No. | 4
| b) | Panel including wiring, lighting,heater, humidity sensor & other accessories | lot | 1
2B.E7 |  | Substation Automation system
| i. | BCU
| a) | for 245kV Circuits | No. | NA
| b) | for 145kV Circuits | No. | 9
| c) | 33kV Circuits | No. | 2
| ii. | Industrial Server PC ( Intel XEON Silver- 4116 processor, ECC memory) cum Operator workstation with SAS & Enginering Software | Set | 2
| iii. | Ethernet Switch for SAS | Lot | 1
| iv. | GPS system | Set | 1
| v. | Common alarm unit with hooter/buzzer for annunciation | Set | 2
| vi. | LCD Monitor, 55" or Large | Set | 1
| vii. | Printer, A4 Laser (One black & White, Other Color) | Set | 2
| viii. | Engineering PC: core i7-9800X series processor, 1TB HDD, 8GB RAM, 22'' display for SAS & SCADA | No. | 1
| ix. | Cable (Fiber Optic, Ethernet, Copper etc.)
| x. | Panel including wiring, lighting,heater & other accessories | Lot | 1
| xi. | Other Accessories (if any) | Lot | 1
2B.F | SCADA system for Telecontrol and Telemetering
| a) | Equipment at Substation
| i. | Gateway (server, engineering software) | Set | 2
| ii. | Ethernet Switch | Set | 2
| iii. | Hardware Firewall | Set | 1
| iv. | Additional 33kV Feeder BCU | set | 5
| v. | Panel including wiring, lighting,heater, humidity sensor & other accessories | lot | 1
| vi. | Cables | lot | 1
| vii. | Other Accessories (if any) | lot | 1
| b) | Integration work with Master & Backup NLDC including Engineering & Commissioning | refere to Schedule B4
2B.G | Digital Fault & Disturbance Recorder
Deleted
2B.H |  | GIL & Power Cable
Deleted
2B.I |  | Multicore Cables
Multicore Cables for control, protection, metering & power circuits
| i. | _LV Control Cable | lot | 1
| ii. | _LV Power Cable | lot | 1
2B.J |  | Earthing and Lightning Protection system and Portable Eathing Equipment
2B.J1 |  | Earthing and Lightning Protection system
| i. | _Earthing system for complete substation | lot | 1
| ii. | _Lighting Protection System for complete substation | lot | 1
2B.J2 |  | Portable(maintenance) earthing equipment device | set | 1
2B.K |  | Batteries, chargers & DC distribution
2B.K1 |  | 110V Ni-cad Batteries with chargers & distribution board (including 2 sets 4kVA UPS, 30 mins) | lot | 1
| i. | _110V Battery Banks, 500Ah | set | 2
| ii. | _Charger 170A | set | 2
| iii. | _5kVA Inverter | set | 1
| iv. | _110V DC Distribution panel, MCC type | lot | 1
2B.K2 |  | 48V Ni-cad Batteries with chargers & distribution board
| i. | _48V battery Banks,150Ah | set | 2
| ii. | _Charger, 70A | set | 2
| iii. | _48V DC Disatribution Panel | lot | 1
2B.L | LVAC Distribution
2B.L1 | _AC 415V or 240V distribution panels (MCC type) |  | lot | 1
2B.L2 | _Tariff metering at LV side(Main & Check) |  | No. | 4
2B.M | Civil Works, Building and Foundation |  | Refer to Schedule B4
2B.M1 | Complete civil items required for outdoor works including boundary wall and slope protection |  | Refer to Schedule B4
2B.M2 | Complete civil works for GIS Hall, Operation & Panel Room
| i) | _Foundation works | Refer to Schedule B4
| ii) | _Super structures | Refer to Schedule B4
| iii) | _All finish works | Refer to Schedule B4
| iv) | _10 ton EOT Crane | No. | 1
| v) | 6 person lift | No | 1
2B.M3 | Testing of Foundation |  | Refer to Schedule B4
2B.M4 | Fire Fighting system for GIS Hall & Control Room
| i) | Fire Fighting system For GIS Room | Lot | 1
| ii) | Fire Fighting system For Operation & Panel Room | Lot | 1
2B.M5 | Complete Water spray system for transformers fire-fighting including reservoir, pipe network and pump etc. |  | Deleted
2B.N | Lighting, small power, air conditioning and Ventilation
2B.N1 | Indoor Lighting (LED type), small power, air conditioning and Ventilation and emergency DC lighting for control building and local control houses |  | lot | 1
2B.N2 | Lighting (LED type) for ouside building area for security, roadway, switchyard and emergency DC lighting |  | lot | 1
2B.N3 | Complete solar system (ikW solar panel) including 12V VRLA maintenace free battery and other accessories for Substation emergency DC Lighting |  | lot | 1
2B.O | Fibre Optic Multiplexer Equipment for Communication and Protection
2B.O1 | Indoor Fibre Optic Multipexer Equipment |  | lot | 1
2B.O2 | PABX card & telephone set |  | lot | 1
2B.O3 | Under ground optical fiber cable, armoured, 48/24 core including Outdoor termination box,indoor MDF & pigtail cables |  | lot | 1
2B.O4 | PDH & SDH and 48/24 Core ODF with necessary connection work and testing shall be installed. |  | lot | 1
Total Price ( for New Muradnagar 132/33kV SS) carried to Summary of Price Schedule
Total Price in words ( for New Muradnagar 132/33kV SS)............................................................................................................................................................................
New 132/33 kV Substation at Chandina
Item No. | Description of Equipment Requirement |  | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
[5 empty] | Unit Price | Total Price | Unit Price | Total Price
[5 empty] | CIP | CIP | EXW | EXW
|  |  |  | (1) | (2) | (3) = (1) x (2) | (4) | (5)=(1)x(4)
2C.A | 230 kV switchgear, equipment connection and steel structures
Deleted
2C.B | 145 kV Indoor Type Gas Insulated Switchgear (GIS), equipment connection and steel structures
2C.B1 | 145kV GIS Line Feeder Bays
| c) | For Chandina SS | set | 2
Each Line bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1600A, 40kA/3s, three phase, single pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1600A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | set | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1600A, 40kA/3s three phase line disconnector integral with high speed earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer | No. | 3
| vii. | 145kV single phase voltage transformer 2 core, Class 0.2 for Metering and Class 3P for Protection, | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Cubicle | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2C.B2 | 145kV GIS Transformer Feeder Bays:
| c) | For Chandina SS | set | 2
Each transformer bay shall comprise of the following equipment:
| i. | 145kV,2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1600A, 40kA/3s, three phase, Gang pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1600A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1600A, 40kA/3s three phase line side disconnector integral with earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer | No. | 3
| vii. | 145kV single phase voltage transformer 2 core, Class 0.2 for Metering and Class 3P for Protection, | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Cubicle | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2C.B3 | 145kV Bus Coupler Bays :
| c) | For Chandina SS | set | 1
Each Bus Coupler Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase double busbar | lot | 1
| ii. | 145kV, 2500A, 40kA/3s, three phase, Gang pole operation circuit breaker complete with spring-stored energy operating mechanism | No. | 1
| iii. | 145kV, 2500A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Sets | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism, on either side of circuit breaker. | sets | 2
| v. | 145kV, 40kA/3s, single phase, 2-core, current transformer with cores as follows: | No. | 3
| vi. | 145kV, 2500A, 40kA/3s, single phase, 3-core, current transformers with cores as follows: | No. | 3
| vii. | Local Control Cubicle | set | 1
| viii. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2C.B4 | 145kV GIS Double Busbar with VT/ES :
| c) | For Chandina SS | Set | 1
Each GIS Double Busbar with VT/ES Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 450kA/3s, three phase double busbars | Lot | 1
| ii. | 145kV single phase, 2 cores voltage transformer | No. | 6
| iii. | 145kV, 40kA/3s, three phase, three position earth switches complete with motor operating Mechanism | Sets | 2
| iv. | Local Control Panel | Set | 1
2C.B5 | 120kV rated voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase surge arresters
| c) | For Chandina SS | No. | 12
2C.B6 | Rigid tubular bus and/or stranded conductors including accessories for each connection as required for completing 145kV GIS Switchyard for all five (05) substations
| i. | Tubular Conductor | Lot | 1
| ii | Flexible Conductor | Lot | 1
2C.B7 | insulator and fittings including all necessary clamps and connectors as required for completing 145kV GIS Switchyard for all five (05) substations
| i | _Insulator | Lot | 1
| ii | Fittings & Clamps_Connector | Lot | 1
| ii | Nut-bolt | Lot | 1
| iv. | _Cable trench including fitting, fixing accessories | Lot | 1
2C.B8 | Steel gantry, having double tier for each double circuit of 145kV Transmission Line including all necessary accessories required for completing 145kV GIS Switchyard
| a) | Steel Structure
| i. | _Gantry Column | No. | 4
| ii. | Beam | No. | 4
| iii. | Nut & Bolts | Lot | 1
| b) | Equipment Structure
| i. | LA | No. | 12
2C.C 33 kV Switchgear, equipment connection and steel structures
One (1) set of complete equipment for switchgear 33 kV shall be designed, supplied, delivered, installed, tested and commissioned, under this contract, comprise the following:
2C.C1 | Circuit Breaker 36 kV, 2500 A, 31.5kA/1s, 50 Hz, 170/70 kV BIL, three pole, vacuum type, for outdoor installation with one spring-stored energy operating mechanism |  | Set | 2
2C.C2 | Disconnector 36 kV, 2500 A, 31.5 kA/1s, 50 Hz, 170/70 kV BIL, three pole, single vertical break, post type, motor operated
| i) | DS without ES | set | 2
| ii) | DS with ES | set | 2
2C.C3 | Current transformer 36 kV, 31.5 kA/1s, 50Hz, 170/70 kV BIL, single phase, 2500/1 , 3-core, post type |  | nos. | 6
2C.C4 | Voltage transformer 36kV, 50Hz, 170/70 kV BIL, single phase, 33/V3 / 0.110/V3 / 0.110/V3 kV, 3 secondary windings, inductive type |  | No. | 6
2C.C5 | Surge arrester 36 kV, 30 kV continuous operating voltage, 10 kA nominal discharge current, 50 Hz, single phase, gapless, metal oxide type for all five (05) substations |  | No. | 6
2C.C6 | DS with load break fuse (10A) etc. for Connection between 36kV busbar & 02 sets of 33/0.415kV Earthing/Auxiliary transformer. |  | Set | 2
2C.C7 | Gantry steel structures for Bus & Equipment, Conductor for 36kV,3000A Bus bar, Insulator and fittings including all necessary clamps and connectors required to complete 33kV switchyard
| i. | Flexible conductor for Bus & Equipment connection | Lot | 1
| ii. | Insulators and fittings incl. all necessary clamps and connectors,Nut-Bolt required for completing 33 kV switchyard | Lot | 1
| iii. | Gantry steel structures for Bus
| a) | Beam | No | 4
| b) | Column | No | 6
| iv. | Gantry steel structures for Transformer
| a) | Beam | No | 2
| b) | Column | No | 3
| v. | steel structures for equipment supports required for completing 33 kV switchgear
| a) | CB,DS; CT,PT & LA ( 3 No.s= 1set) | set | 11
| vi. | XLPE Cable | Deleted
| vii. | Cable Sealing End | Deleted
| viii. | Cable trench | Lot | 1
2C.D | Transformers
2C.D1 |  | Deleted
2C.D2 |  | Three phase outdoor type two-winding power transformer, 132/36kV, 80/120MVA (ONAN/ONAF) | Set | 2
2C.D3 |  | On-line Dissolved Gas monitoring system for 230/138/33kV auto transformers | Deleted
2C.D4 |  | Earthing / Auxiliary Power Transformer 33/0.415 kV, three phase 250 kVA, Dyn11, ONAN , associated outdoor neutral CTs and steel support structures including all necessary connections. | Set | 2
2C.D5 |  | Complete Fire Fighting system for GIS Hall & Control Room
| i) | 230kV GIS Hall | Deleted
| ii) | 132kV GIS Hall | Lot | 1
| iii) | Panel & Control Room | Lot | 1
2C.D6 |  | Transformer Fire-Fighting system (water Spray type) for three phase outdoor type power transformer | Deleted
2C.E | Control, Protection, SAS and Metering
245kV Circuits
Deleted
145kV Circuits
2C.E1 |  | Control, Protection,monitoring & SAS function for overhead line circuits | set | 2
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main & Backup) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Protecttion Panel including wiring, lighting,heater & other accessories | set | 1
2C.E2 |  | Control, Protection,monitoring & SAS function for Power transformer circuits | set | 2
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main & Backup) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Protecttion Panel including wiring, lighting,heater & other accessories | set | 1
2C.E3 |  | Control, Protection,monitoring & SAS function for Bus Coupler circuits | set | 1
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay | set | 1
| c) | Auxiliary relays (TCS, Lockout etc) | set | 1
| d) | Protecttion Panel including wiring, lighting,heater & other accessories | set | 1
2C.E3 |  | Busbar Protection | set | 1
| a) | Control panel with Mimic & all accessories including monitoring | NA
| b) | Protection main relay | set | 1
| i. | Bay unit with HMI | set | 5
| ii. | Central unit with HMI | set | 1
| c) | Selector Switch for Enabling/Disabling BBP,BFP, all function | set | 1
| d) | Protecttion Panel including wiring, lighting,heater & other accessories | set | 1
2C.E4 |  | Tariff metering | lot | 1
| a) | Meters | lot | 1
| b) | Panel including wiring, lighting,heater, HUMIDITY SENSOR & other accessories | lot | 1
36kV Circuit
2C.E5 |  | Control, Monitoring, Protection & SAS for 33kV station power system | Set | 2
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | Set | 1
| b) | Protection main relay (67,67N,50,50N,51,51N etc) | Set | 1
| c) | Auxiliary relays (TCS, Lockout etc) | Set | 1
| d) | Protecttion Panel including wiring, lighting,heater, humidity sensor & other accessories | Set | 1
2C.E6 |  | Tariff metering
| a) | Meters (Main & Check) | No. | 4
| b) | Panel including wiring, lighting,heater & other accessories | Set | 1
2C.E7 | Substation Automation system
| i. | BCU
| a) | for 245kV Circuits | No. | NA
| b) | for 145kV Circuits | No. | 3
| c) | 33kV Circuits | No. | 2
| ii. | Industrial Server PC ( Intel XEON Silver- 4116 processor, ECC memory) cum Operator workstation with SAS & Enginering Software | Set | 2
| iii. | Ethernet Switch for SAS | Lot | 1
| iv. | GPS system | Set | 1
| v. | Common alarm unit with hooter/buzzer for annunciation | Set | 2
| vi. | LCD Monitor, 55" or Large | Set | 1
| vii. | Printer, A4 Laser (One black & White, Other Color) | Set | 2
| viii. | Engineering PC: core i7-9800X series processor, 1TB HDD, 16GB RAM, 22'' display for SAS & SCADA | No. | 1
| ix. | Cable (Fiber Optic, Ethernet, Copper etc.)
| x. | Panel including wiring, lighting,heater & other accessories | Lot | 1
| xi. | Other Accessories (if any) | Lot | 1
2C.F | SCADA system for Telecontrol and Telemetering
| a) | Equipment at Substation
| i. | Gateway (server, engineering software) | Set | 2
| ii. | Ethernet Switch | Set | 2
| iii. | Hardware Firewall | Set | 1
| iv. | Additional 33kV Feeder BCU | set | 5
| v. | Panel including wiring, lighting,heater & other accessories | lot | 1
| vi. | Cables | lot | 1
| vii. | Other Accessories (if any) | lot | 1
| b) | Integration work with Master & Backup NLDC including Engineering & Commissioning | refere to Schedule B4
2C.G | Digital Fault & Disturbance Recorder
Deleted
2C.H |  | GIL & Power Cable
Deleted
2C.I |  | Multicore Cables
Multicore Cables for control, protection, metering & power circuits
| i. | _LV Control Cable | lot | 1
| ii. | _LV Power Cable | lot | 1
2C.J |  | Earthing and Lightning Protection system and Portable Eathing Equipment
2C.J1 |  | Earthing and Lightning Protection system
| i. | _Earthing system for complete substation | lot | 1
| ii. | _Lighting Protection System for complete substation | lot | 1
2C.J2 |  | Portable(maintenance) earthing equipment device | set | 1
2C.K |  | Batteries, chargers & DC distribution
2C.K1 |  | 110V Ni-cad Batteries with chargers & distribution board (including 2 sets 4kVA Inverter) | lot | 1
| i. | _110V Battery Banks, 500Ah | set | 2
| ii. | _Charger 170A | set | 2
| iii. | _4kVA Inverter | set | 1
| iv. | _110V DC Distribution panel, MCC type | lot | 1
2C.K2 |  | 48V Ni-cad Batteries with chargers & distribution board
| i. | _48V battery Banks,150Ah | set | 2
| ii. | _Charger, 70A | set | 2
| iii. | _48V DC Disatribution Panel | lot | 1
2C.L | LVAC Distribution
2C.L1 | _AC 415V or 240V distribution panels (MCC type) |  | lot | 1
2C.L2 | _Tariff metering at LV side(Main & Check) |  | No. | 4
2C.M | Civil Works, Building and Foundation |  | Refer to Schedule B4
2C.M1 | Complete civil items required for outdoor works including boundary wall and slope protection |  | Refer to Schedule B4
2C.M2 | Complete civil works for GIS Hall, Operation & Panel Room
| i) | _Foundation works | Refer to Schedule B4
| ii) | _Super structures | Refer to Schedule B4
| iii) | _All finish works | Refer to Schedule B4
| iv) | _10 ton EOT Crane | No. | 1
| v) | 6 person lift | No | 1
2C.M3 | Testing of Foundation |  | Refer to Schedule B4
2C.M4 | Fire Fighting system for GIS Hall & Control Room
| i) | Fire Fighting system For GIS Room | Lot | 1
| ii) | Fire Fighting system For Operation & Panel Room | Lot | 1
2C.M5 | Complete Water spray system for transformers fire-fighting including reservoir, pipe network and pump etc. |  | Deleted
2C.N | Lighting, small power, air conditioning and Ventilation
2C.N1 | Indoor Lighting (LED type), small power, air conditioning and Ventilation and emergency DC lighting for control building and local control houses |  | lot | 1
2C.N2 | Lighting (LED type) for ouside building area for security, roadway, switchyard and emergency DC lighting |  | lot | 1
2C.N3 | Complete solar system (ikW solar panel) including 12V VRLA maintenace free battery and other accessories for Substation emergency DC Lighting |  | Set | 1
2C.O | Fibre Optic Multiplexer Equipment for Communication and Protection
2C.O1 | Indoor Fibre Optic Multipexer Equipment |  | lot | 1
2C.O2 | PABX Card & telephone set |  | lot | 1
2C.O3 | Under ground optical fiber cable, armoured, 48/24 core including Outdoor termination box,indoor MDF & pigtail cables |  | lot | 1
2C.O4 | PDH & SDH and 48/24 Core ODF with necessary connection work and testing shall be installed. |  | lot | 1
Total Price ( for New Chandina 132/33kV SS) carried to Summary of Price Schedule
Total Price in words ( for New Chandina 132/33kV SS)............................................................................................................................................................................
New 132/33 kV Substation at Laxmipur
Item No. | Description of Equipment Requirement |  | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
[5 empty] | Unit Price | Total Price | Unit Price | Total Price
[5 empty] | CIP | CIP | EXW | EXW
|  |  |  | (1) | (2) | (3) = (1) x (2) | (4) | (5)=(1)x(4)
2D.A | 230 kV switchgear, equipment connection and steel structures
Deleted
2D.B | 145 kV Indoor Type Gas Insulated Switchgear (GIS), equipment connection and steel structures
2D.B1 | 145kV GIS Line Feeder Bays
| d) | For Laxmipur SS | set | 2
Each Line bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1600A, 40kA/3s, three phase, single pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1600A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1600A, 40kA/3s three phase line disconnector integral with high speed earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer with cores as follows | No. | 3
| vii. | 145kV single phase voltage transformer 2 core, Class 0.2,5VA for Metering and Class 3P,10VA for Protection | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Panel | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2D.B2 | 145kV GIS Transformer Feeder Bays:
| d) | For Laxmipur SS | Set | 2
Each Line bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1600A, 40kA/3s, three phase, Gang pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1600A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1600A, 40kA/3s three phase line disconnector integral with earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer with cores as follows | No. | 3
| vii. | 145kV single phase voltage transformer 3 core, Class 0.2 for Metering and Class 3P for Protection, | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Panel | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2D.B3 | 145kV Bus Coupler Bays :
| d) | For Laxmipur SS | set | 1
Each Bus Coupler Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase double busbar | lot | 1
| ii. | 145kV, 2500A, 40kA/3s, three phase, Gang pole operation circuit breaker complete with spring-stored energy operating mechanism | No. | 1
| iii. | 145kV, 2500A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Sets | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism, on either side of circuit breaker. | sets | 2
| v. | 145kV, 40kA/3s, single phase, 2-core, current transformer with cores as follows: | No. | 3
| vi. | 145kV, 2500A, 40kA/3s, single phase, 2-core, current transformers with cores as follows: | No. | 3
| vii. | Local Control Panel | set | 1
| viii. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2D.B4 | 145kV GIS Double Busbar with VT/ES :
| d) | For Laxmipur SS | Set | 1
Each GIS Double Busbar with VT/ES Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase double busbars | Lot | 1
| ii. | 145kV single phase, 2 core, voltage transformer | No. | 6
| iii. | 145kV, 40kA/3s, three phase, three position earth switches complete with motor operating Mechanism | Sets | 2
| iv. | Local Control Panel | Set | 1
2D.B5 | 120kV rated voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase surge arresters
| d) | For Laxmipur SS | No. | 12
2D.B6 | Rigid tubular bus and/or stranded conductors including accessories for each connection as required for completing 145kV GIS Switchyard for all five (05) substations
| i. | Tubular Conductor | Lot | 1
| ii | Flexible Conductor | Lot | 1
2D.B7 | Insulator and fittings including all necessary clamps and connectors as required for completing 145kV GIS Switchyard
| i | _Insulator | Lot | 1
| ii | Fittings & Clamps_Connector | Lot | 1
| ii | Nut-bolt | Lot | 1
| iv. | _Cable trench including fitting, fixing accessories | Lot | 1
2D.B8 | Steel gantry, having double tier for each double circuit of 145kV Transmission Line including all necessary accessories required for completing 145kV GIS Switchyard
| a) | Steel Structure
| i. | _Gantry Column | No. | 6
| ii. | Beam | No. | 4
| iii. | Nut & Bolts | Lot | 1
| b) | Equipment Structure
| i. | LA | No. | 12
2D.C 33 kV Switchgear, equipment connection and steel structures
One (1) set of complete equipment for switchgear 33 kV shall be designed, supplied, delivered, installed, tested and commissioned, under this contract, comprise the following:
2D.C1 | Circuit Breaker 36 kV, 2500 A, 31.5kA/1s, 50 Hz, 170/70 kV BIL, three pole, vacuum type, for outdoor installation with one spring-stored energy operating mechanism |  | Set | 2
2D.C2 | Disconnector 36 kV, 2500 A, 31.5 kA/1s, 50 Hz, 170/70 kV BIL, three pole, single vertical break, post type, motor operated
| i) | DS without ES | set | 2
| ii) | DS with ES | set | 2
2D.C3 | Current transformer 36 kV, 31.5 kA/1s, 50Hz, 170/70 kV BIL, single phase, 630-1250/1/1 , 2-core, post type |  | nos. | 6
2D.C4 | Voltage transformer 36kV, 50Hz, 170/70 kV BIL, single phase, 33/V3 / 110/V3 / 110/V3 kV/V/V, 2 secondary windings, inductive type |  | No. | 6
2D.C5 | Surge arrester 36 kV, 30 kV continuous operating voltage, 10 kA nominal discharge current, 50 Hz, single phase, gapless, metal oxide type for all five (05) substations |  | No. | 6
2D.C6 | DS with load break fuse (6A) etc. for Connection between 36kV busbar & 02 sets of 33/0.415kV Earthing/Auxiliary transformer. |  | Set | 2
2D.C7 | Gantry steel structures for Bus & Equipment, Conductor for 36kV,3000A Bus bar, Insulator and fittings including all necessary clamps and connectors required to complete 33kV switchyard
| i. | Flexible conductor for Bus & Equipment connection | Lot | 1
| ii. | Insulators and fittings incl. all necessary clamps and connectors,Nut-Bolt required for completing 33 kV switchyard | Lot | 1
| iii. | Gantry steel structures for Bus
| a) | Beam | No | 4
| b) | Column | No | 6
| iv. | Gantry steel structures for Transformer
| a) | Beam | No | 2
| b) | Column | No | 3
| v. | steel structures for equipment supports required for completing 33 kV switchgear
| a) | CB,DS; CT,PT & LA ( 3 No.s= 1set) | set | 11
| vi. | XLPE Cable | Deleted
| vii. | Cable Sealing End | Deleted
| viii. | Cable trench | Lot | 1
2D.D |  | Transformers
2D.D1 |  | Deleted
2D.D2 |  | Three phase outdoor type two-winding power transformer, 132/36kV, 80/120MVA (ONAN/ONAF) | Set | 2
2D.D3 |  | On-line Dissolved Gas monitoring system for 230/138/33kV auto transformers | Deleted
2D.D4 |  | Earthing / Auxiliary Power Transformer 33/0.415 kV, three phase 250 kVA, Dyn11, ONAN , associated outdoor neutral CTs and steel support structures including all necessary connections. | Set | 2
2D.D5 |  | Complete Fire Fighting system for GIS Hall & Control Room
| i) | 230kV GIS Hall | Deleted
| ii) | 132kV GIS Hall | Lot | 1
| iii) | Panel & Control Room | Lot | 1
2D.D6 |  | Transformer Fire-Fighting system (water Spray type) for three phase outdoor type power transformer | Deleted
2D.E | Control, Protection, SAS and Metering
245kV Circuits
Deleted
145kV Circuits
2D.E1 |  | Control, Protection,monitoring & SAS function for overhead line circuits | set | 2
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main & Backup) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2D.2E2 |  | Control, Protection,monitoring & SAS function for Auto transformer circuits | set | 2
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main & Backup) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2D.E3 |  | Control, Protection,monitoring & SAS function for Bus Coupler circuits | set | 1
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main-1, Main-2) | set | 1
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2D.E3 |  | Busbar Protection | set | 1
| a) | Control panel with Mimic & all accessories including monitoring | NA
| b) | Protection main relay
| i. | Bay Unit | set | 5
| ii. | Central Unit | set | 1
| c) | Selector Switch for Enabling/Disabling BBP,BFP, all function | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2D.E4 |  | Tariff metering
| a) | Meters (Main & Check) | No. | 8
| b) | Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
36kV Circuit
2D.E5 |  | Control, Monitoring, Protection & SAS for 33kV station power system | Set | 2
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | set | 1
| b) | Protection main relay (67,67N,50,50N,51,51N etc) | Set | 1
| c) | Auxiliary relays (TCS, Lockout etc) | Set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | Set | 1
2D.E6 |  | Tariff metering
| a) | Meters (Main & Check) | No. | 4
| b) | Panel including wiring, lighting,humidity controller, heater & other accessories | lot | 1
2D.E7 | Substation Automation system
| i. | BCU/BCPU
| a) | for 245kV Circuits | No. | NA
| b) | for 145kV Circuits | No. | 5
| c) | 33kV Circuits | No. | 2
| ii. | Industrial Server PC cum Operator workstation with SAS & Enginering Software | Set | 2
| iii. | Ethernet Switch for SAS | Lot | 1
| iv. | GPS system | Set | 1
| v. | Common alarm unit with hooter/buzzer for annunciation | Set | 2
| vi. | LCD Monitor, 55" or Large | Set | 1
| vii. | Printer, A4 Laser (One black & White, Other Color) | Set | 2
| viii. | Engineering PC: core i7, 1TB HDD, 8GB RAM, 22'' display for SAS & SCADA | No. | 1
| ix. | Cable (Fiber Optic, Ethernet, Copper etc.)
| x. | Panel including wiring, lighting,heater & other accessories | Lot | 1
| xi. | Other Accessories (if any) | Lot | 1
2D.F | SCADA system for Telecontrol and Telemetering
| a) | Equipment at Substation
| i. | Gateway (server, engineering software) | Set | 2
| ii. | Ethernet Switch | Set | 2
| iii. | Hardware Firewall | Set | 1
| iv. | Additional 33kV Feeder BCU | set | 5
| v. | Panel including wiring, lighting,heater & other accessories | lot | 1
| vi. | Cables | lot | 1
| vii. | Other Accessories (if any) | lot | 1
| b) | Integration work with Master & Backup NLDC including Engineering & Commissioning | refere to Schedule B4
2D.G | Digital Fault & Disturbance Recorder
Deleted
2D.H |  | GIL & Power Cable
Deleted
2D.I |  | Multicore Cables
Multicore Cables for control, protection, metering & power circuits
| i. | _LV Control Cable | lot | 1
| ii. | _LV Power Cable | lot | 1
2D.J |  | Earthing and Lightning Protection system and Portable Eathing Equipment
2D.J1 |  | Earthing and Lightning Protection system
| i. | _Earthing system for complete substation | lot | 1
| ii. | _Lighting Protection System for complete substation | lot | 1
2D.J2 |  | Portable(maintenance) earthing equipment device | set | 1
2D.K |  | Batteries, chargers & DC distribution
2D.K1 |  | 110V Ni-cad Batteries with chargers & distribution board (including 2 sets 4kVA UPS, 30 mins) | lot | 1
| i. | _110V Battery Banks, 350Ah | set | 2
| ii. | _Charger 120A | set | 2
| iii. | _5kVA,30 mins Inverter | set | 1
| iv. | _110V DC Distribution panel, MCC type | lot | 1
2D.K2 |  | 48V Ni-cad Batteries with chargers & distribution board
| i. | _48V battery Banks,125Ah | set | 2
| ii. | _Charger, 50A | set | 2
| iii. | _48V DC Disatribution Panel | lot | 1
2D.L | LVAC Distribution
2D.L1 | _AC 415V or 240V distribution panels (MCC type) |  | lot | 1
2D.L2 | _Tariff metering at LV side(Main & Check) |  | No. | 4
2D.M | Civil Works, Building and Foundation |  | Refer to Schedule B4
2D.M1 | Complete civil items required for outdoor works including boundary wall and slope protection |  | Refer to Schedule B4
2D.M2 | Complete civil works for GIS Hall, Operation & Panel Room
| i) | _Foundation works | Refer to Schedule B4
| ii) | _Super structures | Refer to Schedule B4
| iii) | _All finish works | Refer to Schedule B4
| iv) | _10 ton EOT Crane | No. | 1
| v) | 6 person lift | No | 1
2D.M3 | Testing of Foundation |  | Refer to Schedule B4
2D.M4 | Fire Fighting system for GIS Hall & Control Room
| i) | Fire Fighting system For GIS Room | Lot | 1
| ii) | Fire Fighting system For Operation & Panel Room | Lot | 1
2D.M5 | Complete transformer Protector system for transformers including Nitrogen Injection system : reservoir, pipe network and pump etc. |  | Deleted
2D.N | Lighting, small power, air conditioning and Ventilation
2D.N1 | Indoor Lighting (LED type), small power, air conditioning and Ventilation and emergency DC lighting for control building and local control houses |  | lot | 1
2D.N2 | Lighting (LED type) for ouside building area for security, roadway, switchyard and emergency DC lighting |  | lot | 1
2D.N3 | Complete solar system (ikW solar panel) including 12V VRLA maintenace free battery and other accessories for Substation emergency DC Lighting |  | Set | 1
2D.O | Fibre Optic Multiplexer Equipment for Communication and Protection
2D.O1 | Indoor Fibre Optic Multipexer Equipment |  | lot | 1
2D.O2 | PABX Card & telephone set |  | lot | 1
2D.O3 | Under ground optical fiber cable, armoured, 48/24 core including Outdoor termination box,indoor MDF & pigtail cables |  | lot | 1
2D.O4 | PDH & SDH and 48/24 Core ODF with necessary connection work and testing shall be installed. |  | lot | 1
Total Price ( for New Laxmipur 132/33kV SS) carried to Summary of Price Schedule
Total Price in words ( for New Laxmipur 132/33kV SS)............................................................................................................................................................................
New 132/33 kV Substation at Kosba
Item No. | Description of Equipment Requirement |  | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
[5 empty] | Unit Price | Total Price | Unit Price | Total Price
[5 empty] | CIP | CIP | EXW | EXW
|  |  |  | (1) | (2) | (3) = (1) x (2) | (4) | (5)=(1)x(4)
2E.A | 230 kV switchgear, equipment connection and steel structures
Deleted
2E.B | 145 kV Indoor Type Gas Insulated Switchgear (GIS), equipment connection and steel structures
2E.B1 | 145kV GIS Line Feeder Bays
| e) | For Kosba SS | set | 2
Each Line bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1250A, 40kA/3s, three phase, single pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1250A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1250A, 40kA/3s three phase line disconnector integral with high speed earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer with cores as follows | sets | 3
| vii. | 145kV single phase voltage transformer 2 core, Class 0.2 for Metering and Class 3P for Protection, | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Panel | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2E.B2 | 145kV GIS Transformer Feeder Bays:
| e) | For Kosba SS | set | 2
Each transformer bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1600A, 40kA/3s, three phase, Gang pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1600A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1600A, 40kA/3s three phase line disconnector integral with earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer with cores as follows | No. | 3
| vii. | 145kV single phase voltage transformer 2 core, Class 0.2,5VA for Metering and Class 3P,10VA for Protection, 145,000/√3:110/√3:110/√3 V, | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Panel | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2E.B3 | 145kV Bus Coupler Bays :
| e) | For Kosba SS | set | 1
Each Bus Coupler Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase double busbar | lot | 1
| ii. | 145kV, 2500A, 40kA/3s, three phase, Gang pole operation circuit breaker complete with spring-stored energy operating mechanism | No. | 1
| iii. | 145kV, 2500A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Sets | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism, on either side of circuit breaker. | sets | 2
| v. | 145kV, 40kA/3s, single phase, 2-core, current transformer with cores as follows: | No. | 3
| vi. | 145kV, 2500A, 40kA/3s, single phase, 2-core, current transformers with cores as follows: | No. | 3
| vii. | Local Control Panel | set | 1
| viii. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2E.B4 | 145kV GIS Double Busbar with VT/ES :
| e) | For Kosba SS | Set | 1
Each GIS Double Busbar with VT/ES Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase double busbars | Lot | 1
| ii. | 145kV single phase, 2 core, voltage transformer with windings as follows: | No. | 6
| iii. | 145kV, 40kA/3s, three phase, three position earth switches complete with motor operating Mechanism | Sets | 2
| iv. | Local Control Panel | Set | 1
2E.B5 | 120kV rated voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase surge arresters
| e) | For Kosba SS | No. | 12
2E.B6 | Rigid tubular bus and/or stranded conductors including accessories for each connection as required for completing 145kV GIS Switchyard
| i. | Tubular Conductor | Lot | 1
| ii | Flexible Conductor | Lot | 1
2E.B7 | insulator and fittings including all necessary clamps and connectors as required for completing 145kV GIS Switchyard
| i | _Insulator | Lot | 1
| ii | Fittings & Clamps_Connector | Lot | 1
| ii | Nut-bolt | Lot | 1
| iv. | _Cable trench including fitting, fixing accessories | Lot | 1
2E.B8 | Steel gantry, having double tier for each double circuit of 145kV Transmission Line including all necessary accessories required for completing 145kV GIS Switchyard
| a) | Steel Structure
| i. | _Gantry Column | No. | 4
| ii. | Beam | No. | 2
| iii. | Nut & Bolts | Lot | 1
| b) | Equipment Structure
| i. | LA | No. | 12
2E.C 33 kV Switchgear, equipment connection and steel structures
One (1) set of complete equipment for switchgear 33 kV shall be designed, supplied, delivered, installed, tested and commissioned, under this contract, comprise the following:
2E.C1 | Circuit Breaker 36 kV, 2500 A, 31.5kA/1s, 50 Hz, 170/70 kV BIL, three pole, vacuum type, for outdoor installation with one spring-stored energy operating mechanism |  | Set | 2
2E.C2 | Disconnector 36 kV, 2500 A, 31.5 kA/1s, 50 Hz, 170/70 kV BIL, three pole, single vertical break, post type, motor operated
| i) | DS without ES | set | 2
| ii) | DS with ES | set | 2
2E.C3 | Current transformer 36 kV, 31.5 kA/1s, 50Hz, 170/70 kV BIL, single phase, 630-1250/1/1 , 2-core, post type |  | nos. | 6
2E.C4 | Voltage transformer 36kV, 50Hz, 170/70 kV BIL, single phase, 33/V3 / 110/V3 / 110/V3 kV/V/V, 2 secondary windings, inductive type |  | No. | 6
2E.C5 | Surge arrester 36 kV, 30 kV continuous operating voltage, 10 kA nominal discharge current, 50 Hz, single phase, gapless, metal oxide type for all five (05) substations |  | No. | 6
2E.C6 | DS with load break fuse (6A) etc. for Connection between 36kV busbar & 02 sets of 33/0.415kV Earthing/Auxiliary transformer. |  | Set | 2
2E.C7 | Gantry steel structures for Bus & Equipment, Conductor for 36kV,3000A Bus bar, Insulator and fittings including all necessary clamps and connectors required to complete 33kV switchyard
| i. | Flexible conductor for Bus & Equipment connection | Lot | 1
| ii. | Insulators and fittings incl. all necessary clamps and connectors,Nut-Bolt required for completing 33 kV switchyard | Lot | 1
| iii. | Gantry steel structures for Bus
| a) | Beam | No | 4
| b) | Column | No | 6
| iv. | Gantry steel structures for Transformer
| a) | Beam | No | 2
| b) | Column | No | 3
| v. | steel structures for equipment supports required for completing 33 kV switchgear
| a) | CB,DS; CT,PT & LA ( 3 No.s= 1set) | set | 11
| vi. | XLPE Cable | Deleted
| vii. | Cable Sealing End | Deleted
| viii. | Cable trench | Lot | 1
2E.D | Transformers
2E.D1 |  | Deleted
2E.D2 |  | Three phase outdoor type two-winding power transformer, 132/36kV, 80/120MVA (ONAN/ONAF) | Set | 2
2E.D3 |  | On-line Dissolved Gas monitoring system for 230/138/33kV auto transformers | Deleted
2E.D4 |  | Earthing / Auxiliary Power Transformer 33/0.415 kV, three phase 250 kVA, Dyn11, ONAN , associated outdoor neutral CTs and steel support structures including all necessary connections. | Set | 2
2E.D5 |  | Complete Fire Fighting system for GIS Hall & Control Room
| i) | 230kV GIS Hall | Deleted
| ii) | 132kV GIS Hall | Lot | 1
| iii) | Panel & Control Room | Lot | 1
2E.D6 |  | Transformer Fire-Fighting system (water Spray type) for three phase outdoor type power transformer | Deleted
2E.E | Control, Protection, SAS and Metering
245kV Circuits
Deleted
145kV Circuits
2E.E1 |  | Control, Protection,monitoring & SAS function for overhead line circuits | set | 2
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main & Backup) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2E2 |  | Control, Protection,monitoring & SAS function for Auto transformer circuits | set | 2
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main & Backup) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2E.E3 |  | Control, Protection,monitoring & SAS function for Bus Coupler circuits | set | 1
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay | set | 1
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2E.E3 |  | Busbar Protection | set | 1
| a) | Control panel with Mimic & all accessories including monitoring | NA
| b) | Protection main relay
| i. | Bay Unit | set | 5
| ii. | Central Unit | set | 1
| c) | Selector Switch for Enabling/Disabling BBP,BFP, all function | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2E.E4 |  | Tariff metering
| a) | Meters (Main & Check) | No. | 8
| b) | Panel including wiring, lighting,heater & other accessories | lot | 1
36kV Circuit
2E.E5 |  | Control, Monitoring, Protection & SAS for 33kV station power system | Set | 2
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | set | 1
| b) | Protection main relay (67,67N,50,50N,51,51N etc) | Set | 1
| c) | Auxiliary relays (TCS, Lockout etc) | Set | 1
| d) | Protecttion Panel including wiring, lighting,heater & other accessories | set | 1
2E.E6 |  | Tariff metering
| a) | Meters | No. | 4
| b) | Panel including wiring, lighting,heater & other accessories | set | 1
2E.E7 | Substation Automation system
| i. | BCU/BCPU
| a) | for 245kV Circuits | No. | NA
| b) | for 145kV Circuits | No. | 5
| c) | 33kV Circuits | No. | 2
| ii. | Industrial Server PC cum Operator workstation with SAS & Enginering Software | Set | 2
| iii. | Ethernet Switch for SAS | Lot | 1
| iv. | GPS system | Set | 1
| v. | Common alarm unit with hooter/buzzer for annunciation | Set | 2
| vi. | LCD Monitor, 55" or Large | Set | 1
| vii. | Printer, A4 Laser (One black & White, Other Color) | Set | 2
| viii. | Engineering PC: core i7, 1TB HDD, 8GB RAM, 22'' display for SAS & SCADA | No. | 1
| ix. | Cable (Fiber Optic, Ethernet, Copper etc.)
| x. | Panel including wiring, lighting,heater & other accessories | Lot | 1
| xi. | Other Accessories (if any) | Lot | 1
2E.F | SCADA system for Telecontrol and Telemetering
| a) | Equipment at Substation
| i. | Gateway (server, engineering software) | Set | 2
| ii. | Ethernet Switch | Set | 2
| iii. | Hardware Firewall | Set | 1
| iv. | Additional 33kV Feeder BCU | set | 5
| v. | Panel including wiring, lighting,heater & other accessories | lot | 1
| vi. | Cables | lot | 1
| vii. | Other Accessories (if any) | lot | 1
| b) | Integration work with Master & Backup NLDC including Engineering & Commissioning | refere to Schedule B4
2E.G | Digital Fault & Disturbance Recorder
Deleted
2E.H |  | GIL & Power Cable
Deleted
2E.I |  | Multicore Cables
Multicore Cables for control, protection, metering & power circuits
| i. | _LV Control Cable | lot | 1
| ii. | _LV Power Cable | lot | 1
2E.J |  | Earthing and Lightning Protection system and Portable Eathing Equipment
2E.J1 |  | Earthing and Lightning Protection system
| i. | _Earthing system for complete substation | lot | 1
| ii. | _Lighting Protection System for complete substation | lot | 1
2E.J2 |  | Portable(maintenance) earthing equipment device | set | 1
2E.K |  | Batteries, chargers & DC distribution
2E.K1 |  | 110V Ni-cad Batteries with chargers & distribution board (including 2 sets 4kVA UPS, 30 mins) | lot | 1
| i. | _110V Battery Banks, 350Ah | set | 2
| ii. | _Charger 120A | set | 2
| iii. | _5kVA,30 mins Inverter | set | 1
| iv. | _110V DC Distribution panel, MCC type | lot | 1
2E.K2 |  | 48V Ni-cad Batteries with chargers & distribution board
| i. | _48V battery Banks,125Ah | set | 2
| ii. | _Charger, 50A | set | 2
| iii. | _48V DC Disatribution Panel | lot | 1
2E.L | LVAC Distribution
2E.L1 | _AC 415V or 240V distribution panels (MCC type) |  | lot | 1
2E.L2 | _Tariff metering at LV side(Main & Check) |  | No. | 4
2E.M | Civil Works, Building and Foundation
2E.M1 | Complete civil items required for outdoor works including boundary wall and slope protection |  | Refer to Schedule B4
2E.M2 | Complete civil works for GIS Hall, Operation & Panel Room
| i) | _Foundation works | Refer to Schedule B4
| ii) | _Super structures | Refer to Schedule B4
| iii) | _All finish works | Refer to Schedule B4
| iv) | _10 ton EOT Crane | No. | 1
| v) | 6 person lift | No | 1
2E.M3 | Testing of Foundation |  | Refer to Schedule B4
2E.M4 | Fire Fighting system for GIS Hall & Control Room
| i) | Fire Fighting system For GIS Room | Lot | 1
| ii) | Fire Fighting system For Operation & Panel Room | Lot | 1
2E.M5 | Complete Water spray system for transformers fire-fighting including reservoir, pipe network and pump etc. |  | Deleted
2E.N | Lighting, small power, air conditioning and Ventilation
2E.N1 | Indoor Lighting (LED type), small power, air conditioning and Ventilation and emergency DC lighting for control building and local control houses |  | lot | 1
2E.N2 | Lighting (LED type) for ouside building area for security, roadway, switchyard and emergency DC lighting |  | lot | 1
2E.N3 | Complete solar system (ikW solar panel) including 12V VRLA maintenace free battery and other accessories for Substation emergency DC Lighting |  | Set | 1
2E.O | Fibre Optic Multiplexer Equipment for Communication and Protection
2E.O1 | Indoor Fibre Optic Multipexer Equipment |  | lot | 1
2E.O2 | PABX Card & telephone set |  | lot | 1
2E.O3 | Under ground optical fiber cable, armoured, 48/24 core including Outdoor termination box,indoor MDF & pigtail cables |  | lot | 1
2E.O4 | PDH & SDH and 48/24 Core ODF with necessary connection work and testing shall be installed. |  | lot | 1
Total Price (for New Kosba 132/33kV SS) carried to Summary of Price Schedule
Total Price in words(for New Kosba 132/33kV SS)............................................................................................................................................................................
Extension of 230kV bays at 230/132 kV GIS GAZARIA Substation
Item No. | Description of Equipment Requirement |  | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
[5 empty] | Unit Price | Total Price | Unit Price | Total Price
[5 empty] | CIP | CIP | EXW | EXW
|  |  |  | (1) | (2) | (3) = (1) x (2) | (4) | (5)=(1)x(4)
3A | 230 kV switchgear, equipment connection and steel structures
3A1 | 245kV GIS Line Feeder Bays, each comprising: |  | Set | 4
| i. | 245kV, 3150A, 50kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 245kV, 3150A, 50kA/3s, three phase, single pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 245kV, 3150A, 50kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 245kV, 50kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 245kV, 3150A, 50kA/3s three phase line disconnector integral with high speed earth switch complete with motor operating mechanism | sets | 1
| vi | 245kV, 3150A, 50kA/3s single phase, 6-core, current transformer with cores as follows: | No. | 3
| vii. | 245kV single phase, 2 core, Class 0.2,5VA for Metering and Class 3P,10VA for Protection voltage transformer | No. | 3
| viii. | 245kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Panel | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
3A2 | 245kV GIS Auto Transformer Feeder Bays, each comprising: |  | Deleted
3A3 | 245kV Bus Coupler Bays , each comprising: |  | Deleted
3A4 | 245kV GIS Double Busbar with VT/ES, each comprising: |  | Deleted
3A5 | 216kV rated voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase surge arresters |  | No. | 12
3A6 | Rigid tubular bus and/or stranded conductors including accessories for each connection as required for completing 230kV GIS Switchyard
| i. | Tubular Conductor | Lot | 1
| ii | Flexible Conductor | Lot | 1
3A7 | Insulator and fittings including all necessary clamps and connectors as required for completing 230kV GIS Switchyard
| i | _Insulator | Lot | 1
| ii | Fittings & Clamps_Connector | Lot | 1
| ii | Nut-bolt | Lot | 1
| iv. | _Cable trench including fitting, fixing accessories | Lot | 1
3A8 | Steel gantry, having double tier for each double circuit of 230kV Transmission Line & Equipment support Structure including all necessary accessories required for completing 230kV GIS Switchyard
| a) | Steel Structure
| i. | _Gantry Column | No. | 5
| ii. | Beam | No. | 4
| iii. | Nut & Bolts | Lot | 1
| b) | Equipment Structure
| i. | LA | No. | 12
| ii. | CVT |  | Deleted
3B | 145 kV Indoor Type Gas Insulated Switchgear (GIS), equipment connection and steel structures
Deleted
3C | 36 kV Switchgear, equipment connection and steel structures
Deleted
3D |  | Transformers
Deleted
3E | Control, Protection, SAS and Metering
245kV Circuits
3E1 |  | Control, Protection,monitoring & SAS Function for overhead line circuits | set | 4
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | set | 1
| b) | Protection main relay (Main-1, Main-2) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
3E2 |  | Deleted
3E3 |  | Deleted
3E4 |  | Extension of Busbar Protection | lot | 1
| a) | Control Mimic panel with all accessories including monitoring | NA
| b) | Protection main relay ( Bay Unit )
| i) | Central Unit extension card | set | 1
| ii) | Bay Unit with HMI | set | 4
| c) | Selector Switch for Enabling/Disabling BBP,BFP, all function | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
3E5 |  | Tarif metering
| a) | Meters | No. | 8
| b) | Panel including wiring, lighting,humidity controller, heater & other accessories | lot | 1
145kV Circuits
Deleted
36kV Circuit
Deleted
3E6 | Substation Automation system
| i. | BCU
| a) | for 245kV Circuits | No. | 4
| b) | for 145kV Circuits | No. | Deleted
| c) | 33kV Circuits | No. | Deleted
| ii. | Industrial Server PC cum Operator workstation with SAS & Enginering Software | Set | Deleted
| iii. | Ethernet Switch for SAS | Lot | 1
| iv. | GPS system | Set | Deleted
| v. | Common alarm unit with hooter/buzzer for annunciation | Set | Deleted
| vi. | LCD Monitor, 55" or Large | Set | Deleted
| vii. | Printer, A4 Laser (One black & White, Other Color) | Set | Deleted
| viii. | Engineering PC: core i7, 1TB HDD, 8GB RAM, 22'' display for SAS & SCADA | No. | Deleted
| ix. | Cable (Fiber Optic, Ethernet, Copper etc.) | Lot | 1
| x. | Panel including wiring, lighting,heater & other accessories | Lot | 1
| xi. | Other Accessories (if any) | Lot | 1
3F | Extension of SCADA system for Telecontrol and Telemetering
| a) | Equipment at Substation
| i. | Modification of Gateway (server, engineering software) | Set | 2
| ii. | Ethernet Switch | Set | Deleted
| iii. | Hardware Firewall | Set | Deleted
| iv. | Additional 33kV Feeder BCU | set | Deleted
| v. | Panel including wiring, lighting,heater & other accessories | lot | Deleted
| vi. | Cables | lot | Deleted
| vii. | Other Accessories (if any) | lot | Deleted
| b) | Integration work with Master & Backup NLDC including Engineering & Commissioning | refere to Schedule B4
3G | Digital Fault & Disturbance Recorder (Extension)
3G1 | i. | DFDR processor | Set | 1
| ii. | Card for each bay including A/D Converter, Digital & Analog data acquisition system
| a) | for 245kV Circuits | set | 4
| b) | for 145kV Circuits | Deleted
| iii. | Ethernet Switch | Deleted
| iv | GPS system | Deleted
| v. | Panel including wiring, lighting,heater & other accessories | Lot | 1
| vi. | Engineering PC: core i7, 500GB HDD, 8GB RAM, 17'' display | set | Deleted
3H |  | GIL & Power Cable
Deleted
3I |  | Multicore Cables
Multicore Cables for control, protection, metering & power circuits
| i. | _LV Control Cable | lot | 1
| ii. | _LV Power Cable | lot | 1
3J |  | Earthing and Lightning Protection system and Portable Eathing Equipment
3J1 |  | Earthing and Lightning Protection system
| i. | _Extension of Earthing system for bay extension work | lot | 1
| ii. | _Extension of Lighting Protection System for bay extension work | lot | 1
3J2 |  | Portable(maintenance) earthing equipment device | set | 1
3K |  | Batteries, chargers & DC distribution
3K1 |  | 110V Ni-cad Batteries with chargers & distribution board (including 2 sets 4kVA Inverter)
| i. | _110V Battery Banks, 600Ah | Deleted
| ii. | _Charger 600A | Deleted
| iii. | _4kVA Inverter | Deleted
| iv. | _ Extension of 110V DC Distribution panel, MCC type | lot | 1
3K2 |  | 48V Ni-cad Batteries with chargers & distribution board
| i. | _48V battery Banks,150Ah | Deleted
| ii. | _Charger 70A | Deleted
| iii. | _Extension of 48V DC Disatribution Panel | lot | 1
3L | LVAC Distribution
3K1 | _Extension of AC 415V or 240V distribution panels (MCC type) |  | lot | 1
3K2 | _Tariff metering at LV side(Main & Check) |  | Deleted
3M | Civil Works, Building and Foundation |  | Refer to Schedule B4
3N | Lighting, small power, air conditioning and Ventilation
3N1 | Indoor Lighting (LED type), small power, air conditioning and Ventilation and emergency DC lighting required for bay extension work for control building and local control houses |  | lot | 1
3N2 | Lighting (LED type) for ouside building required for bay extension work for security, roadway, switchyard and emergency DC lighting |  | lot | 1
3O | Fibre Optic Multiplexer Equipment for Communication and Protection
3O1 | Extension of Indoor Fibre Optic Multipexer Equipment |  | lot | 1
3O2 | PABX Card & telephone set |  | Deleted
3O3 | Under ground optical fiber cable, armoured, 48 core including Outdoor termination box,indoor MDF & pigtail cables |  | lot | 1
3O4 | Extension of PDH & SDH and 48 Core ODF with necessary connection work and testing shall be installed. |  | lot | 1
Total Price (for Extension works at GAZARIA SS) carried to Summary of Price Schedule
Total Price in words (for Extension works at GAZARIA SS)............................................................................................................................................................................
Extension of 132kV AIS bays at 230/132 kV Comilla (North) AIS Substation
Item No. | Description of Equipment Requirement |  | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
[5 empty] | Unit Price | Total Price | Unit Price | Total Price
[5 empty] | CIP | CIP | EXW | EXW
|  |  |  | (1) | (2) | (3) = (1) x (2) | (4) | (5)=(1)x(4)
4A | 230 kV switchgear, equipment connection and steel structures
Deleted
4B | 145 kV Indoor Type Gas Insulated Switchgear (GIS), equipment connection and steel structures
Deleted
145 kV Indoor Type Air Insulated Switchgear (AIS), equipment connection and steel structures
4B1 |  | SF6 Circuit breaker,1600A, 40kA/1s,live tank, single pole operating for Line Bay | Set | 2
4B2 |  | Disconnector switch without E/S, 1600A,40kA/1s for Line bay | Set | 4
4B3 |  | Disconnector switch with E/S, 1600A,40kA/1s | Set | 2
4B4 |  | Disconnector switch without E/S, 1600A,40kA/1s | Set | 2
4B5 |  | Single phase current transformer, 5-core,40kA/1s | No. | 6
4B6 |  | Single phase Inductive voltage transformer (IVT), 2-core | No. | 6
4B7 |  | Single phase surge arrester, 120kV rated,10kA | No. | 6
4B8 |  | Flexible conductorsfor bus and jumper, insulators, fittings including all necessary clamps and connectors for extension work
| i. | _Flexible Conductor for Bus, jumper, equipment connections | Lot | 1
| ii. | _Insulator | Lot | 1
| iii. | _Fittings | Lot | 1
4B9 |  | Steel Structures for gantry and equipment supports required for this extension work
| a) | _Gantry Column including nut & bolts
| i) | For Main Bus | nos. | 2
| ii) | For Jack-Bus | nos. | 2
| b) | _Gantry beam at Main Bus & Jack-Bus height including nut & bolts | nos. | 4
| c) | _Equipment support structures including nut & bolts
| i) | CB | set | 2
| ii) | DS without ES | set | 6
| iii) | DS with ES | set | 2
| iv) | Bus ES | Deleted
| v) | CT | nos. | 6
| vi) | CVT/IVT | nos. | 6
| vii) | LA | nos. | 6
| ix) | PI | Deleted
| d) | _Cable tray including fitting, fixing accessories | lot | 1
4C | 33 kV Switchgear, equipment connection and steel structures
Deleted
4D | Transformers
Deleted
4E | Control, Protection, SAS and Metering
245kV Circuits
Deleted
145kV Circuits
4E1 |  | Control, Protection,monitoring & SAS Function for overhead line circuits | set | 2
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main & Backup) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
4E2 |  | Deleted
4E3 |  | Deleted
4E4 |  | Extension of Busbar Protection | lot | 1
| a) | Control Mimic panel with all accessories including monitoring | NA
| b) | Protection main relay ( Bay Unit ) | lot | 1
| i) | Central Unit extension card | lot | 1
| ii) | Bay Unit with HMI | lot | 1
| c) | Selector Switch for Enabling/Disabling BBP,BFP, all function | lot | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | lot | 1
4E5 |  | Tarif metering | lot | 1
| a) | Meters | No. | 4
| b) | Panel including wiring, lighting,heater, humidity sensor & other accessories | lot | 1
36kV Circuit
Deleted
4E6 | Substation Automation system |  | Deleted
| i. | BCU
| a) | for 245kV Circuits | No. | #REF!
| b) | for 145kV Circuits | No. | #REF!
| c) | 33kV Circuits | No. | #REF!
| ii. | Industrial Server PC ( and/ HMI) with SAS & Enginering Software | Set | 2
| iii. | Ethernet Switch for SAS | Lot | 1
| iv. | GPS system | Set | 1
| v. | Operator workstation | Set | 2
| vi. | LCD Monitor, 55" or Large | Set | 1
| vii. | Printer, A4 Laser (One black & White, Other Color) | Set | 2
| viii. | Engineering PC: core i7, 1TB HDD, 8GB RAM, 22'' display for SAS & SCADA | No. | 1
| ix. | Cable (Fiber Optic, Ethernet, Copper etc.) | Lot | 1
| x. | Panel including wiring, lighting,heater & other accessories | Lot | 1
| xi. | Other Accessories (if any) | Lot | 1
4F | SCADA system for Telecontrol and Telemetering |  |  | 1
| a) | Extension of SCADA system including hardwire & software modification in existing RTU/gateway, Supply of IED/transducer, sub-rack with I/O card, CPU, necessary wiring required for MiCOM264 RTU | lot | 1
| b) | Integration work with Master & Backup NLDC including Engineering & Commissioning | refere to Schedule B4
4G | Digital Fault & Disturbance Recorder |  | Deleted
4H |  | GIL & Power Cable | Deleted
4I |  | Multicore Cables
Multicore Cables for control, protection, metering & power circuits
| i. | _LV Control Cable | lot | 1
| ii. | _LV Power Cable | lot | 1
4J |  | Earthing and Lightning Protection system and Portable Eathing Equipment
1J1 |  | Earthing and Lightning Protection system
| i. | _Extension of Earthing system for bay extension work | lot | 1
| ii. | _Extension of Lighting Protection System for bay extension work | lot | 1
4J2 |  | Portable(maintenance) earthing equipment device | set | 1
4K | Batteries, chargers & DC distribution
4K1 |  | 110V Ni-cad Batteries with chargers & distribution board (including 2 sets 4kVA UPS, 30 mins)
| i. | _110V Battery Banks, 500Ah | Deleted
| ii. | _Charger 170A | Deleted
| iii. | _4kVA Inverter | Deleted
| iv. | _ Extension of 110V DC Distribution panel, MCC type | lot | 1
4K2 |  | 48V Ni-cad Batteries with chargers & distribution board
| i. | _48V battery Banks,150Ah | Deleted
| ii. | _Charger 70A | Deleted
| iii. | _Extension of 48V DC Disatribution Panel | lot | 1
4L | LVAC Distribution
4L1 | _Extension of AC 415V or 240V distribution panels (MCC type) |  | lot | 1
4L2 | _Tariff metering at LV side(Main & Check) |  | Deleted
4M | Civil Works, Building and Foundation |  | Refer to Schedule B4
4N | Lighting, small power, air conditioning and Ventilation
4N1 | Indoor Lighting (LED type), small power, air conditioning and Ventilation and emergency DC lighting required for bay extension work for control building and local control houses |  | Deleted
4N2 | Lighting (LED type) for ouside building required for bay extension work for security, roadway, switchyard and emergency DC lighting |  | lot | 1
4O | Fibre Optic Multiplexer Equipment and PLC Equipment for Communication and Protection
4O1 | Extension of Indoor Fibre Optic Multipexer Equipment |  | lot | 1
4O2 | PABX Card & telephone set |  | Deleted
4O3 | Under ground optical fiber cable, armoured, 48 core including Outdoor termination box,indoor MDF & pigtail cables |  | lot | 1
4O4 | Extension of PDH & SDH and 48 Core ODF with necessary connection work and testing shall be installed. |  | lot | 1
Total Price (for Extension works at Comilla(N) SS) carried to Summary of Price Schedule
Total Price in words (for Extension works at Comilla(N) SS)............................................................................................................................................................................

## Schedule B3
Schedule B3: Design Services
New 230/132/33 kV Substation at KACHUA
Item No | Description of Required Services | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
|  |  |  | Unit Price | Total Price | Unit Price | Total Price
|  |  |  | foreign portion | foreign portion | local portion | local portion
|  |  | (1) | (2) | (3) = (1) x (2) | (4) | (5)=(1) x (4)
| Design and engineering services, local and foreign part | Lump sum | 1
New 230/132/33 kV Substation at KACHUA
Subtotal - to Schedule B5 - Grand Total
New 132/33 kV Substation at LAKSHAM
Item No | Description of Required Services | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
|  |  |  | Unit Price | Total Price | Unit Price | Total Price
|  |  |  | foreign portion | foreign portion | local portion | local portion
|  |  | (1) | (2) | (3) = (1) x (2) | (4) | (5)=(1) x (4)
| Design and engineering services, local and foreign part | Lump sum | 1
New 132/33 kV Substation at LAKSHAM
Subtotal - to Schedule B5 - Grand Total
New 132/33 kV Substation at Muradnagar
Item No | Description of Required Services | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
|  |  |  | Unit Price | Total Price | Unit Price | Total Price
|  |  |  | foreign portion | foreign portion | local portion | local portion
|  |  | (1) | (2) | (3) = (1) x (2) | (4) | (5)=(1) x (4)
| Design and engineering services, local and foreign part | Lump sum | 1
New 132/33 kV Substation at Muradnagar
Subtotal - to Schedule B5 - Grand Total
New 132/33 kV Substation at Chandina
Item No | Description of Required Services | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
|  |  |  | Unit Price | Total Price | Unit Price | Total Price
|  |  |  | foreign portion | foreign portion | local portion | local portion
|  |  | (1) | (2) | (3) = (1) x (2) | (4) | (5)=(1) x (4)
| Design and engineering services, local and foreign part | Lump sum | 1
New 132/33 kV Substation at Chandina
Subtotal - to Schedule B5 - Grand Total
New 132/33 kV Substation at Laxmipur
Item No | Description of Required Services | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
|  |  |  | Unit Price | Total Price | Unit Price | Total Price
|  |  |  | foreign portion | foreign portion | local portion | local portion
|  |  | (1) | (2) | (3) = (1) x (2) | (4) | (5)=(1) x (4)
| Design and engineering services, local and foreign part | Lump sum | 1
New 132/33 kV Substation at Laxmipur
Subtotal - to Schedule B5 - Grand Total
New 132/33 kV Substation at Kosba
Item No | Description of Required Services | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
|  |  |  | Unit Price | Total Price | Unit Price | Total Price
|  |  |  | foreign portion | foreign portion | local portion | local portion
|  |  | (1) | (2) | (3) = (1) x (2) | (4) | (5)=(1) x (4)
| Design and engineering services, local and foreign part | Lump sum | 1
New 132/33 kV Substation at Kosba
Subtotal - to Schedule B5 - Grand Total
Extension of 230kV Bays at GAZARIA 230/132 kV GIS Substation
Item No | Description of Required Services | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
|  |  |  | Unit Price | Total Price | Unit Price | Total Price
|  |  |  | foreign portion | foreign portion | local portion | local portion
|  |  | (1) | (2) | (3) = (1) x (2) | (4) | (5)=(1) x (4)
| Design and engineering services, local and foreign part | Lump sum | 1
Extension of 230kV Bays at GAZARIA 230/132 kV GIS Substation
Subtotal - to Schedule B5 - Grand Total
Extension of 132kV Bays at existing COMILLA NORTH 230/132 kV AIS Substation
Item No | Description of Required Services | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
|  |  |  | Unit Price | Total Price | Unit Price | Total Price
|  |  |  | foreign portion | foreign portion | local portion | local portion
|  |  | (1) | (2) | (3) = (1) x (2) | (4) | (5)=(1) x (4)
| Design and engineering services, local and foreign part | Lump sum | 1
Extension of 132kV Bays at existing COMILLA NORTH 230/132 kV AIS Substation
Subtotal - to Schedule B5 - Grand Total

## Schedule B4
Schedule 4: Installation and Other Services
New 230/132/33 kV Substation at KACHUA
Item No. | Description of Equipment Requirement |  | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
[5 empty] | Unit Price | Total Price | Unit Price | Total Price
[7 empty] | EXW | EXW
|  |  |  | (1) | (2) | (3) = (1) x (2) | (4) | (5)=(1)x(4)
A | 230 kV switchgear, equipment connection and steel structures
1A1 | 245kV GIS Line Feeder Bays, each comprising: |  | Set | 8
| i. | 245kV, 4000A, 50kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 245kV, 3150A, 50kA/3s, three phase, single pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 245kV,3150A, 50kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 245kV, 50kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 245kV, 3150A, 50kA/3s three phase line disconnector integral with high speed earth switch complete with motor operating mechanism | sets | 1
| vi | 245kV, 50kA/3s single phase, 5-core, current transformer | No. | 3
| vii. | 245kV single phase, 3 core, Class 0.2, 10VA for Metering and Class 3P,15VA for Protection, voltage transformer | No. | 3
| viii. | 245kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Cubicle | set | 1
| x | Offline PD Monitoring facility in compartments | Lot | 1
| xi. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
1A2 | 245kV GIS Auto Transformer Feeder Bays, each comprising: |  | Set | 2
| i. | 245kV, 4000A, 50kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 245kV, 3150A, 50kA/3s, three phase, Gang pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 245kV, 3150A, 50kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 245kV, 50kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 245kV, 3150A, 50kA/3s, three phase line side disconnector with earth switch complete with motor operating mechanism | sets | 1
| vi | 245kV, 50kA/3s, single phase, 5-core, current transformer | No. | 3
| vii. | 245kV single phase, 3 core, Class 0.2,10VA for Metering and Class 3P,15VA for Protection, voltage transformer | No. | 3
| viii. | 245kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Cubicle | No. | 1
| x | Offline PD Monitoring facility in compartments | Lot | 1
| xi. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for single-core cables, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
1A3 | 245kV Bus Coupler Bays , each comprising: |  | set | 1
| i. | 245kV, 4000A, 50kA/3s, three phase double busbar | Lot | 1
| ii. | 245kV, 50kA/3s, three phase, gang pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| ii. | 245kV, 50kA/3s, three phase busbar disconnector complete with motor operating mechanism | Set | 2
| iv. | 245kV, 50kA/3s, three phase, three position earth switch complete with motor operating mechanism, on either side of circuit breaker. | Set | 2
| v. | 245kV, 50kA/3s, single phase, 3-core, current transformer | No. | 3
| vi. | 245kV, 50kA/3s, single phase, 2-core, current transformers | No. | 3
| vii. | Local Control Cubicle | set | 1
| viii. | Offline PD Monitoring facility in compartments | Lot | 1
| ix. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
1A4 | 245kV GIS Double Busbar with VT/ES, each comprising: |  | Set | 1
| i. | 245kV, 4000A, 50kV/3s, three phase double busbars | Lot | 1
| ii. | 245kV single phase, 2 core, Class 0.2, 10VA for Metering and Class 3P, 15VA for Protection, voltage transformer | No. | 6
| iii. | 245kV, 50kA/3s, three phase, three position earth switches complete with motor operating Mechanism | set | 2
| iv. | Offline PD Monitoring facility in compartments | Lot | 1
| v. | Local Control Cubicle | No. | 1
1A5 | 216kV rated voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase surge arresters |  | No. | 30
1A6 | Rigid tubular conductor and/or stranded conductors including accessories for each connection as required for completing 230kV GIS Switchyard
| i. | Tubular Conductor | Lot | 1
| ii | Flexible Conductor | Lot | 1
1A7 | Insulator and fittings including all necessary clamps and connectors as required for completing 230kV GIS Switchyard
| i | Insulator | Lot | 1
| ii | Fittings & Clamps_Connector | Lot | 1
| ii | Nut-bolt | Lot | 1
| iv. | Cable trench including fitting, fixing accessories | Lot | 1
1A8 | Steel gantry, having double tier for each double circuit of 230kV Transmission Line & Equipment support Structure including all necessary accessories required for completing 230kV GIS Switchyard
| a) | Steel Structure
| i. | Gantry Column | No. | 10
| ii. | Beam | No. | 8
| iii. | Nut & Bolts | Lot | 1
| b) | Equipment Structure
| i. | LA | No. | 30
| ii. | CVT |  | Deleted
1B | 145 kV Indoor Type Gas Insulated Switchgear (GIS), equipment connection and steel structures
145 kV Indoor Type Gas Insulated Switchgear (GIS),
Deleted
145 kV Outdoor Type Air Insulated Switchgear (AIS)
1B1 | SF6 Circuit breaker,1600A,40kA/1s, live tank, single pole operating for Line Bay |  | set | 2
1B2 | SF6 Circuit breaker,2500A, 40kA/1s,live tank, gang operating for Transformer Bay |  | set | 2
1B3 | Disconnector switch without E/S, 1600A,40kA/1s for Line bay |  |  | 4
1B4 | Disconnector switch with E/S, 1600A,40kA/1s for Line Bay |  |  | 2
1B5 | Disconnector switch without E/S, 2500A,40kA/1s for Transformer Bay |  | set | 4
1B6 | Disconnector switch with E/S, 2500A,40kA/1s for Transformer Bay |  | set | 2
1B7 | Single phase current transformer,1600-3200/1, 5-core,40kA/1s for Line Bay |  | nos. | 6
1B8 | Single phase current transformer,2000-3200/1, 5-core,40kA/1s for tansformer bay |  | nos. | 6
1B9 | Single phase voltage transformer (VT), 3-core |  | nos. | 12
1B10 | 120kV rated voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase surge arresters |  | No. | 12
1B11 | Rigid tubular bus and/or stranded conductors including accessories for each connection as required for completing 145kV GIS Switchyard
| i. | Tubular Conductor | Lot | 1
| ii | Flexible Conductor | Lot | 1
1B12 | insulator and fittings including all necessary clamps and connectors as required for completing 145kV GIS Switchyard
| i | Insulator | Lot | 1
| ii | Fittings & Clamps_Connector | Lot | 1
| ii | Nut-bolt | Lot | 1
| iv. | Cable trench including fitting, fixing accessories | Lot | 1
1B13 | steel gantry, having double tier for each double circuit of 145kV Transmission Line including all necessary accessories required for completing 145kV GIS Switchyard
| a) | Steel Structure
| i. | _Gantry Column | No. | 5
| ii. | Beam
| 1) | at Bus Height | No. | 2
| 2) | at Jack-Bus Height | No. | 2
| iii. | Nut & Bolts | Lot | 1
| b) | Equipment Structure
| i. | CB | set | 4
| ii. | DS without ES | set | 8
| ii. | DS with ES | set | 4
| iv. | Bus ES | Deleted
| v. | CT | nos. | 12
| vi. | CVT/IVT | nos. | 12
| vii. | LA | nos. | 12
1C | 33 kV Switchgear, equipment connection and steel structures
One (1) set of complete equipment for switchgear 33 kV shall be designed, supplied, delivered, installed, tested and commissioned, under this contract, comprise the following:
1C1 | Circuit Breaker 36 kV, 630 A, 31.5kA/1s, 50 Hz, 170/70 kV BIL, three pole, vacuum type, for outdoor installation with one spring-stored energy operating mechanism |  | Set | 2
1C2 | Disconnector 36 kV, 630 A, 31.5kA/1s, 50 Hz, 170/70 kV BIL, three pole, single vertical break, post type, motor operated
| i) | DS without ES | set | 2
| ii) | DS with ES | set | 2
1C3 | Current transformer 36 kV, 31.5kA/1s, 50Hz, 170/70 kV BIL, single phase, 10/1, 630-1250/1 , 2-core, post type |  | nos. | 6
1C4 | Voltage transformer 36kV, 50Hz, 170/70 kV BIL, single phase, 33/V3 / 110/V3 / 110/V3 kV/V/V, 2 secondary windings, inductive type |  | nos. | 6
1C5 | Surge arrester 36 kV, 30 kV continuous operating voltage, 10 kA nominal discharge current, 50 Hz, single phase, gapless, metal oxide type |  | nos. | 6
1C6 | Gantry steel structures for Bus & Equipment, Conductor for 36kV Bus bar & equipment, 36kV XLPE cable for Tertiary side connection from power trans-former, Insulator and fittings including all necessary clamps and connectors, cable trench required to complete 33kV switchyard.
| i. | Flexible conductor for Bus & Equipment connection | Lot | 1
| ii. | Insulators and fittings incl. all necessary clamps and connectors,Nut-Bolt required for completing 33 kV switchyard | Lot | 1
| iii. | Gantry steel structures for Bus
| a) | Beam | No | 4
| b) | Column | No | 6
| iv. | steel structures for equipment supports required for completing 33 kV switchgear
| a) | CB,DS; CT,PT & LA ( 3 no.'s= 1set) | set | 12
| v. | XLPE Cable | m | 120
| vi. | Cable Sealing End | No | 12
| vii. | Cable trench | Lot | 1
1D |  | Transformers
1D1 |  | Autotransformer 230/135/34.5 kV three phase ONAF 350/350/100 MVA, ONAN 250/250/70 MVA, YNa0d1, with On-load tap changer, with tertiary winding (brought out to terminal bushings) | Set | 2
1D2 |  | Deleted
1D3 |  | On-line Dissolved Gas Analyzer & Moisture monitoring system for 230/135/34.5kV auto transformers | Set | 2
1D4 |  | Earthing / Auxiliary Power Transformer 33/0.415 kV, three phase 350 kVA, ZNyn11, ONAN, with Off-load tap changer, associated outdoor neutral CTs and steel support structures including all necessary connections. | Set | 2
1D5 |  | Complete Fire Fighting system for GIS Hall & Control Room
| i) | 230kV GIS Hall | Lot | 1
| ii) | 132kV GIS Hall | Deleted
| iii) | Panel & Control Room | Lot | 1
1D6 | a) | Fast Depressurization system for three phase outdoor type auto transformer | Set | 2
| b) | Water Spray system for three phase outdoor type auto transformer | Set | 2
1E | Control, Protection, SAS and Metering
245kV Circuits
1E1 | Control, Protection,monitoring & SAS Function for overhead line circuits |  | set | 8
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | set | 1
| b) | Protection main relays, Main-1 & Main-2 | set | 2
| c) | Auxiliary relays (TCS, Lockout etc) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
1E2 |  | Control, monitoring, Protection, monitoring & SAS Function for Auto transformer circuits | set | 2
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | set | 1
| b) | Protection main relay (Main-1, Main-2) | set | 2
| c) | Auxiliary relays (TCS, Lockout etc) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
1E3 |  | Control, Protection,monitoring & SAS Function for Bus Coupler circuits | set | 1
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | set | 1
| b) | Protection main relay | set | 1
| c) | Auxiliary relays (TCS, Lockout etc) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
1E4 |  | Busbar Protection | set | 1
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | NA
| b) | Protection main relay | set | 1
| i. | Bay unit with HMI | set | 11
| ii. | Central unit with HMI | set | 1
| c) | Selector Switch for Enabling/Disabling BBP,BFP, all function | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
1E5 |  | Tarif metering
| a) | Meters (Main & Check) | No. | 20
| b) | Panel including wiring, lighting, heater, humidity controller & other accessories | lot | 1
145kV Circuits
1E6 |  | Control, Protection,monitoring & SAS for overhead line circuits | set | 2
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | set | 1
| b) | Protection main relay (Main-1, Main-2) | set | 2
| c) | Auxiliary relays (TCS, Lockout etc) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
1E7 |  | Control, Protection,monitoring & SAS for Auto transformer circuits | set | 2
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | set | 1
| b) | Protection main relay (as Backup: 67,67N,50,50N,51,51N) | set | 2
| c) | Auxiliary relays (TCS, Lockout etc) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
1E8 |  | Deleted
1E9 |  | Busbar Protection | set | 1
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | NA
| b) | Protection main relay
| i. | Bay unit with HMI | set | 4
| ii. | Central unit HMI | set | 1
| c) | Selector Switch for Enabling/Disabling BBP,BFP, all function | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
1E10 |  | Tariff metering
| a) | Meters | No. | 8
| b) | Panel including wiring, lighting,heater, humidity controller & other accessories | lot | 1
36kV Circuit
1E11 |  | Control, Monitoring, Protection & SAS function for 33kV station power system | Set | 2
| a) | Control Mimic panel with all accessories including monitoring | Set | 2
| b) | Protection main relay ( as backup: 67,67N,50,50N,51,51N) | Set | 2
| c) | Auxiliary relays (TCS, Lockout etc) | Set | 2
| d) | Protecttion Panel including wiring, lighting,heater, humidity controller & other accessories | Set | 2
1E12 |  | Tariff metering
| a) | Meters (Main & Check) | No. | 4
| b) | Panel including wiring, lighting,heater, humidity sensor & other accessories | lot | 1
1E13 | Substation Automation system
| i. | BCU
| a) | for 245kV Circuits | No. | 11
| b) | for 145kV Circuits | No. | 4
| c) | 33kV Circuits | No. | 2
| ii. | Industrial Server PC ( Intel XEON Silver- 4116 processor, ECC memory) cum Operator workstation with SAS & Enginering Software | Set | 2
| iii. | Ethernet Switch for SAS | Lot | 1
| iv. | GPS system | Set | 1
| v. | Common alarm unit with hooter/buzzer for annunciation | Set | 1
| vi. | LCD Monitor, 55" or Large | Set | 1
| vii. | Printer, A4 Laser (One black & White, Other Color) | Set | 2
| viii. | Engineering PC: core i7-9800X series processor, 1TB HDD, 16GB RAM, 22'' display for SAS & SCADA | No. | 1
| ix. | Cable (Fiber Optic, Ethernet, Copper etc.) | Lot | 1
| x. | Panel including wiring, lighting,heater & other accessories | Lot | 1
| xi. | Other Accessories (if any) | Lot | 1
1F | SCADA system for Telecontrol and Telemetering
| a) | Equipment at Substation
| i. | Gateway (server, engineering software) | Set | 2
| ii. | Ethernet Switch | Set | 2
| iii. | Hardware Firewall | Set | 1
| iv. | Additional 33kV Feeder BCU | set | 5
| v. | Panel including wiring, lighting,heater, humidity controller & other accessories | lot | 1
| vi. | Cables | lot | 1
| vii. | Other Accessories (if any) | lot | 1
| b) | Integration work with Master & Backup NLDC including Engineering & Commissioning | lot | 1
1G | Digital Fault & Disturbance Recorder
1G1 | i. | DFDR processor | Set | 1
| ii. | Card for each bay including A/D Converter, Digital & Analog data acquisition system
| a) | for 245kV Circuits | set | 11
| b) | for 145kV Circuits | set | 4
| iii. | Ethernet Switch | set | 1
| iv | GPS system | set | 1
| v. | Panel including wiring, lighting, heater, humidity sensor & other accessories | Lot | 1
| vi. | Engineering PC: core i7-9700K, 1 TB HDD, 16GB RAM, 17'' display | set | 1
1H | GIL & Power Cable
1H1 | 132kV, 2000A GIL for connection between secondary side of Power transformer & 132kV switchgear near existing 132kV AIS Bus
| i) | GIL | m | 240
| ii) | SF6-Air Bushing | No. | 12
1H2 | 132kV, 2000A rated in Buried Soil XLPE power cable for con-nection between secondary side of Power transformer & 132kV switchgear near existing 132kV AIS Bus
| i) | Cable | m | 720
| ii) | Cable sealing End | No. | 12
1H3 | 36kV, 300 mm2 XLPE power cable for connection between tertiary side of Power transformer & 33/0.415kV Auxiliary transformer.
| i) | Cable | m | 90
| ii) | Cable sealing End | No. | 12
1I | Multicore Cables
Multicore Cables for control, protection, metering & power circuits
| i. | _LV Control Cable | lot | 1
| ii. | _LV Power Cable | lot | 1
1J | Earthing and Lightning Protection system and Portable Eathing Equipment
1J1 | Earthing and Lightning Protection system
| i. | _Earthing system for complete substation | lot | 1
| ii. | _Lighting Protection System for complete substation | lot | 1
1J2 | Portable(maintenance) earthing equipment device |  | set | 2
1K | Batteries, chargers & DC distribution
1K1 | 110V Ni-cad Batteries with chargers & distribution board (including 2 sets 5kVA Inverter) |  | lot | 1
| i. | _110V Battery Banks, 600Ah | set | 2
| ii. | _Charger 220A | set | 2
| iii. | _5kVA Inverter | set | 2
| iv. | _110V DC Distribution panel, MCC type | lot | 1
1K2 |  | 48V Ni-cad Batteries with chargers & distribution board
| i. | _48V battery Banks,150Ah | set | 2
| ii. | _Charger 70A | set | 2
| iii. | _48V DC Disatribution Panel | lot | 1
1L | LVAC Distribution
1L1 | _AC 415V or 240V distribution panels (MCC type) |  | lot | 1
1L2 | _Tariff metering at LV side(Main & Check) |  | No | 4
1M | Civil Works, Building and Foundation
1M.1 | Complete civil items required for outdoor works including boundary wall and slope protection
| a) | Complete Compacted Land development with carried/dredged earthfilling | CuM | 80950
| b) | Slope protection | sqm | 5100
| c) | Complete outdoor civil works
| i) | _Outdoor gantry foundation 230kV switchyard | nos. | 10
| ii) | _Outdoor equipment foundation 230kV switchyard
| a) | LA | nos. | 30
| iii) | _230kV Indoor GIS Foundation | Deleted
| iii) | _Outdoor gantry foundation 132kV switchyard | nos. | 5
| iv) | _Outdoor equipment foundation 132kV switchyard
| a) | CB | set | 4
| b) | DS without ES | set | 8
| c) | DS with ES | set | 4
| d) | Bus ES | Deleted
| e) | CT | nos. | 12
| f) | CVT/IVT | nos. | 12
| g) | LA | nos. | 12
| v) | _Outdoor equipment foundation 33kV switchyard
| a) | CB | set | 2
| b) | DS | set | 4
| c) | CT | set | 2
| d) | IVT | set | 2
| e) | LA | set | 2
| vi) | _Outdoor gantry/tubular busbar foundation 33kV switchyard | No | 6
| vii) | _Transformer foundation including oilpit & carrage way | No. | 2
| viii) | _Blast wall | nos. | 3
| ix) | Property Line Demarkation | rm | 600
| x) | _Security Boundary Wall
| a) | Boundary Wall | m | 600
| xi) | _Substation Main gate | No. | 1
| xii) | _Chainlink Fencing | Deleted
| xiii) | _Approach raod 6m width | m | 20
| xiv) | Box Culvert | Lot | 1
| xv) | _Internal road | lot | 1
| xvi) | _Surface drain | m | 600
| xvii) | _Cable Trench | lot | 1
| xviii) | _Switchyard surface finishing with drainage system | lot | 1
| xix) | _Gravel laying | lot | 1
| xx) | _Septic tank, sowak way | lot | 1
| xxi) | _Pump house including deep tubewell, motor, pump, water reservoir, water pipe line etc. | lot | 1
| xxii) | _Gurd house | No. | 1
| xxiii) | sentry post, | Nos | 4
| xxiv | car port | No | 1
1M2 | Complete civil works for 1 No. three storied GIS Hall, Operation & Panel Room
| i) | _Foundation works | lot | 1
| ii) | _Super structures | lot | 1
| iii) | _All finish works | lot | 1
| iv) | _10 ton EOT Crane | No. | 1
| v) | 6 person capacity lift | No | 1
1M3 | Testing of Foundation
| i) | _Compression Test | No. | 2
| ii) | _ Uplift Test | No. | 1
1M4 | Fire Fighting system for GIS Hall & Control Room
| i) | Fire Fighting system For GIS Room | Lot | 1
| ii) | Fire Fighting system For Operation & Panel Room | Lot | 1
1M5 | Complete transformer Protector system for transformers including Nitrogen Injection system : reservoir, pipe network and pump etc. |  | lot | 1
1M6 | Preservation of top soil before filling and re-spread of preserved soil after filling |  | sqm | 10120
1M7 | Laboratory test (Pb, Cd, Cr, Zn, Mn, As, Hg) of fill material for ensuring suitable material (non-contaminated). Once before filling |  | lot | 1
1M8 | Ensuring fencing, fire safety and occupational health safety during construction |  | lot | 1
1N | Lighting, small power, air conditioning and Ventilation
1N1 | Indoor Lighting (LED type), small power, air conditioning and Ventilation and emergency DC lighting for control building and local control houses |  | lot | 1
1N2 | Lighting (LED type) for ouside building for security, roadway, switchyard |  | lot | 1
1N3 | Complete solar system (1kW solar panel) including 12V VRLA maintenace free battery and other accessories for Substation emergency DC Lighting |  | Set | 1
1O | Fibre Optic Multiplexer Equipment and PLC Equipment for Communication and Protection
1O1 | Indoor Fibre Optic Multipexer Equipment |  | lot | 1
1O2 | PABX Card & tele-phone set |  | lot | 1
1O3 | under ground optical fiber cable, armoured, 48/24 core including Outdoor termination box,indoor MDF & pigtail cables |  | lot | 1
1O4 | PDH & SDH and 48/24 Core ODF with necessary connection work and testing shall be installed. |  | lot | 1
Total Price( for New Kochua 230/132/33kV SS) carried to Summary of Price Schedule
Total Price in words ( for New Kochua 230/132/33kV SS)...........................................................................................................................................................................
New 132/33 kV Substation at Laksham
Item No. | Description of Equipment Requirement |  | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
[5 empty] | Unit Price | Total Price | Unit Price | Total Price
[7 empty] | EXW | EXW
|  |  |  | (1) | (2) | (3) = (1) x (2) | (4) | (5)=(1)x(4)
2A.A | 230 kV switchgear, equipment connection and steel structures
Deleted
2A.B | 145 kV Indoor Type Gas Insulated Switchgear (GIS), equipment connection and steel structures
2A.B1 | 145kV GIS Line Feeder Bays
| a) | For Laksham SS | set | 2
Each Line bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1600A, 40kA/3s, three phase, single pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1600A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1600A, 40kA/3s three phase line disconnector integral with high speed earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer | sets | 3
| vii. | 145kV single phase voltage transformer 2 core, Class 0.2 for Metering and Class 3P for Protection | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Cubicle | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2A.B2 | 145kV GIS Transformer Feeder Bays: |  | Set | 2
| a) | For Laksham SS | set | 2
Each transformer bay shall comprise of the following equipment:
| i. | 145kV,2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1600A, 40kA/3s, three phase, Gang pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1600A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1600A, 40kA/3s three phase line side disconnector integral with earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer | sets | 3
| vii. | 145kV single phase voltage transformer 2core, Class 0.2 for Metering and Class 3P for Protection | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Cubicle | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2A.B3 | 145kV Bus Coupler Bays :
| a) | For Laksham SS | set | 1
Each Bus Coupler Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase double busbar | lot | 1
| ii. | 145kV, 2500A, 40kA/3s, three phase, Gang pole operation circuit breaker complete with spring-stored energy operating mechanism | No. | 1
| iii. | 145kV, 2500A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Sets | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism, on either side of circuit breaker. | sets | 2
| v. | 145kV, 2500A,40kA/3s, single phase, 2-core, current transformer | No. | 3
| vi. | 145kV, 2500A, 40kA/3s, single phase, 3-core, current transformers | No. | 3
| vii. | Local Control Cubicle | set | 1
| viii. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2A.B4 | 145kV GIS Double Busbar with VT/ES :
| a) | For Laksham SS | Set | 1
Each GIS Double Busbar with VT/ES Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase double busbars | Lot | 1
| ii. | 145kV, single phase, 2 cores voltage transformer | No. | 6
| iii. | 145kV, 40kA/3s, three phase, three position earth switches complete with motor operating Mechanism | Sets | 2
| iv. | Local Control Cubicle | Set | 1
132kV Air I nsulated Switchgear
2A.B5 | 120kV rated voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase surge arrester
| a) | For Laksham SS | No. | 12
2A.B6 | Rigid tubular conductor and/or stranded conductors including accessories for each connection as required for completing 145kV GIS Switchyard for all five (05) substations
| i. | Tubular Conductor | Lot | 1
| ii | Flexible Conductor | Lot | 1
2A.B7 | insulator and fittings including all necessary clamps and connectors as required for completing 145kV GIS Switchyard for all five (05) substations
| i | _Insulator | Lot | 1
| ii | Fittings & Clamps_Connector | Lot | 1
| ii | Nut-bolt | Lot | 1
| iv. | _Cable trench including fitting, fixing accessories | Lot | 1
2A.B8 | Steel gantry, having double tier for each double circuit of 145kV Transmission Line including all necessary accessories required for completing 145kV GIS Switchyard
| a) | Steel Structure
| i. | _Gantry Column | No. | 3
| ii. | Beam | No. | 2
| iii. | Nut & Bolts | Lot | 1
| b) | Equipment Structure
| i. | LA | No. | 12
2A.C 33 kV Switchgear, equipment connection and steel structures
One (1) set of complete equipment for switchgear 33 kV shall be designed, supplied, delivered, installed, tested and commissioned, under this contract, comprise the following:
2A.C1 | Circuit Breaker 36 kV, 2500 A, 31.5kA/1s, 50 Hz, 170/70 kV BIL, three pole, vacuum type, for outdoor installation with one spring-stored energy operating mechanism |  | Set | 2
2A.C2 | Disconnector 36 kV, 2500 A, 31.5 kA/1s, 50 Hz, 170/70 kV BIL, three pole, single vertical break, post type, motor operated
| i) | DS without ES | set | 2
| ii) | DS with ES | set | 2
2A.C3 | Current transformer 36 kV, 31.5 kA/1s, 50Hz, 170/70 kV BIL, single phase, 2500/1 , 3-core, post type with double secondary box |  | nos. | 6
2A.C4 | Voltage transformer 36kV, 50Hz, 170/70 kV BIL, single phase, 33/V3 / 0.110/V3 / 0.110/V3 kV, 3 secondary windings, inductive type with double secondary box |  | No. | 6
2A.C5 | Surge arrester 36 kV, 30 kV continuous operating voltage, 10 kA nominal discharge current, 50 Hz, single phase, gapless, metal oxide type for all five (05) substations |  | No. | 6
2A.C6 | DS with load break fuse (10A) etc. for Connection between 36kV busbar & 02 sets of 33/0.415kV Earthing/Auxiliary transformer. |  | Set | 2
2A.C7 | Gantry steel structures for Bus & Equipment, Conductor for 36kV,3000A Bus bar, Insulator and fittings including all necessary clamps and connectors required to complete 33kV switchyard
| i. | Flexible conductor for Bus & Equipment connection | Lot | 1
| ii. | Insulators and fittings incl. all necessary clamps and connectors,Nut-Bolt required for completing 33 kV switchyard | Lot | 1
| iii. | Gantry steel structures for Bus
| a) | Beam | No | 4
| b) | Column | No | 6
| iv. | Gantry steel structures for Transformer
| a) | Beam | No | 2
| b) | Column | No | 3
| v. | steel structures for equipment supports required for completing 33 kV switchgear
| a) | CB,DS; CT,PT & LA ( 3 No.s= 1set) | set | 11
| vi. | XLPE Cable | Deleted
| vii. | Cable Sealing End | Deleted
| viii. | Cable trench | Lot | 1
2A.D | Transformers
2A.D1 |  | Deleted
2A.D2 | Three phase outdoor type two-winding power transformer, 132/34.5kV, 80/120MVA (ONAN/ONAF) |  | Set | 2
2A.D3 | On-line Dissolved Gas monitoring system for 132/34.5kV transformers |  | Deleted
2A.D4 | Earthing / Auxiliary Power Transformer 33/0.415 kV, three phase 250 kVA, Dyn11, ONAN , associated outdoor neutral CTs and steel support structures including all necessary connections. |  | Set | 2
2A.D5 |  | Complete Fire Fighting system for GIS Hall & Control Room
| i) | 230kV GIS Hall | Deleted
| ii) | 132kV GIS Hall | Lot | 1
| iii) | Panel & Control Room | Lot | 1
2A.D6 | Transformer Fire-Fighting system (water Spray type) for three phase outdoor type power transformer |  | Deleted
2A.E | Control, Protection, SAS and Metering
245kV Circuits
Deleted
145kV Circuits
2A.E1 |  | Control, Protection,monitoring & SAS function for overhead line circuits | set | 2
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main & Backup) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2E2 |  | Control, Protection,monitoring & SAS function for Power transformer circuits | set | 2
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main & Backup) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2A.E3 |  | Control, Protection,monitoring & SAS function for Bus Coupler circuits | set | 1
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay | set | 1
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2A.E3 |  | Busbar Protection | set | 1
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | NA
| b) | Protection main relay
| i. | Bay unit with HMI | set | 5
| ii. | Central unit HMI | set | 1
| c) | Selector Switch for Enabling/Disabling BBP,BFP, all function | set | 1
| d) | Protecttion Panel including wiring, lighting,heater, humidity sensor & other accessories | set | 1
2A.E4 |  | Tariff metering
| a) | Meters (Main & Check) | No. | 8
| b) | Panel including wiring, lighting,heater, humidity sensor & other accessories | lot | 1
36kV Circuit
2A.E5 |  | Control, Monitoring, Protection & SAS for 33kV station power system | Set | 2
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | Set | 1
| b) | Protection main relay (67,67N,50,50N,51,51N etc) | Set | 1
| c) | Auxiliary relays (TCS, Lockout etc) | Set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | Set | 1
2A.E6 |  | Tariff metering
| a) | Meters (Main & Check) | No. | 4
| b) | Panel including wiring, lighting,heater & other accessories | lot | 1
2A.E7 |  | Substation Automation system
| i. | BCU
| a) | for 245kV Circuits | No. | NA
| b) | for 145kV Circuits | No. | 2
| c) | 33kV Circuits | No. | 2
| ii. | Industrial Server PC ( Intel XEON Silver- 4116 processor, ECC memory) cum Operator workstation with SAS & Enginering Software | Set | 2
| iii. | Ethernet Switch for SAS | Lot | 1
| iv. | GPS system | Set | 1
| v. | Common alarm unit with hooter/buzzer for annunciation | Set | 2
| vi. | LCD Monitor, 55" or Large | Set | 1
| vii. | Printer, A4 Laser (One black & White, Other Color) | Set | 2
| viii. | Engineering PC: core i7-9800X series processor, 1TB HDD, 16GB RAM, 22'' display for SAS & SCADA | No. | 1
| ix. | Cable (Fiber Optic, Ethernet, Copper etc.)
| x. | Panel including wiring, lighting,heater & other accessories | Lot | 1
| xi. | Other Accessories (if any) | Lot | 1
2A.F | SCADA system for Telecontrol and Telemetering
| a) | Equipment at Substation
| i. | Gateway (server, engineering software) | Set | 2
| ii. | Ethernet Switch | Set | 2
| iii. | Hardware Firewall | Set | 1
| iv. | Additional 33kV Feeder BCU | set | 5
| v. | Panel including wiring, lighting,heater & other accessories | lot | 1
| vi. | Cables | lot | 1
| vii. | Other Accessories (if any) | lot | 1
| b) | Integration work with Master & Backup NLDC including Engineering & Commissioning | lot | 1
2A.G | Digital Fault & Disturbance Recorder
Deleted
2A.H |  | GIL & Power Cable
Deleted
2A.I |  | Multicore Cables
Multicore Cables for control, protection, metering & power circuits
| i. | _LV Control Cable | lot | 1
| ii. | _LV Power Cable | lot | 1
2A.J |  | Earthing and Lightning Protection system and Portable Eathing Equipment
2A.J1 |  | Earthing and Lightning Protection system
| i. | _Earthing system for complete substation | lot | 1
| ii. | _Lightning Protection System for complete substation | lot | 1
2A.I2 |  | Portable(maintenance) earthing equipment device | set | 1
2A.K |  | Batteries, chargers & DC distribution
2A.K1 |  | 110V Ni-cad Batteries with chargers & distribution board (including 2 sets 3kVA Inverter) | lot | 1
| i. | _110V Battery Banks, 500Ah | set | 2
| ii. | _Charger 170A | set | 2
| iii. | _3kVA Inverter | set | 1
| iv. | _110V DC Distribution panel, MCC type | lot | 1
2A.K2 |  | 48V Ni-cad Batteries with chargers & distribution board
| i. | _48V battery Banks,150Ah | set | 2
| ii. | _Charger, 70A | set | 2
| iii. | _48V DC Disatribution Panel | lot | 1
2A.L | LVAC Distribution
2A.L1 | _AC 415V or 240V distribution panels (MCC type) |  | lot | 1
2A.L2 | _Tariff metering at LV side(Main & Check) |  | No. | 4
2A.M | Civil Works, Building and Foundation
2A.M1 |  | Complete civil items required for outdoor works including boundary wall and slope protection
| a) | Complete Compacted Land development with carried/dredged earthfilling | CuM | 32400
| b) | Slope Protection | sqm | 3250
| c) | Complete outdoor civil works
| i) | _Outdoor gantry foundation 230kV switchyard | Deleted
| ii) | _Outdoor equipment foundation 230kV switchyard | Deleted
| iii) | _Indoor GIS Foundation 230kV | Deleted
| iii) | _Outdoor gantry foundation 132kV switchyard | nos. | 3
| iv) | _Outdoor equipment foundation 132kV switchyard
| a) | LA | nos. | 12
| v) | _Indoor GIS Foundation 132kV | Deleted
| vi) | _Outdoor equipment foundation 33kV switchyard
| a) | CB | set | 2
| b) | DS | set | 4
| c) | CT | set | 2
| d) | IVT | set | 2
| e) | LA | set | 2
| vii) | _Outdoor gantry/tubular busbar foundation 33kV switchyard | No | 9
| viii) | _Transformer foundation including oilpit & carrage way | nos. | 2
| ix) | _Blast wall | nos. | 3
| x) | Property line Demarkation | rm | 400
| xi) | _Security Boundary Wall with retaining wall | m | 400
| xii) | _Substation Main gate | No. | 1
| xiii) | _Chainlink Fencing | Deleted
| xiv) | _Approach raod 6m width | m | 20
| xv) | Box Culvert | lot | 1
| xvi) | _Internal road | lot | 1
| xvii) | _Surface drain | m | 400
| xviii) | _Cable Trench | lot | 1
| xix) | _Switchyard surface finishing with drainage system | lot | 1
| xx) | _Gravel laying | lot | 1
| xxi) | _Septic tank, sowak way | lot | 1
| xxii) | _Pump house including deep tubewell, motor, pump, water reservoir, water pipe line etc. | lot | 1
| xxiii) | _Gurd house | No | 1
| xxiv) | sentry post, | No. | 4
| xxv) | car port | No. | 1
2A.M2 | Complete civil works for one no's three storied 132kV GIS & Operation Room
| i) | _Foundation works | Lot | 1
| ii) | _Super structures | Lot | 1
| iii) | _All finish works | Lot | 1
| iv) | _10 ton EOT Crane | No. | 1
| v) | 6 person lift | No | 1
2A.M3 |  | Testing of Foundation
| i) | Compression test of pile | Nos | 2
| ii) | Uplift test of pile | Nos | 1
2A.M4 | Fire Fighting system for GIS Hall & Control Room
| i) | Fire Fighting system For GIS Room | Lot | 1
| ii) | Fire Fighting system For Operation & Panel Room | Lot | 1
2A.M5 | Complete Water spray system for transformers fire-fighting including reservoir, pipe network and pump etc. |  | Deleted
2A.M6 | Preservation of top soil before filling and re-spread of preserved soil after filling |  | sqm | 4050 |  |  |  |  | 4046.856
2A.M7 | Laboratory test (Pb, Cd, Cr, Zn, Mn, As, Hg) of fill material for ensuring suitable material (non-contaminated). Once before filling |  | lot | 1
2A.M8 | Ensuring fencing, fire safety and occupational health safety during construction |  | lot | 1
2A.N | Lighting, small power, air conditioning and Ventilation
2A.N1 | Indoor Lighting (LED type), small power, air conditioning and Ventilation and emergency DC lighting for control building and local control houses |  | lot | 1
2A.N2 | Lighting (LED type) for ouside building area for security, roadway, switchyard and emergency DC lighting |  | lot | 1
2A.N3 | Complete solar system (1kW solar panel) including 12V VRLA maintenace free battery and other accessories for Substation emergency DC Lighting |  | Set | 1
2A.O | Fibre Optic Multiplexer Equipment for Communication and Protection
2A.O1 | Indoor Fibre Optic Multipexer Equipment |  | lot | 1
2A.O2 | PABX Card & telephone set |  | lot | 1
2A.O3 | Under ground optical fiber cable, armoured, 48/24 core including Outdoor termination box,indoor MDF & pigtail cables |  | lot | 1
2A.O4 | PDH & SDH and 48/24 Core ODF with necessary connection work and testing shall be installed. |  | lot | 1
Total Price ( for New Laksham 132/33kV SS) carried to Summary of Price Schedule
Total Price in words ( for New Laksham 132/33kV SS) ............................................................................................................................................................................
New132/33 kV Substation at Muradnagar
Item No. | Description of Equipment Requirement |  | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
[5 empty] | Unit Price | Total Price | Unit Price | Total Price
[7 empty] | EXW | EXW
|  |  |  | (1) | (2) | (3) = (1) x (2) | (4) | (5)=(1)x(4)
2B.A | 230 kV switchgear, equipment connection and steel structures
Deleted
2B.B | 145 kV Indoor Type Gas Insulated Switchgear (GIS), equipment connection and steel structures
2B.B1 | 145kV GIS Line Feeder Bays
| b) | For Muradnagr SS | set | 6
Each Line bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1600A, 40kA/3s, three phase, single pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1600A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1600A, 40kA/3s three phase line disconnector integral with high speed earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer | sets | 3
| vii. | 145kV single phase voltage transformer 2 core, Class 0.2 for Metering and Class 3P for Protection | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Cubicle | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2B.B2 | 145kV GIS Transformer Feeder Bays:
| b) | For Muradnagr SS | set | 2
Each transformer bay shall comprise of the following equipment:
| i. | 145kV,2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1600A, 40kA/3s, three phase, Gang pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1600A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1600A, 40kA/3s three phase line side disconnector integral with earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer | sets | 3
| vii. | 145kV single phase voltage transformer 2core, Class 0.2 for Metering and Class 3P for Protection | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Cubicle | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2B.B3 | 145kV Bus Coupler Bays :
| a) | For Laksham SS | set | 1
Each Bus Coupler Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase double busbar | lot | 1
| ii. | 145kV, 2500A, 40kA/3s, three phase, Gang pole operation circuit breaker complete with spring-stored energy operating mechanism | No. | 1
| iii. | 145kV, 2500A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Sets | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism, on either side of circuit breaker. | sets | 2
| v. | 145kV, 40kA/3s, single phase, 2-core, current transformer with cores as follows: | No. | 3
| vi. | 145kV, 2500A, 40kA/3s, single phase, 3-core, current transformers with cores as follows: | No. | 3
| vii. | Local Control Cubicle | set | 1
| viii. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2B.B4 | 145kV GIS Double Busbar with VT/ES :
| a) | For Muradnagar SS | Set | 1
Each GIS Double Busbar with VT/ES Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kV/3s, three phase double busbars | Lot | 1
| ii. | 145kV, single phase, 2 cores voltage transformer | No. | 6
| iii. | 145kV, 40kA/3s, three phase, three position earth switches complete with motor operating Mechanism | Sets | 2
| iv. | Local Control Cubicle | Set | 1
132kV Air I nsulated Switchgear
2A.B5 | 120kV rated voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase surge arresters
| b) | For Muradnagr SS | No. | 24
2B.B6 | Rigid tubular bus and/or stranded conductors including accessories for each connection as required for completing 145kV GIS Switchyard for all five (05) substations
| i. | Tubular Conductor | Lot | 1
| ii | Flexible Conductor | Lot | 1
2B.B7 | insulator and fittings including all necessary clamps and connectors as required for completing 145kV GIS Switchyard
| i | _Insulator | Lot | 1
| ii | Fittings & Clamps_Connector | Lot | 1
| ii | Nut-bolt | Lot | 1
| iv. | _Cable trench including fitting, fixing accessories | Lot | 1
2B.B8 | Steel gantry, having double tier for each double circuit of 145kV Transmission Line including all necessary accessories required for completing 145kV GIS Switchyard
| a) | Steel Structure
| i. | _Gantry Column | No. | 9
| ii. | Beam | No. | 8
| iii. | Nut & Bolts | Lot | 1
| b) | Equipment Structure
| i. | LA | No. | 24
2B.C 33 kV Switchgear, equipment connection and steel structures
One (1) set of complete equipment for switchgear 33 kV shall be designed, supplied, delivered, installed, tested and commissioned, under this contract, comprise the following:
2B.C1 | Circuit Breaker 36 kV, 2500 A, 31.5kA/1s, 50 Hz, 170/70 kV BIL, three pole, vacuum type, for outdoor installation with one spring-stored energy operating mechanism |  | Set | 2
2B.C2 | Disconnector 36 kV, 2500 A, 31.5 kA/1s, 50 Hz, 170/70 kV BIL, three pole, single vertical break, post type, motor operated
| i) | DS without ES | set | 2
| ii) | DS with ES | set | 2
2B.C3 | Current transformer 36 kV, 31.5 kA/1s, 50Hz, 170/70 kV BIL, single phase, 2500/1 , 3-core, post type with double secondary box |  | nos. | 6
2B.C4 | Voltage transformer 36kV, 50Hz, 170/70 kV BIL, single phase, 33/V3 / 0.110/V3 / 0.110/V3 kV, 3 secondary windings, inductive type with double secondary box |  | No. | 6
2B.C5 | Surge arrester 36 kV, 30 kV continuous operating voltage, 10 kA nominal discharge current, 50 Hz, single phase, gapless, metal oxide type for all five (05) substations |  | No. | 6
2B.C6 | DS with load break fuse (10A) etc. for Connection between 36kV busbar & 02 sets of 33/0.415kV Earthing/Auxiliary transformer. |  | Set | 2
2B.C7 | Gantry steel structures for Bus & Equipment, Conductor for 36kV,3000A Bus bar, Insulator and fittings including all necessary clamps and connectors required to complete 33kV switchyard
| i. | Flexible conductor for Bus & Equipment connection | Lot | 1
| ii. | Insulators and fittings incl. all necessary clamps and connectors,Nut-Bolt required for completing 33 kV switchyard | Lot | 1
| iii. | Gantry steel structures for Bus
| a) | Beam | No | 4
| b) | Column | No | 6
| iv. | Gantry steel structures for Transformer
| a) | Beam | No | 2
| b) | Column | No | 3
| v. | steel structures for equipment supports required for completing 33 kV switchgear
| a) | CB,DS; CT,PT & LA ( 3 No.s= 1set) | set | 11
| vi. | XLPE Cable | Deleted
| vii. | Cable Sealing End | Deleted
| viii. | Cable trench | Lot | 1
2B.D | Transformers
2B.D1 |  | Deleted
2B.D2 |  | Three phase outdoor type two-winding power transformer, 132/34.5kV, 80/120MVA (ONAN/ONAF) | Set | 2
2B.D3 |  | On-line Dissolved Gas monitoring system for 230/138/33kV auto transformers | Deleted
2B.D4 |  | Earthing / Auxiliary Power Transformer 33/0.415 kV, three phase 250 kVA, Dyn11, ONAN , associated outdoor neutral CTs and steel support structures including all necessary connections. | Set | 2
2B.D5 |  | Complete Fire Fighting system for GIS Hall & Control Room
| i) | 230kV GIS Hall | Deleted
| ii) | 132kV GIS Hall | Lot | 1
| iii) | Panel & Control Room | Lot | 1
2B.D6 |  | Transformer Fire-Fighting system (water Spray type) for three phase outdoor type power transformer | Deleted
2B.E | Control, Protection, SAS and Metering
245kV Circuits
Deleted
145kV Circuits
2B.E1 |  | Control, Protection,monitoring & SAS function for overhead line circuits | set | 6
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main & Backup) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2B.E2 |  | Control, Protection,monitoring & SAS function for Auto transformer circuits | set | 2
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main & Backup) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2B.E3 |  | Control, Protection,monitoring & SAS function for Bus Coupler circuits | set | 1
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay | set | 1
| c) | Auxiliary relay (TCS, Lockout etc.)
| d) | Protecttion Panel including wiring, lighting,heater, humidity sensor & other accessories | set | 1
2B.E3 |  | Busbar Protection | set | 1
Each Comprising
| a) | Control panel with all accessories including monitoring | set | 1
| b) | Protection main relay
| i. | Bay unit with HMI | set | 5
| ii. | Central unit with HMI | set | 1
| c) | Selector Switch for Enabling/Disabling BBP,BFP, all function | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2B.E4 |  | Tariff metering
| a) | Meters (Main & Check) | No. | 16
| b) | Panel including wiring, lighting,heater & other accessories | lot | 1
36kV Circuit
2B.E5 |  | Control, Monitoring, Protection & SAS for 33kV station power system | set | 2
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | set | 1
| b) | Protection main relay (67,67N,50,50N,51,51N etc) | Set | 1
| c) | Auxiliary relays (TCS, Lockout etc) | Set | 1
| d) | Protecttion Panel including wiring, lighting,heater, humidity sensor & other accessories | set | 1
2B.E6 |  | Tariff metering
| a) | Meters (Main & Check) | No. | 4
| b) | Panel including wiring, lighting,heater, humidity sensor & other accessories | lot | 1
2B.E7 |  | Substation Automation system
| i. | BCU
| a) | for 245kV Circuits | No. | NA
| b) | for 145kV Circuits | No. | 9
| c) | 33kV Circuits | No. | 2
| ii. | Industrial Server PC ( Intel XEON Silver- 4116 processor, ECC memory) cum Operator workstation with SAS & Enginering Software | Set | 2
| iii. | Ethernet Switch for SAS | Lot | 1
| iv. | GPS system | Set | 1
| v. | Common alarm unit with hooter/buzzer for annunciation | Set | 2
| vi. | LCD Monitor, 55" or Large | Set | 1
| vii. | Printer, A4 Laser (One black & White, Other Color) | Set | 2
| viii. | Engineering PC: core i7-9800X series processor, 1TB HDD, 8GB RAM, 22'' display for SAS & SCADA | No. | 1
| ix. | Cable (Fiber Optic, Ethernet, Copper etc.)
| x. | Panel including wiring, lighting,heater & other accessories | Lot | 1
| xi. | Other Accessories (if any) | Lot | 1
2B.F | SCADA system for Telecontrol and Telemetering
| a) | Equipment at Substation
| i. | Gateway (server, engineering software) | Set | 2
| ii. | Ethernet Switch | Set | 2
| iii. | Hardware Firewall | Set | 1
| iv. | Additional 33kV Feeder BCU | set | 5
| v. | Panel including wiring, lighting,heater, humidity sensor & other accessories | lot | 1
| vi. | Cables | lot | 1
| vii. | Other Accessories (if any) | lot | 1
| b) | Integration work with Master & Backup NLDC including Engineering & Commissioning | lot | 1
2B.G | Digital Fault & Disturbance Recorder
Deleted
2B.H |  | GIL & Power Cable
Deleted
2B.I |  | Multicore Cables
Multicore Cables for control, protection, metering & power circuits
| i. | _LV Control Cable | lot | 1
| ii. | _LV Power Cable | lot | 1
2B.J |  | Earthing and Lightning Protection system and Portable Eathing Equipment
2B.J1 |  | Earthing and Lightning Protection system
| i. | _Earthing system for complete substation | lot | 1
| ii. | _Lighting Protection System for complete substation | lot | 1
2B.J2 |  | Portable(maintenance) earthing equipment device | set | 1
2B.K |  | Batteries, chargers & DC distribution
2B.K1 |  | 110V Ni-cad Batteries with chargers & distribution board (including 2 sets 4kVA UPS, 30 mins) | lot | 1
| i. | _110V Battery Banks, 500Ah | set | 2
| ii. | _Charger 170A | set | 2
| iii. | _5kVA Inverter | set | 1
| iv. | _110V DC Distribution panel, MCC type | lot | 1
2B.K2 |  | 48V Ni-cad Batteries with chargers & distribution board
| i. | _48V battery Banks,150Ah | set | 2
| ii. | _Charger, 70A | set | 2
| iii. | _48V DC Disatribution Panel | lot | 1
2B.L | LVAC Distribution
2B.L1 | _AC 415V or 240V distribution panels (MCC type) |  | lot | 1
2B.L2 | _Tariff metering at LV side(Main & Check) |  | No. | 4
2B.M | Civil Works, Building and Foundation
2B.M1 | Complete civil items required for outdoor works including boundary wall and slope protection
| a) | Complete Compacted Land development with carried/dredged earthfilling | CuM | 80950
| b) | Slope Protection | sqm | 5100
| c) | Complete outdoor civil works
| i) | _Outdoor gantry foundation 230kV switchyard | Deleted
| ii) | _Outdoor equipment foundation 230kV switchyard | Deleted
| iii) | _132kV Indoor GIS Foundation | Deleted
| iii) | _Outdoor gantry foundation 132kV switchyard | nos. | 9
| iv) | _Outdoor equipment foundation 132kV switchyard
| a) | LA | nos. | 24
| v) | _Outdoor equipment foundation 33kV switchyard
| a) | CB | set | 2
| b) | DS | set | 4
| c) | CT | set | 2
| d) | IVT | set | 2
| e) | LA | set | 2
| vi) | _Outdoor gantry/tubular busbar foundation 33kV switchyard | No | 9
| vii) | _Transformer foundation including oilpit & carrage way | nos. | 2
| viii) | _Blast wall | nos. | 3
| ix) | Property line Demarkation | rm | 600
| x) | _Security Boundary Wall without retaining wall | m | 600
| xi) | _Substation Main gate | No | 1
| xii) | _Chainlink Fencing | Deleted
| xiii) | _Approach raod 6m width | m | 20
| xiv) | Box Culvert | lot | 1
| xv) | _Internal road | lot | 1
| xvi) | _Surface drain | m | 600
| xvii) | _Cable Trench | lot | 1
| xviii) | _Switchyard surface finishing with drainage system | lot | 1
| xix) | _Gravel laying | lot | 1
| xx) | _Septic tank, sowak way | lot | 1
| xxi) | _Pump house including deep tubewell, motor, pump, water reservoir, water pipe line etc. | lot | 1
| xxii) | _Gurd house | No | 1
| xxiii) | sentry post, | No | 4
| xxiv) | car port | No | 1
2B.M2 | Complete civil works for one no's three storied 132kV GIS & Operation Room
| i) | _Foundation works | Lot | 1
| ii) | _Super structures | Lot | 1
| iii) | _All finish works | Lot | 1
| iv) | _10 ton EOT Crane | No. | 1
| v) | 6 person lift | No | 1
2B.M3 | Testing of Foundation |  | No. | 1
| i) | Compression test of pile | Nos | 2
| ii) | Uplift test of pile | Nos | 1
2B.M4 | Fire Fighting system for GIS Hall & Control Room
| i) | Fire Fighting system For GIS Room | Lot | 1
| ii) | Fire Fighting system For Operation & Panel Room | Lot | 1
2B.M5 | Complete Water spray system for transformers fire-fighting including reservoir, pipe network and pump etc. |  | Set | 2
2B.M6 | Preservation of top soil before filling and re-spread of preserved soil after filling |  | sqm | 10120 | [5 empty] | 1017.14
2B.M7 | Laboratory test (Pb, Cd, Cr, Zn, Mn, As, Hg) of fill material for ensuring suitable material (non-contaminated). Once before filling |  | lot | 1
2B.M8 | Ensuring fencing, fire safety and occupational health safety during construction |  | lot | 1
2B.N | Lighting, small power, air conditioning and Ventilation
2B.N1 | Indoor Lighting (LED type), small power, air conditioning and Ventilation and emergency DC lighting for control building and local control houses |  | lot | 1
2B.N2 | Lighting (LED type) for ouside building area for security, roadway, switchyard and emergency DC lighting |  | lot | 1
2B.N3 | Complete solar system (1kW solar panel) including 12V VRLA maintenace free battery and other accessories for Substation emergency DC Lighting |  | lot | 1
2B.O | Fibre Optic Multiplexer Equipment for Communication and Protection
2B.O1 | Indoor Fibre Optic Multipexer Equipment |  | lot | 1
2B.O2 | PABX card & telephone set |  | lot | 1
2B.O3 | Under ground optical fiber cable, armoured, 48/24 core including Outdoor termination box,indoor MDF & pigtail cables |  | lot | 1
2B.O4 | PDH & SDH and 48/24 Core ODF with necessary connection work and testing shall be installed. |  | lot | 1
Total Price ( for New Muradnagar 132/33kV SS) carried to Summary of Price Schedule
Total Price in words ( for New Muradnagar 132/33kV SS)............................................................................................................................................................................
New 132/33 kV Substation at Chandina
Item No. | Description of Equipment Requirement |  | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
[5 empty] | Unit Price | Total Price | Unit Price | Total Price
[7 empty] | EXW | EXW
|  |  |  | (1) | (2) | (3) = (1) x (2) | (4) | (5)=(1)x(4)
2C.A | 230 kV switchgear, equipment connection and steel structures
Deleted
2C.B | 145 kV Indoor Type Gas Insulated Switchgear (GIS), equipment connection and steel structures
2C.B1 | 145kV GIS Line Feeder Bays
| c) | For Chandina SS | set | 2
Each Line bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1600A, 40kA/3s, three phase, single pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1600A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | set | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1600A, 40kA/3s three phase line disconnector integral with high speed earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer | No. | 3
| vii. | 145kV single phase voltage transformer 2 core, Class 0.2 for Metering and Class 3P for Protection | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Cubicle | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2C.B2 | 145kV GIS Transformer Feeder Bays:
| c) | For Chandina SS | set | 2
Each transformer bay shall comprise of the following equipment:
| i. | 145kV,2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1600A, 40kA/3s, three phase, Gang pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1600A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1600A, 40kA/3s three phase line side disconnector integral with earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer | No. | 3
| vii. | 145kV single phase voltage transformer 2core, Class 0.2 for Metering and Class 3P for Protection | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Cubicle | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2C.B3 | 145kV Bus Coupler Bays :
| c) | For Chandina SS | set | 1
Each Bus Coupler Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase double busbar | lot | 1
| ii. | 145kV, 2500A, 40kA/3s, three phase, Gang pole operation circuit breaker complete with spring-stored energy operating mechanism | No. | 1
| iii. | 145kV, 2500A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Sets | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism, on either side of circuit breaker. | sets | 2
| v. | 145kV, 40kA/3s, single phase, 2-core, current transformer with cores as follows: | No. | 3
| vi. | 145kV, 2500A, 40kA/3s, single phase, 3-core, current transformers with cores as follows: | No. | 3
| vii. | Local Control Cubicle | set | 1
| viii. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2C.B4 | 145kV GIS Double Busbar with VT/ES :
| c) | For Chandina SS | Set | 1
Each GIS Double Busbar with VT/ES Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 450kA/3s, three phase double busbars | Lot | 1
| ii. | 145kV single phase, 2 cores voltage transformer | No. | 6
| iii. | 145kV, 40kA/3s, three phase, three position earth switches complete with motor operating Mechanism | Sets | 2
| iv. | Local Control Panel | Set | 1
2C.B5 | 120kV rated voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase surge arresters
| c) | For Chandina SS | No. | 12
2C.B6 | Rigid tubular bus and/or stranded conductors including accessories for each connection as required for completing 145kV GIS Switchyard for all five (05) substations
| i. | Tubular Conductor | Lot | 1
| ii | Flexible Conductor | Lot | 1
2C.B7 | insulator and fittings including all necessary clamps and connectors as required for completing 145kV GIS Switchyard for all five (05) substations
| i | _Insulator | Lot | 1
| ii | Fittings & Clamps_Connector | Lot | 1
| ii | Nut-bolt | Lot | 1
| iv. | _Cable trench including fitting, fixing accessories | Lot | 1
2C.B8 | Steel gantry, having double tier for each double circuit of 145kV Transmission Line including all necessary accessories required for completing 145kV GIS Switchyard
| a) | Steel Structure
| i. | _Gantry Column | No. | 4
| ii. | Beam | No. | 4
| iii. | Nut & Bolts | Lot | 1
| b) | Equipment Structure
| i. | LA | No. | 12
2C.C 33 kV Switchgear, equipment connection and steel structures
One (1) set of complete equipment for switchgear 33 kV shall be designed, supplied, delivered, installed, tested and commissioned, under this contract, comprise the following:
2C.C1 | Circuit Breaker 36 kV, 2500 A, 31.5kA/1s, 50 Hz, 170/70 kV BIL, three pole, vacuum type, for outdoor installation with one spring-stored energy operating mechanism |  | Set | 2
2C.C2 | Disconnector 36 kV, 2500 A, 31.5 kA/1s, 50 Hz, 170/70 kV BIL, three pole, single vertical break, post type, motor operated
| i) | DS without ES | set | 2
| ii) | DS with ES | set | 2
2C.C3 | Current transformer 36 kV, 31.5 kA/1s, 50Hz, 170/70 kV BIL, single phase, 2500/1 , 3-core, post type with double secondary box |  | nos. | 6
2C.C4 | Voltage transformer 36kV, 50Hz, 170/70 kV BIL, single phase, 33/V3 / 0.110/V3 / 0.110/V3 kV, 3 secondary windings, inductive type with double secondary box |  | No. | 6
2C.C5 | Surge arrester 36 kV, 30 kV continuous operating voltage, 10 kA nominal discharge current, 50 Hz, single phase, gapless, metal oxide type for all five (05) substations |  | No. | 6
2C.C6 | DS with load break fuse (10A) etc. for Connection between 36kV busbar & 02 sets of 33/0.415kV Earthing/Auxiliary transformer. |  | Set | 2
2C.C7 | Gantry steel structures for Bus & Equipment, Conductor for 36kV,3000A Bus bar, Insulator and fittings including all necessary clamps and connectors required to complete 33kV switchyard
| i. | Flexible conductor for Bus & Equipment connection | Lot | 1
| ii. | Insulators and fittings incl. all necessary clamps and connectors,Nut-Bolt required for completing 33 kV switchyard | Lot | 1
| iii. | Gantry steel structures for Bus
| a) | Beam | No | 4
| b) | Column | No | 6
| iv. | Gantry steel structures for Transformer
| a) | Beam | No | 2
| b) | Column | No | 3
| v. | steel structures for equipment supports required for completing 33 kV switchgear
| a) | CB,DS; CT,PT & LA ( 3 No.s= 1set) | set | 11
| vi. | XLPE Cable | Deleted
| vii. | Cable Sealing End | Deleted
| viii. | Cable trench | Lot | 1
2C.D | Transformers
2C.D1 |  | Deleted
2C.D2 |  | Three phase outdoor type two-winding power transformer, 132/36kV, 80/120MVA (ONAN/ONAF) | Set | 2
2C.D3 |  | On-line Dissolved Gas monitoring system for 230/138/33kV auto transformers | Deleted
2C.D4 |  | Earthing / Auxiliary Power Transformer 33/0.415 kV, three phase 250 kVA, Dyn11, ONAN , associated outdoor neutral CTs and steel support structures including all necessary connections. | Set | 2
2C.D5 |  | Complete Fire Fighting system for GIS Hall & Control Room
| i) | 230kV GIS Hall | Deleted
| ii) | 132kV GIS Hall | Lot | 1
| iii) | Panel & Control Room | Lot | 1
2C.D6 |  | Transformer Fire-Fighting system (water Spray type) for three phase outdoor type power transformer | Deleted
2C.E | Control, Protection, SAS and Metering
245kV Circuits
Deleted
145kV Circuits
2C.E1 |  | Control, Protection,monitoring & SAS function for overhead line circuits | set | 2
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main & Backup) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2C.E2 |  | Control, Protection,monitoring & SAS function for Power transformer circuits | set | 2
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main & Backup) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2C.E3 |  | Control, Protection,monitoring & SAS function for Bus Coupler circuits | set | 1
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay | set | 1
| c) | Auxiliary relays (TCS, Lockout etc) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2C.E3 |  | Busbar Protection | set | 1
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | NA
| b) | Protection main relay | set | 1
| i. | Bay unit with HMI | set | 5
| ii. | Central unit with HMI | set | 1
| c) | Selector Switch for Enabling/Disabling BBP,BFP, all function | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2C.E4 |  | Tariff metering | lot | 1
| a) | Meters | lot | 1
| b) | Panel including wiring, lighting,heater, HUMIDITY SENSOR & other accessories | lot | 1
36kV Circuit
2C.E5 |  | Control, Monitoring, Protection & SAS for 33kV station power system | Set | 2
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | Set | 1
| b) | Protection main relay (67,67N,50,50N,51,51N etc) | Set | 1
| c) | Auxiliary relays (TCS, Lockout etc) | Set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | Set | 1
2C.E6 |  | Tariff metering
| a) | Meters (Main & Check) | No. | 4
| b) | Panel including wiring, lighting,heater & other accessories | lot | 1
2C.E7 | Substation Automation system
| i. | BCU
| a) | for 245kV Circuits | No. | NA
| b) | for 145kV Circuits | No. | 3
| c) | 33kV Circuits | No. | 2
| ii. | Industrial Server PC ( Intel XEON Silver- 4116 processor, ECC memory) cum Operator workstation with SAS & Enginering Software | Set | 2
| iii. | Ethernet Switch for SAS | Lot | 1
| iv. | GPS system | Set | 1
| v. | Common alarm unit with hooter/buzzer for annunciation | Set | 2
| vi. | LCD Monitor, 55" or Large | Set | 1
| vii. | Printer, A4 Laser (One black & White, Other Color) | Set | 2
| viii. | Engineering PC: core i7-9800X series processor, 1TB HDD, 16GB RAM, 22'' display for SAS & SCADA | No. | 1
| ix. | Cable (Fiber Optic, Ethernet, Copper etc.)
| x. | Panel including wiring, lighting,heater & other accessories | Lot | 1
| xi. | Other Accessories (if any) | Lot | 1
2C.F | SCADA system for Telecontrol and Telemetering
| a) | Equipment at Substation
| i. | Gateway (server, engineering software) | Set | 2
| ii. | Ethernet Switch | Set | 2
| iii. | Hardware Firewall | Set | 1
| iv. | Additional 33kV Feeder BCU | set | 5
| v. | Panel including wiring, lighting,heater & other accessories | lot | 1
| vi. | Cables | lot | 1
| vii. | Other Accessories (if any) | lot | 1
| b) | Integration work with Master & Backup NLDC including Engineering & Commissioning | lot | 1
2C.G | Digital Fault & Disturbance Recorder
Deleted
2C.H |  | GIL & Power Cable
Deleted
2C.I |  | Multicore Cables
Multicore Cables for control, protection, metering & power circuits
| i. | _LV Control Cable | lot | 1
| ii. | _LV Power Cable | lot | 1
2C.J |  | Earthing and Lightning Protection system and Portable Eathing Equipment
2C.J1 |  | Earthing and Lightning Protection system
| i. | _Earthing system for complete substation | lot | 1
| ii. | _Lighting Protection System for complete substation | lot | 1
2C.J2 |  | Portable(maintenance) earthing equipment device | set | 1
2C.K |  | Batteries, chargers & DC distribution
2C.K1 |  | 110V Ni-cad Batteries with chargers & distribution board (including 2 sets 4kVA Inverter) | lot | 1
| i. | _110V Battery Banks, 500Ah | set | 2
| ii. | _Charger 170A | set | 2
| iii. | _4kVA Inverter | set | 1
| iv. | _110V DC Distribution panel, MCC type | lot | 1
2C.K2 |  | 48V Ni-cad Batteries with chargers & distribution board
| i. | _48V battery Banks,150Ah | set | 2
| ii. | _Charger, 70A | set | 2
| iii. | _48V DC Disatribution Panel | lot | 1
2C.L | LVAC Distribution
2C.L1 | _AC 415V or 240V distribution panels (MCC type) |  | lot | 1
2C.L2 | _Tariff metering at LV side(Main & Check) |  | No. | 4
2C.M | Civil Works, Building and Foundation
2C.M1 | Complete civil items required for outdoor works including boundary wall and slope protection
| a) | Complete Compacted Land development with carried/dredged earthfilling | CuM | 32400
| b) | Slope protection | sqm | 3250
| c) | Complete outdoor civil works
| i) | _Outdoor gantry foundation 230kV switchyard | Deleted
| ii) | _Outdoor equipment foundation 230kV switchyard | Deleted
| iii) | _132kV Indoor GIS Foundation | Deleted
| iii) | _Outdoor gantry foundation 132kV switchyard | nos. | 4
| iv) | _Outdoor equipment foundation 132kV switchyard
| a) | LA | nos. | 12
| v) | _Outdoor equipment foundation 33kV switchyard
| a) | CB | set | 2
| b) | DS | set | 4
| c) | CT | set | 2
| d) | IVT | set | 2
| e) | LA | set | 2
| vi) | _Outdoor gantry/tubular busbar foundation 33kV switchyard | No. | 9
| vii) | _Transformer foundation including oilpit & carrage way | nos. | 2
| viii) | _Blast wall | nos. | 3
| ix) | Property Line Demarkation | rm | 400
| x) | _Security Boundary Wall with retaining wall | m | 400
| xi) | _Substation Main gate | lot | 1
| xii) | _Chainlink Fencing | Deleted
| xiii) | _Approach raod 6m width | m | 20
| xiv) | Box Culvert | lot | 1
| xv) | _Internal road | lot | 1
| xvi) | _Surface drain | m | 400
| xvii) | _Cable Trench | lot | 1
| xviii) | _Switchyard surface finishing | lot | 1
| xix) | _Gravel laying | lot | 1
| xx) | _Septic tank, sowak way | lot | 1
| xxi) | _Pump house including deep tubewell, motor, pump, water reservoir, water pipe line etc. | lot | 1
| xxii) | _Gurd house | lot | 1
| xxiii) | sentry post, | lot | 1
| xxiv) | car port | lot | 1
2C.M2 | Complete civil works for Operation & Panel Room
Complete civil works for one no's three storied 132kV GIS & Operation Room
| i) | _Foundation works | Lot | 1
| ii) | _Super structures | Lot | 1
| iii) | _All finish works | Lot | 1
| iv) | _10 ton EOT Crane | No. | 1
| v) | 6 person lift | No. | 1
2C.M3 |  | Testing of Foundation
| i) | Compression test of pile | No. | 2
| ii) | Uplift test of pile | No. | 2
2C.M4 | Fire Fighting system for GIS Hall & Control Room
| i) | Fire Fighting system For GIS Room | Lot | 1
| ii) | Fire Fighting system For Operation & Panel Room | Lot | 1
2C.M5 | Complete Water spray system for transformers fire-fighting including reservoir, pipe network and pump etc. |  | Deleted
2C.M6 | Preservation of top soil before filling and re-spread of preserved soil after filling |  | sqm | 4050
2C.M7 | Laboratory test (Pb, Cd, Cr, Zn, Mn, As, Hg) of fill material for ensuring suitable material (non-contaminated). Once before filling |  | lot | 1
2C.M8 | Ensuring fencing, fire safety and occupational health safety during construction |  | lot | 1
2C.N | Lighting, small power, air conditioning and Ventilation
2C.N1 | Indoor Lighting (LED type), small power, air conditioning and Ventilation and emergency DC lighting for control building and local control houses |  | lot | 1
2C.N2 | Lighting (LED type) for ouside building area for security, roadway, switchyard and emergency DC lighting |  | lot | 1
2C.N3 | Complete solar system (1kW solar panel) including 12V VRLA maintenace free battery and other accessories for Substation emergency DC Lighting |  | Set | 1
2C.O | Fibre Optic Multiplexer Equipment for Communication and Protection
2C.O1 | Indoor Fibre Optic Multipexer Equipment |  | lot | 1
2C.O2 | PABX Card & telephone set |  | lot | 1
2C.O3 | Under ground optical fiber cable, armoured, 48/24 core including Outdoor termination box,indoor MDF & pigtail cables |  | lot | 1
2C.O4 | PDH & SDH and 48/24 Core ODF with necessary connection work and testing shall be installed. |  | lot | 1
Total Price ( for New Chandina 132/33kV SS) carried to Summary of Price Schedule
Total Price in words ( for New Chandina 132/33kV SS)............................................................................................................................................................................
New 132/33 kV Substation at Laxmipur
Item No. | Description of Equipment Requirement |  | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
[5 empty] | Unit Price | Total Price | Unit Price | Total Price
[7 empty] | EXW | EXW
|  |  |  | (1) | (2) | (3) = (1) x (2) | (4) | (5)=(1)x(4)
2D.A | 230 kV switchgear, equipment connection and steel structures
Deleted
2D.B | 145 kV Indoor Type Gas Insulated Switchgear (GIS), equipment connection and steel structures
2D.B1 | 145kV GIS Line Feeder Bays
| d) | For Laxmipur SS | set | 2
Each Line bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1600A, 40kA/3s, three phase, single pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1600A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1600A, 40kA/3s three phase line disconnector integral with high speed earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer with cores as follows | No. | 3
| vii. | 145kV single phase voltage transformer 2core, Class 0.2,5VA for Metering and Class 3P,10VA for Protection | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Panel | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2D.B2 | 145kV GIS Transformer Feeder Bays:
| d) | For Laxmipur SS | Set | 2
Each Line bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1600A, 40kA/3s, three phase, Gang pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1600A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1600A, 40kA/3s three phase line disconnector integral with earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer with cores as follows | No. | 3
| vii. | 145kV single phase voltage transformer 3 core, Class 0.2 for Metering and Class 3P for Protection | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Panel | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2D.B3 | 145kV Bus Coupler Bays :
| d) | For Laxmipur SS | set | 1
Each Bus Coupler Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase double busbar | lot | 1
| ii. | 145kV, 2500A, 40kA/3s, three phase, Gang pole operation circuit breaker complete with spring-stored energy operating mechanism | No. | 1
| iii. | 145kV, 2500A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Sets | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism, on either side of circuit breaker. | sets | 2
| v. | 145kV, 40kA/3s, single phase, 2-core, current transformer with cores as follows: | No. | 3
| vi. | 145kV, 2500A, 40kA/3s, single phase, 2-core, current transformers with cores as follows: | No. | 3
| vii. | Local Control Panel | set | 1
| viii. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2D.B4 | 145kV GIS Double Busbar with VT/ES :
| d) | For Laxmipur SS | Set | 1
Each GIS Double Busbar with VT/ES Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase double busbars | Lot | 1
| ii. | 145kV single phase, 2 core, voltage transformer | No. | 6
| iii. | 145kV, 40kA/3s, three phase, three position earth switches complete with motor operating Mechanism | Sets | 2
| iv. | Local Control Panel | Set | 1
2D.B5 | 120kV rated voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase surge arresters
| d) | For Laxmipur SS | No. | 12
2D.B6 | Rigid tubular bus and/or stranded conductors including accessories for each connection as required for completing 145kV GIS Switchyard for all five (05) substations
| i. | Tubular Conductor | Lot | 1
| ii | Flexible Conductor | Lot | 1
2D.B7 | Insulator and fittings including all necessary clamps and connectors as required for completing 145kV GIS Switchyard
| i | _Insulator | Lot | 1
| ii | Fittings & Clamps_Connector | Lot | 1
| ii | Nut-bolt | Lot | 1
| iv. | _Cable trench including fitting, fixing accessories | Lot | 1
2D.B8 | Steel gantry, having double tier for each double circuit of 145kV Transmission Line including all necessary accessories required for completing 145kV GIS Switchyard
| a) | Steel Structure
| i. | _Gantry Column | No. | 6
| ii. | Beam | No. | 4
| iii. | Nut & Bolts | Lot | 1
| b) | Equipment Structure
| i. | LA | No. | 12
2D.C 33 kV Switchgear, equipment connection and steel structures
One (1) set of complete equipment for switchgear 33 kV shall be designed, supplied, delivered, installed, tested and commissioned, under this contract, comprise the following:
2D.C1 | Circuit Breaker 36 kV, 2500 A, 31.5kA/1s, 50 Hz, 170/70 kV BIL, three pole, vacuum type, for outdoor installation with one spring-stored energy operating mechanism |  | Set | 2
2D.C2 | Disconnector 36 kV, 2500 A, 31.5 kA/1s, 50 Hz, 170/70 kV BIL, three pole, single vertical break, post type, motor operated
| i) | DS without ES | set | 2
| ii) | DS with ES | set | 2
2D.C3 | Current transformer 36 kV, 31.5 kA/1s, 50Hz, 170/70 kV BIL, single phase, 630-1250/1/1 , 2-core, post type |  | nos. | 6
2D.C4 | Voltage transformer 36kV, 50Hz, 170/70 kV BIL, single phase, 33/V3 / 110/V3 / 110/V3 kV/V/V, 2 secondary windings, inductive type |  | No. | 6
2D.C5 | Surge arrester 36 kV, 30 kV continuous operating voltage, 10 kA nominal discharge current, 50 Hz, single phase, gapless, metal oxide type |  | No. | 6
2D.C6 | DS with load break fuse (6A) etc. for Connection between 36kV busbar & 02 sets of 33/0.415kV Earthing/Auxiliary transformer. |  | Set | 2
2D.C7 | Gantry steel structures for Bus & Equipment, Conductor for 36kV,3000A Bus bar, Insulator and fittings including all necessary clamps and connectors required to complete 33kV switchyard
| i. | Flexible conductor for Bus & Equipment connection | Lot | 1
| ii. | Insulators and fittings incl. all necessary clamps and connectors,Nut-Bolt required for completing 33 kV switchyard | Lot | 1
| iii. | Gantry steel structures for Bus
| a) | Beam | No | 4
| b) | Column | No | 6
| iv. | Gantry steel structures for Transformer
| a) | Beam | No | 2
| b) | Column | No | 3
| v. | steel structures for equipment supports required for completing 33 kV switchgear
| a) | CB,DS; CT,PT & LA ( 3 No.s= 1set) | set | 11
| vi. | XLPE Cable | Deleted
| vii. | Cable Sealing End | Deleted
| viii. | Cable trench | Lot | 1
2D.D |  | Transformers
2D.D1 |  | Deleted
2D.D2 |  | Three phase outdoor type two-winding power transformer, 132/36kV, 80/120MVA (ONAN/ONAF) | Set | 2
2D.D3 |  | On-line Dissolved Gas monitoring system for 230/138/33kV auto transformers | Deleted
2D.D4 |  | Earthing / Auxiliary Power Transformer 33/0.415 kV, three phase 250 kVA, Dyn11, ONAN , associated outdoor neutral CTs and steel support structures including all necessary connections. | Set | 2
2D.D5 |  | Complete Fire Fighting system for GIS Hall & Control Room
| i) | 230kV GIS Hall | Deleted
| ii) | 132kV GIS Hall | Lot | 1
| iii) | Panel & Control Room | Lot | 1
2D.D6 |  | Transformer Fire-Fighting system (water Spray type) for three phase outdoor type power transformer | Deleted
2D.E | Control, Protection, SAS and Metering
245kV Circuits
Deleted
145kV Circuits
2D.E1 |  | Control, Protection,monitoring & SAS function for overhead line circuits | set | 2
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main & Backup) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2D.2E2 |  | Control, Protection,monitoring & SAS function for Auto transformer circuits | set | 2
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main & Backup) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2D.E3 |  | Control, Protection,monitoring & SAS function for Bus Coupler circuits | set | 1
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay | set | 1
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2D.E3 |  | Busbar Protection | set | 1
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | NA
| b) | Protection main relay
| i. | Bay Unit | set | 5
| ii. | Central Unit | set | 1
| c) | Selector Switch for Enabling/Disabling BBP,BFP, all function | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2D.E4 |  | Tariff metering | lot | 1
| a) | Meters (Main & Check) | No. | 8
| b) | Panel including wiring, lighting,heater & other accessories | lot | 1
36kV Circuit
2D.E5 |  | Control, Monitoring, Protection & SAS for 33kV station power system | Set | 2
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | set | 1
| b) | Protection main relay (67,67N,50,50N,51,51N etc) | Set | 1
| c) | Auxiliary relays (TCS, Lockout etc) | Set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2D.E6 |  | Tariff metering
| a) | Meters (Main & Check) | No. | 4
| b) | Panel including wiring, lighting,humidity controller, heater & other accessories | Set | 1
2D.E7 | Substation Automation system
| i. | BCU/BCPU
| a) | for 245kV Circuits | No. | NA
| b) | for 145kV Circuits | No. | 5
| c) | 33kV Circuits | No. | 2
| ii. | Industrial Server PC cum Operator workstation with SAS & Enginering Software | Set | 2
| iii. | Ethernet Switch for SAS | Lot | 1
| iv. | GPS system | Set | 1
| v. | Common alarm unit with hooter/buzzer for annunciation | Set | 2
| vi. | LCD Monitor, 55" or Large | Set | 1
| vii. | Printer, A4 Laser (One black & White, Other Color) | Set | 2
| viii. | Engineering PC: core i7, 1TB HDD, 8GB RAM, 22'' display for SAS & SCADA | No. | 1
| ix. | Cable (Fiber Optic, Ethernet, Copper etc.)
| x. | Panel including wiring, lighting,heater & other accessories | Lot | 1
| xi. | Other Accessories (if any) | Lot | 1
2D.F | SCADA system for Telecontrol and Telemetering
| a) | Equipment at Substation
| i. | Gateway (server, engineering software) | Set | 2
| ii. | Ethernet Switch | Set | 2
| iii. | Hardware Firewall | Set | 1
| iv. | Additional 33kV Feeder BCU | set | 5
| v. | Panel including wiring, lighting,heater & other accessories | lot | 1
| vi. | Cables | lot | 1
| vii. | Other Accessories (if any) | lot | 1
| b) | Integration work with Master & Backup NLDC including Engineering & Commissioning | lot | 1
2D.G | Digital Fault & Disturbance Recorder
Deleted
2D.H |  | GIL & Power Cable
Deleted
2D.I |  | Multicore Cables
Multicore Cables for control, protection, metering & power circuits
| i. | _LV Control Cable | lot | 1
| ii. | _LV Power Cable | lot | 1
2D.J |  | Earthing and Lightning Protection system and Portable Eathing Equipment
2D.J1 |  | Earthing and Lightning Protection system
| i. | _Earthing system for complete substation | lot | 1
| ii. | _Lighting Protection System for complete substation | lot | 1
2D.J2 |  | Portable(maintenance) earthing equipment device | set | 1
2D.K |  | Batteries, chargers & DC distribution
2D.K1 |  | 110V Ni-cad Batteries with chargers & distribution board (including 2 sets 4kVA UPS, 30 mins) | lot | 1
| i. | _110V Battery Banks, 350Ah | set | 2
| ii. | _Charger 120A | set | 2
| iii. | _5kVA,30 mins Inverter | set | 1
| iv. | _110V DC Distribution panel, MCC type | lot | 1
2D.K2 |  | 48V Ni-cad Batteries with chargers & distribution board
| i. | _48V battery Banks,125Ah | set | 2
| ii. | _Charger, 50A | set | 2
| iii. | _48V DC Disatribution Panel | lot | 1
2D.L | LVAC Distribution
2D.L1 | _AC 415V or 240V distribution panels (MCC type) |  | lot | 1
2D.L2 | _Tariff metering at LV side(Main & Check) |  | No. | 4
2D.M | Civil Works, Building and Foundation
2D.M1 | Complete civil items required for outdoor works including boundary wall and slope protection
| a) | Complete Compacted Land development with carried/dredged earthfilling | CuM | 80950
| b) | Slope Protection | Sqm | 5100
| c) | Complete outdoor civil works
| i) | _Outdoor gantry foundation 230kV switchyard | Deleted
| ii) | _Outdoor equipment foundation 230kV switchyard | Deleted
| iii) | _132kV Indoor GIS Foundation | Deleted | 5
| iii) | _Outdoor gantry foundation 132kV switchyard | nos. | 6
| iv) | _Outdoor equipment foundation 132kV switchyard
| a) | LA | nos. | 12
| v) | _Outdoor equipment foundation 33kV switchyard
| a) | CB | set | 2
| b) | DS | set | 4
| c) | CT | set | 2
| d) | IVT | set | 2
| e) | LA | set | 2
| vi) | _Outdoor gantry/tubular busbar foundation 33kV switchyard | No. | 9
| vii) | _Transformer foundation including oilpit & carrage way | nos. | 2
| viii) | _Blast wall | nos. | 3
| ix) | Property line Demarkation | rm | 600
| x) | _Security Boundary Wall without retaining wall | m | 600
| xi) | _Substation Main gate | lot | 1
| xii) | _Chainlink Fencing | Deleted
| xiii) | _Approach raod 6m width | m | 20
| xiv) | Box Culvert | lot | 1
| xv) | _Internal road | lot | 1
| xvi) | _Surface drain | m | 600
| xvii) | _Cable Trench | lot | 1
| xviii) | _Switchyard surface finishing with drainage system | lot | 1
| xix) | _Gravel laying | lot | 1
| xx) | _Septic tank, sowak way | lot | 1
| xxi) | _Pump house including deep tubewell, motor, pump, water reservoir, water pipe line etc. | lot | 1
| xxii) | _Gurd house | No. | 1
| xxiii) | sentry post, | No. | 4
| xxiv) | car port | No. | 1
2D.M2 |  | Complete civil works for one no's three storied 132kV GIS & Operation Room
| i) | _Foundation works | Lot | 1
| ii) | _Super structures | Lot | 1
| iii) | _All finish works | Lot | 1
| iv) | _10 ton EOT Crane | No. | 1
| v) | 6 person lift | No | 1
2D.M3 |  | Testing of Foundation
| i) | Compression test of pile | No. | 2
| ii) | Uplift test of pile | No. | 1
2D.M4 | Fire Fighting system for GIS Hall & Control Room
| i) | Fire Fighting system For GIS Room | Lot | 1
| ii) | Fire Fighting system For Operation & Panel Room | Lot | 1
2D.M5 | Complete Water spray system for transformers fire-fighting including reservoir, pipe network and pump etc. |  | Deleted
2D.M6 | Preservation of top soil before filling and re-spread of preserved soil after filling |  | sqm | 10120 | [5 empty] | 10117.14
2D.M7 | Laboratory test (Pb, Cd, Cr, Zn, Mn, As, Hg) of fill material for ensuring suitable material (non-contaminated). Once before filling |  | lot | 1
2D.M8 | Ensuring fencing, fire safety and occupational health safety during construction |  | lot | 1
2D.N | Lighting, small power, air conditioning and Ventilation
2D.N1 | Indoor Lighting (LED type), small power, air conditioning and Ventilation and emergency DC lighting for control building and local control houses |  | lot | 1
2D.N2 | Lighting (LED type) for ouside building area for security, roadway, switchyard and emergency DC lighting |  | lot | 1
2D.N3 | Complete solar system (1kW solar panel) including 12V VRLA maintenace free battery and other accessories for Substation emergency DC Lighting |  | Set | 1
2D.O | Fibre Optic Multiplexer Equipment for Communication and Protection
2D.O1 | Indoor Fibre Optic Multipexer Equipment |  | lot | 1
2D.O2 | PABX Card & telephone set |  | lot | 1
2D.O3 | Under ground optical fiber cable, armoured, 48/24 core including Outdoor termination box,indoor MDF & pigtail cables |  | lot | 1
2D.O4 | PDH & SDH and 48/24 Core ODF with necessary connection work and testing shall be installed. |  | lot | 1
Total Price ( for New Laxmipur 132/33kV SS) carried to Summary of Price Schedule
Total Price in words ( for New Laxmipur 132/33kV SS)............................................................................................................................................................................
New 132/33 kV Substation at Kosba
Item No. | Description of Equipment Requirement |  | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
[5 empty] | Unit Price | Total Price | Unit Price | Total Price
[7 empty] | EXW | EXW
|  |  |  | (1) | (2) | (3) = (1) x (2) | (4) | (5)=(1)x(4)
2E.A | 230 kV switchgear, equipment connection and steel structures
Deleted
2E.B | 145 kV Indoor Type Gas Insulated Switchgear (GIS), equipment connection and steel structures
2E.B1 | 145kV GIS Line Feeder Bays
| e) | For Kosba SS | set | 2
Each Line bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1600A, 40kA/3s, three phase, single pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1600A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1600A, 40kA/3s three phase line disconnector integral with high speed earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer with cores as follows | sets | 3
| vii. | 145kV single phase voltage transformer 2 core, Class 0.2 for Metering and Class 3P for Protection | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Panel | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2E.B2 | 145kV GIS Transformer Feeder Bays:
| e) | For Kosba SS | set | 2
Each transformer bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 145kV, 1600A, 40kA/3s, three phase, Gang pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 145kV, 1600A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 145kV, 1600A, 40kA/3s three phase line disconnector integral with earth switch complete with motor operating mechanism | Set | 1
| vi | 145kV, 40kA/3s single phase, 5-core, current transformer with cores as follows | No. | 3
| vii. | 145kV single phase voltage transformer 2 core, Class 0.2,5VA for Metering and Class 3P,10VA for Protection | No. | 3
| viii. | 145kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Panel | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2E.B3 | 145kV Bus Coupler Bays :
| e) | For Kosba SS | set | 1
Each Bus Coupler Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase double busbar | lot | 1
| ii. | 145kV, 2500A, 40kA/3s, three phase, Gang pole operation circuit breaker complete with spring-stored energy operating mechanism | No. | 1
| iii. | 145kV, 2500A, 40kA/3s, three phase busbar disconnector complete with motor operating mechanism | Sets | 2
| iv. | 145kV, 40kA/3s, three phase, three position earth switch complete with motor operating mechanism, on either side of circuit breaker. | sets | 2
| v. | 145kV, 40kA/3s, single phase, 2-core, current transformer with cores as follows: | No. | 3
| vi. | 145kV, 2500A, 40kA/3s, single phase, 2-core, current transformers with cores as follows: | No. | 3
| vii. | Local Control Panel | set | 1
| viii. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
2E.B4 | 145kV GIS Double Busbar with VT/ES :
| e) | For Kosba SS | Set | 1
Each GIS Double Busbar with VT/ES Bay shall comprise of the following equipment:
| i. | 145kV, 2500A, 40kA/3s, three phase double busbars | Lot | 1
| ii. | 145kV single phase voltage transformer with windings as follows: | No. | 6
| iii. | 145kV, 40kA/3s, three phase, three position earth switches complete with motor operating Mechanism | Sets | 2
| iv. | Local Control Panel | Set | 1
2E.B5 | 120kV rated voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase surge arresters
| e) | For Kosba SS | No. | 12
2E.B6 | Rigid tubular bus and/or stranded conductors including accessories for each connection as required for completing 145kV GIS Switchyard
| i. | Tubular Conductor | Lot | 1
| ii | Flexible Conductor | Lot | 1
2E.B7 | insulator and fittings including all necessary clamps and connectors as required for completing 145kV GIS Switchyard
| i | _Insulator | Lot | 1
| ii | Fittings & Clamps_Connector | Lot | 1
| ii | Nut-bolt | Lot | 1
| iv. | _Cable trench including fitting, fixing accessories | Lot | 1
2E.B8 | Steel gantry, having double tier for each double circuit of 145kV Transmission Line including all necessary accessories required for completing 145kV GIS Switchyard
| a) | Steel Structure
| i. | _Gantry Column | No. | 4
| ii. | Beam | No. | 2
| iii. | Nut & Bolts | Lot | 1
| b) | Equipment Structure
| i. | LA | No. | 12
2E.C 33 kV Switchgear, equipment connection and steel structures
One (1) set of complete equipment for switchgear 33 kV shall be designed, supplied, delivered, installed, tested and commissioned, under this contract, comprise the following:
2E.C1 | Circuit Breaker 36 kV, 2500 A, 31.5kA/1s, 50 Hz, 170/70 kV BIL, three pole, vacuum type, for outdoor installation with one spring-stored energy operating mechanism |  | Set | 2
2E.C2 | Disconnector 36 kV, 2500 A, 31.5 kA/1s, 50 Hz, 170/70 kV BIL, three pole, single vertical break, post type, motor operated
| i) | DS without ES | set | 2
| ii) | DS with ES | set | 2
2E.C3 | Current transformer 36 kV, 31.5 kA/1s, 50Hz, 170/70 kV BIL, single phase, 630-1250/1/1 , 2-core, post type |  | nos. | 6
2E.C4 | Voltage transformer 36kV, 50Hz, 170/70 kV BIL, single phase, 33/V3 / 110/V3 / 110/V3 kV/V/V, 2 secondary windings, inductive type |  | No. | 6
2E.C5 | Surge arrester 36 kV, 30 kV continuous operating voltage, 10 kA nominal discharge current, 50 Hz, single phase, gapless, metal oxide type for all five (05) substations |  | No. | 6
2E.C6 | DS with load break fuse (6A) etc. for Connection between 36kV busbar & 02 sets of 33/0.415kV Earthing/Auxiliary transformer. |  | Set | 2
2E.C7 | Gantry steel structures for Bus & Equipment, Conductor for 36kV,3000A Bus bar, Insulator and fittings including all necessary clamps and connectors required to complete 33kV switchyard
| i. | Flexible conductor for Bus & Equipment connection | Lot | 1
| ii. | Insulators and fittings incl. all necessary clamps and connectors,Nut-Bolt required for completing 33 kV switchyard | Lot | 1
| iii. | Gantry steel structures for Bus
| a) | Beam | No | 4
| b) | Column | No | 6
| iv. | Gantry steel structures for Transformer
| a) | Beam | No | 2
| b) | Column | No | 3
| v. | steel structures for equipment supports required for completing 33 kV switchgear
| a) | CB,DS; CT,PT & LA ( 3 No.s= 1set) | set | 11
| vi. | XLPE Cable | Deleted
| vii. | Cable Sealing End | Deleted
| viii. | Cable trench | Lot | 1
2E.D |  | Transformers
2E.D1 |  | Deleted
2E.D2 |  | Three phase outdoor type two-winding power transformer, 132/36kV, 80/120MVA (ONAN/ONAF) | Set | 2
2E.D3 |  | On-line Dissolved Gas monitoring system for 230/138/33kV auto transformers | Deleted
2E.D4 |  | Earthing / Auxiliary Power Transformer 33/0.415 kV, three phase 250 kVA, Dyn11, ONAN , associated outdoor neutral CTs and steel support structures including all necessary connections. | Set | 2
2E.D5 |  | Complete Fire Fighting system for GIS Hall & Control Room
| i) | 230kV GIS Hall | Deleted
| ii) | 132kV GIS Hall | Lot | 1
| iii) | Panel & Control Room | Lot | 1
2E.D6 |  | Transformer Fire-Fighting system (water Spray type) for three phase outdoor type power transformer | Deleted
2E.E | Control, Protection, SAS and Metering
245kV Circuits
Deleted
145kV Circuits
2E.E1 |  | Control, Protection,monitoring & SAS function for overhead line circuits | set | 2
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main & Backup) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Protecttion Panel including wiring, lighting,heater & other accessories | set | 1
2E2 |  | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 2
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main & Backup) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2E.E3 |  | Control, Protection,monitoring & SAS function for Bus Coupler circuits | set | 1
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay | set | 1
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2E.E3 |  | Busbar Protection | set | 1
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | NA
| b) | Protection main relay
| i. | Bay Unit | set | 5
| ii. | Central Unit | set | 1
| c) | Selector Switch for Enabling/Disabling BBP,BFP, all function | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
2E.E4 |  | Tariff metering
| a) | Meters (Main & Check) | No. | 8
| b) | Panel including wiring, lighting,humidity controller, heater & other accessories | lot | 1
36kV Circuit
2E.E5 |  | Control, Monitoring, Protection & SAS for 33kV station power system | Set | 2
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | Set | 1
| b) | Protection main relay (67,67N,50,50N,51,51N etc) | Set | 1
| c) | Auxiliary relays (TCS, Lockout etc) | Set | 1
| d) | Protecttion Panel including wiring, lighting,heater & other accessories | Lot | 1
2E.E6 |  | Tariff metering | lot | 1
| a) | Meters | No. | 4
| b) | Panel including wiring, lighting,heater & other accessories | lot | 1
2E.E7 | Substation Automation system
| i. | BCU/BCPU
| a) | for 245kV Circuits | No. | NA
| b) | for 145kV Circuits | No. | 5
| c) | 33kV Circuits | No. | 2
| ii. | Industrial Server PC cum Operator workstation with SAS & Enginering Software | Set | 2
| iii. | Ethernet Switch for SAS | Lot | 1
| iv. | GPS system | Set | 1
| v. | Common alarm unit with hooter/buzzer for annunciation | Set | 2
| vi. | LCD Monitor, 55" or Large | Set | 1
| vii. | Printer, A4 Laser (One black & White, Other Color) | Set | 2
| viii. | Engineering PC: core i7, 1TB HDD, 8GB RAM, 22'' display for SAS & SCADA | No. | 1
| ix. | Cable (Fiber Optic, Ethernet, Copper etc.)
| x. | Panel including wiring, lighting,heater & other accessories | Lot | 1
| xi. | Other Accessories (if any) | Lot | 1
2E.F | SCADA system for Telecontrol and Telemetering
| a) | Equipment at Substation
| i. | Gateway (server, engineering software) | Set | 2
| ii. | Ethernet Switch | Set | 2
| iii. | Hardware Firewall | Set | 1
| iv. | Additional 33kV Feeder BCU | set | 5
| v. | Panel including wiring, lighting,heater & other accessories | lot | 1
| vi. | Cables | lot | 1
| vii. | Other Accessories (if any) | lot | 1
| b) | Integration work with Master & Backup NLDC including Engineering & Commissioning | lot | 1
2E.G | Digital Fault & Disturbance Recorder
Deleted
2E.H |  | GIL & Power Cable
Deleted
2E.I |  | Multicore Cables
Multicore Cables for control, protection, metering & power circuits
| i. | _LV Control Cable | lot | 1
| ii. | _LV Power Cable | lot | 1
2E.J |  | Earthing and Lightning Protection system and Portable Eathing Equipment
2E.J1 |  | Earthing and Lightning Protection system
| i. | _Earthing system for complete substation | lot | 1
| ii. | _Lighting Protection System for complete substation | lot | 1
2E.J2 |  | Portable(maintenance) earthing equipment device | set | 1
2E.K |  | Batteries, chargers & DC distribution
2E.K1 |  | 110V Ni-cad Batteries with chargers & distribution board (including 2 sets 4kVA UPS, 30 mins) | lot | 1
| i. | _110V Battery Banks, 350Ah | set | 2
| ii. | _Charger 120A | set | 2
| iii. | _5kVA,30 mins Inverter | set | 1
| iv. | _110V DC Distribution panel, MCC type | lot | 1
2E.K2 |  | 48V Ni-cad Batteries with chargers & distribution board
| i. | _48V battery Banks,125Ah | set | 2
| ii. | _Charger, 50A | set | 2
| iii. | _48V DC Disatribution Panel | lot | 1
2E.L | LVAC Distribution
2E.L1 | _AC 415V or 240V distribution panels (MCC type) |  | lot | 1
2E.L2 | _Tariff metering at LV side(Main & Check) |  | No. | 4
2E.M | Civil Works, Building and Foundation
2E.M1 | Complete civil items required for outdoor works including boundary wall and slope protection
| a) | Complete Compacted Land development with carried/dredged earthfilling | CuM | 202400
| b) | Slope Protection | sqm | 12800
| c) | Complete outdoor civil works
| i) | _Outdoor gantry foundation 230kV switchyard | Deleted
| ii) | _Outdoor equipment foundation 230kV switchyard | Deleted
| iii) | _132kV Indoor GIS Foundation | Deleted
| iii) | _Outdoor gantry foundation 132kV switchyard | nos. | 4
| iv) | _Outdoor equipment foundation 132kV switchyard
| a) | LA | nos. | 12
| v) | _Outdoor equipment foundation 33kV switchyard
| a) | CB | set | 2
| b) | DS | set | 4
| c) | CT | set | 2
| d) | IVT | set | 2
| e) | LA | set | 2
| vi) | _Outdoor gantry/tubular busbar foundation 33kV switchyard | No | 9
| vii) | _Transformer foundation including oilpit & carrage way | nos. | 2
| viii) | _Blast wall | nos. | 3
| ix) | _Security Boundary Wall
| a) | Boundary Wall with retaining wall | m | 600
| x) | _Substation Main gate | No. | 1
| xi) | _Chainlink Fencing | Deleted
| xii) | _Approach raod 6m width | m | 20
| xiii) | With Box Culvert | lot | 1
| xiv) | _Internal road | lot | 1
| xv) | _Surface drain | m | 600
| xvi) | _Cable Trench | lot | 1
| xvii) | _Switchyard surface finishing with drainage system | lot | 1
| xviii) | _Gravel laying | lot | 1
| xix) | _Septic tank, sowak way | lot | 1
| xx) | _Pump house including deep tubewell, motor, pump, water reservoir, water pipe line etc. | lot | 1
| xxi) | _Gurd house | No. | 1
| xxii) | sentry post, | No. | 4
| xxiii) | car port | No. | 1
2E.M2 |  | Complete civil works for Operation & Panel Room
Complete civil works for one no's three storied 132kV GIS & Operation Room
| i) | _Foundation works | Lot | 1
| ii) | _Super structures | Lot | 1
| iii) | _All finish works | Lot | 1
| iv) | _10 ton EOT Crane | No. | 1
| v) | 6 person lift | No. | 1
2E.M3 |  | Testing of Foundation
| i) | Compression test of pile | Nos | 2
| ii) | Uplift test of pile | Nos | 1
2E.M4 | Fire Fighting system for GIS Hall & Control Room
| i) | Fire Fighting system For GIS Room | Lot | 1
| ii) | Fire Fighting system For Operation & Panel Room | Lot | 1
2E.M5 | Complete Water spray system for transformers fire-fighting including reservoir, pipe network and pump etc. |  | Deleted
2E.M6 | Preservation of top soil before filling and re-spread of preserved soil after filling |  | sqm | 10120 | [5 empty] | 10117.14
2E.M7 | Laboratory test (Pb, Cd, Cr, Zn, Mn, As, Hg) of fill material for ensuring suitable material (non-contaminated). Once before filling |  | lot | 1
2E.M8 | Ensuring fencing, fire safety and occupational health safety during construction |  | lot | 1
2E.N | Lighting, small power, air conditioning and Ventilation
2E.N1 | Indoor Lighting (LED type), small power, air conditioning and Ventilation and emergency DC lighting for control building and local control houses |  | lot | 1
2E.N2 | Lighting (LED type) for ouside building area for security, roadway, switchyard and emergency DC lighting |  | lot | 1
2E.N3 | Complete solar system (1kW solar panel) including 12V VRLA maintenace free battery and other accessories for Substation emergency DC Lighting |  | Set | 1
2E.O | Fibre Optic Multiplexer Equipment for Communication and Protection
2E.O1 | Indoor Fibre Optic Multipexer Equipment |  | lot | 1
2E.O2 | PABX Card & telephone set |  | lot | 1
2E.O3 | Under ground optical fiber cable, armoured, 48/24 core including Outdoor termination box,indoor MDF & pigtail cables |  | lot | 1
2E.O4 | PDH & SDH and 48/24 Core ODF with necessary connection work and testing shall be installed. |  | lot | 1
Total Price (for New Kosba 132/33kV SS) carried to Summary of Price Schedule
Total Price in words(for New Kosba 132/33kV SS)............................................................................................................................................................................
Extension of 230kV bays at 230/132 kV GIS GAZARIA Substation
Item No. | Description of Equipment Requirement |  | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
[5 empty] | Unit Price | Total Price | Unit Price | Total Price
[7 empty] | EXW | EXW
|  |  |  | (1) | (2) | (3) = (1) x (2) | (4) | (5)=(1)x(4)
3A | 230 kV switchgear, equipment connection and steel structures
3A1 | 245kV GIS Line Feeder Bays, each comprising: |  | Set | 4
| i. | 245kV, 3150A, 50kA/3s, three phase Enclosure double busbar | Lot | 1
| ii. | 245kV, 3150A, 50kA/3s, three phase, single pole operation circuit breaker complete with spring-stored energy operating mechanism | Set | 1
| iii. | 245kV, 3150A, 50kA/3s, three phase busbar disconnector complete with motor operating mechanism | Stes | 2
| iv. | 245kV, 50kA/3s, three phase, three position earth switch complete with motor operating mechanism at both sides of CB | Sets | 2
| v. | 245kV, 3150A, 50kA/3s three phase line disconnector integral with high speed earth switch complete with motor operating mechanism | sets | 1
| vi | 245kV, 3150A, 50kA/3s single phase, 6-core, current transformer with cores as follows: | No. | 3
| vii. | 245kV single phase, 2 core, Class 0.2,5VA for Metering and Class 3P,10VA for Protection, voltage transformer | No. | 3
| viii. | 245kV Gas Insulated Line (GIL) with GIS-to-AIR Bushing, terminating chambers complete with support structure, etc. for incoming line feeder. | Lot | 1
The Length of GIL shall be different for different bay as per actual design
| ix | Local Control Panel | set | 1
| x. | Complete set of miscellaneous items required for safe and efficient operation of the switchgear, terminal arrangements for GIL, busbar end covers or link to adjacent switchgear panel, cables, metal support structure, grounding, etc. as appropriate | Lot | 1
3A2 | 245kV GIS Auto Transformer Feeder Bays, each comprising: |  | Deleted
3A3 | 245kV Bus Coupler Bays , each comprising: |  | Deleted
3A4 | 245kV GIS Double Busbar with VT/ES, each comprising: |  | Deleted
3A5 | 216kV rated voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase surge arresters |  | No. | 12
3A6 | Rigid tubular bus and/or stranded conductors including accessories for each connection as required for completing 230kV GIS Switchyard
| i. | Tubular Conductor | Lot | 1
| ii | Flexible Conductor | Lot | 1
3A7 | Insulator and fittings including all necessary clamps and connectors as required for completing 230kV GIS Switchyard
| i | _Insulator | Lot | 1
| ii | Fittings & Clamps_Connector | Lot | 1
| ii | Nut-bolt | Lot | 1
| iv. | _Cable trench including fitting, fixing accessories | Lot | 1
3A8 | Steel gantry, having double tier for each double circuit of 230kV Transmission Line & Equipment support Structure including all necessary accessories required for completing 230kV GIS Switchyard
| a) | Steel Structure
| i. | _Gantry Column | No. | 5
| ii. | Beam | No. | 4
| iii. | Nut & Bolts | Lot | 1
| b) | Equipment Structure
| i. | LA | No. | 12
| ii. | CVT |  | Deleted
3B | 145 kV Indoor Type Gas Insulated Switchgear (GIS), equipment connection and steel structures
Deleted
3C | 36 kV Switchgear, equipment connection and steel structures
Deleted
3D |  | Transformers
Deleted
3E | Control, Protection, SAS and Metering
245kV Circuits
3E1 |  | Control, Protection,monitoring & SAS Function for overhead line circuits | set | 4
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | set | 1
| b) | Protection main relay (Main-1, Main-2) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
3E2 |  | Deleted
3E3 |  | Deleted
3E4 |  | Extension of Busbar Protection | lot | 1
Each Comprising
| a) | Control Mimic panel with all accessories including monitoring | NA
| b) | Protection main relay ( Bay Unit )
| i) | Central Unit extension card | set | 1
| ii) | Bay Unit with HMI | set | 4
| c) | Selector Switch for Enabling/Disabling BBP,BFP, all function | set | 1
| d) | Protection Panel including wiring, lighting,heater, humidity sensor & other accessories | lot | 1
3E5 |  | Tarif metering
| a) | Meters | No. | 8
| b) | Panel including wiring, lighting,humidity controller, heater & other accessories | lot | 1
145kV Circuits
Deleted
36kV Circuit
Deleted
3E5 | Substation Automation system
| i. | BCU
| a) | for 245kV Circuits | No. | 4
| b) | for 145kV Circuits | No. | Deleted
| c) | 33kV Circuits | No. | Deleted
| ii. | Industrial Server PC cum Operator workstation with SAS & Enginering Software | Set | Deleted
| iii. | Ethernet Switch for SAS | Lot | 1
| iv. | GPS system | Set | Deleted
| v. | Common alarm unit with hooter/buzzer for annunciation | Set | Deleted
| vi. | LCD Monitor, 55" or Large | Set | Deleted
| vii. | Printer, A4 Laser (One black & White, Other Color) | Set | Deleted
| viii. | Engineering PC: core i7, 1TB HDD, 8GB RAM, 22'' display for SAS & SCADA | No. | Deleted
| ix. | Cable (Fiber Optic, Ethernet, Copper etc.) | Lot | 1
| x. | Panel including wiring, lighting,heater & other accessories | Lot | 1
| xi. | Other Accessories (if any) | Lot | 1
3F | Extension of SCADA system for Telecontrol and Telemetering
| a) | Equipment at Substation
| i. | Modification of Gateway (server, engineering software) | Set | 2
| ii. | Ethernet Switch | Set | Deleted
| iii. | Hardware Firewall | Set | Deleted
| iv. | Additional 33kV Feeder BCU | set | Deleted
| v. | Panel including wiring, lighting,heater & other accessories | lot | Deleted
| vi. | Cables | lot | Deleted
| vii. | Other Accessories (if any) | lot | Deleted
| b) | Integration work with Master & Backup NLDC including Engineering & Commissioning | lot | 1
3G | Digital Fault & Disturbance Recorder (Extension)
3G1 | i. | DFDR processor | Set | 1
| ii. | Card for each bay including A/D Converter, Digital & Analog data acquisition system
| a) | for 245kV Circuits | set | 4
| b) | for 145kV Circuits | Deleted
| iii. | Ethernet Switch | Deleted
| iv | GPS system | Deleted
| v. | Panel including wiring, lighting,heater & other accessories | Lot | 1
| vi. | Engineering PC: core i7, 500GB HDD, 8GB RAM, 17'' display | set | Deleted
3H |  | GIL & Power Cable
Deleted
3I |  | Multicore Cables
Multicore Cables for control, protection, metering & power circuits
| i. | _LV Control Cable | lot | 1
| ii. | _LV Power Cable | lot | 1
3J |  | Earthing and Lightning Protection system and Portable Eathing Equipment
3J1 |  | Earthing and Lightning Protection system
| i. | _Extension of Earthing system for bay extension work | lot | 1
| ii. | _Extension of Lighting Protection System for bay extension work | lot | 1
3J2 |  | Portable(maintenance) earthing equipment device | set | 1
3K |  | Batteries, chargers & DC distribution
3K1 |  | 110V Ni-cad Batteries with chargers & distribution board (including 2 sets 4kVA Inverter)
| i. | _110V Battery Banks, 600Ah | Deleted
| ii. | _Charger 600A | Deleted
| iii. | _4kVA Inverter | Deleted
| iv. | _ Extension of 110V DC Distribution panel, MCC type | lot | 1
3K2 |  | 48V Ni-cad Batteries with chargers & distribution board
| i. | _48V battery Banks,150Ah | Deleted
| ii. | _Charger 70A | Deleted
| iii. | _Extension of 48V DC Disatribution Panel | lot | 1
3L | LVAC Distribution
3K1 | _Extension of AC 415V or 240V distribution panels (MCC type) |  | lot | 1
3K2 | _Tariff metering at LV side(Main & Check) |  | Deleted
3M | Civil Works, Building and Foundation
3M1 | Complete civil items required for outdoor works including boundary wall and slope protection
| a) | Complete Land development with carried/dredged earthfilling | Deleted
| b) | Slope Protection | Deleted
| c) | Complete outdoor civil works
| i) | _Outdoor gantry foundation 230kV switchyard | No. | 5
| ii) | _Outdoor equipment foundation 230kV switchyard
| a) | LA | nos. | 12
| iii) | _Indoor equipment foundation 230kV switchyard | Deleted
| iv) | _Internal road | Deleted
| v) | _Cable Trench | lot | 1
| vi) | _Switchyard surface finishing with drainage system | lot | 1
| vii) | _Gravel laying | lot | 1
3M2 |  | complete civil works in existing control building to accommodate the equipment which is in the scope of work | lot | 1
3M3 |  | Deleted
3M4 |  | Deleted
3M5 |  | Deleted
3N | Lighting, small power, air conditioning and Ventilation
3N1 | Indoor Lighting (LED type), small power, air conditioning and Ventilation and emergency DC lighting required for bay extension work for control building and local control houses |  | lot | 1
3N2 | Lighting (LED type) for ouside building required for bay extension work for security, roadway, switchyard and emergency DC lighting |  | lot | 1
3O | Fibre Optic Multiplexer Equipment for Communication and Protection
3O1 | Extension of Indoor Fibre Optic Multipexer Equipment |  | lot | 1
3O2 | PABX Card & telephone set |  | Deleted
3O3 | Under ground optical fiber cable, armoured, 48 core including Outdoor termination box,indoor MDF & pigtail cables |  | lot | 1
3O4 | Extension of PDH & SDH and 48 Core ODF with necessary connection work and testing shall be installed. |  | lot | 1
Total Price (for Extension works at GAZARIA SS) carried to Summary of Price Schedule
Total Price in words (for Extension works at GAZARIA SS)............................................................................................................................................................................
Extension of 132kV AIS bays at 230/132 kV Comilla (North) AIS Substation
Item No. | Description of Equipment Requirement |  | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
[5 empty] | Unit Price | Total Price | Unit Price | Total Price
[7 empty] | EXW | EXW
|  |  |  | (1) | (2) | (3) = (1) x (2) | (4) | (5)=(1)x(4)
4A | 230 kV switchgear, equipment connection and steel structures
Deleted
4B | 145 kV Indoor Type Gas Insulated Switchgear (GIS), equipment connection and steel structures
Deleted
145 kV Indoor Type Air Insulated Switchgear (AIS), equipment connection and steel structures
4B1 | SF6 Circuit breaker,1600A, 40kA/1s,live tank, single pole operating for Line Bay |  | Set | 2
4B2 | Disconnector switch without E/S, 1600A,40kA/1s for Line bay |  | Set | 4
4B3 | Disconnector switch with E/S, 1600A,40kA/1s |  | Set | 2
4B4 | Disconnector switch without E/S, 1600A,40kA/1s |  | Set | 2
4B5 | Single phase current transformer, 5-core,40kA/1s |  | No. | 6
4B6 | Single phase Inductive voltage transformer (IVT), 2-core, 132/√3/0.110/√3:0.110/√3:.110/√3kV |  | No. | 6
4B7 | Single phase surge arrester, 120kV rated,10kA |  | No. | 6
4B8 | Flexible conductorsfor bus and jumper, insulators, fittings including all necessary clamps and connectors for extension work
| i. | _Flexible Conductor for Bus, jumper, equipment connections | Lot | 1
| ii. | _Insulator | Lot | 1
| iii. | _Fittings | Lot | 1
4B9 |  | Steel Structures for gantry and equipment supports required for this extension work
| a) | _Gantry Column including nut & bolts
| i) | For Main Bus | nos. | 2
| ii) | For Jack-Bus | nos. | 2
| b) | _Gantry beam at Main Bus & Jack-Bus height including nut & bolts | nos. | 4
| c) | _Equipment support structures including nut & bolts
| i) | CB | set | 2
| ii) | DS without ES | set | 6
| iii) | DS with ES | set | 2
| iv) | Bus ES | Deleted
| v) | CT | nos. | 6
| vi) | CVT/IVT | nos. | 6
| vii) | LA | nos. | 6
| ix) | PI | Deleted
| d) | _Cable tray including fitting, fixing accessories | lot | 1
4C | 33 kV Switchgear, equipment connection and steel structures
Deleted
4D |  | Transformers
Deleted
4E | Control, Protection, SAS and Metering
245kV Circuits
Deleted
145kV Circuits
4E1 |  | Control, Protection,monitoring & SAS Function for overhead line circuits | set | 2
Each Comprising
| a) | Control panel with Mimic & all accessories including monitoring | set | 1
| b) | Protection main relay (Main & Backup) | set | 2
| c) | Auxiliary relay (TCS, Lockout etc.) | set | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | set | 1
4E2 |  | Deleted
4E3 |  | Deleted
4E4 |  | Extension of Busbar Protection | lot | 1
| a) | Control Mimic panel with all accessories including monitoring | NA
| b) | Protection main relay ( Bay Unit ) | lot | 1
| i) | Central Unit extension card | lot | 1
| ii) | Bay Unit with HMI | lot | 1
| c) | Selector Switch for Enabling/Disabling BBP,BFP, all function | lot | 1
| d) | Complete Protection Panel including wiring, lighting,humidity controller, heater & other accessories | lot | 1
4E5 |  | Tarif metering | lot | 1
| a) | Meters | No. | 4
| b) | Panel including wiring, lighting,heater, humidity sensor & other accessories | lot | 1
36kV Circuit
Deleted
4E6 | Substation Automation system |  | Deleted
4F | SCADA system for Telecontrol and Telemetering |  |  | 1
| a) | Extension of SCADA system including hardwire & software modification in existing RTU/gateway, Supply of IED/transducer, sub-rack with I/O card, CPU, necessary wiring required for MiCOM264 RTU | lot | 1
| b) | Integration work with Master & Backup NLDC including Engineering & Commissioning | lot | 1
4G | Digital Fault & Disturbance Recorder |  | Deleted
4H |  | GIL & Power Cable | Deleted
4I |  | Multicore Cables
Multicore Cables for control, protection, metering & power circuits
| i. | _LV Control Cable | lot | 1
| ii. | _LV Power Cable | lot | 1
4J |  | Earthing and Lightning Protection system and Portable Eathing Equipment
1J1 |  | Earthing and Lightning Protection system
| i. | _Extension of Earthing system for bay extension work | lot | 1
| ii. | _Extension of Lighting Protection System for bay extension work | lot | 1
4J2 |  | Portable(maintenance) earthing equipment device | set | 1
4K |  | Batteries, chargers & DC distribution
4K1 |  | 110V Ni-cad Batteries with chargers & distribution board (including 2 sets 4kVA UPS, 30 mins)
| i. | _110V Battery Banks, 500Ah | Deleted
| ii. | _Charger 170A | Deleted
| iii. | _4kVA Inverter | Deleted
| iv. | _ Extension of 110V DC Distribution panel, MCC type | lot | 1
4K2 |  | 48V Ni-cad Batteries with chargers & distribution board
| i. | _48V battery Banks,150Ah | Deleted
| ii. | _Charger 70A | Deleted
| iii. | _Extension of 48V DC Disatribution Panel | lot | 1
4L | LVAC Distribution
4L1 | _Extension of AC 415V or 240V distribution panels (MCC type) |  | lot | 1
4L2 | _Tariff metering at LV side(Main & Check) |  | Deleted
4M | Civil Works, Building and Foundation
4M1 | Complete civil items required for outdoor works including boundary wall and slope protection
| i) | _Outdoor gantry foundation 230kV switchyard |  | Deleted
| ii) | _Outdoor equipment foundation 230kV switchyard |  | Deleted
| iii) | _230kV Indoor GIS Foundation | Deleted | Deleted
| iii) | _Outdoor gantry foundation 132kV switchyard | nos. | 4
| iv) | _Outdoor equipment foundation 132kV switchyard
| a) | CB | set | 2
| b) | DS without ES | set | 6
| c) | DS with ES | set | 2
| d) | Bus ES | Deleted
| e) | CT | nos. | 6
| f) | CVT/IVT | nos. | 6
| g) | LA | nos. | 6
| v) | _Internal road | lot | 1
| vi) | _Cable Trench | lot | 1
| vii) | _Switchyard surface finishing with drainage system | lot | 1
| viii) | _Gravel laying | lot | 1
4M2 | complete civil works in existing control building to accommodate the equipment which is in the scope of work |  | lot | 1
4M3 | Test of Foundation
| i) | Compression of Pile | Deleted
| ii) | Uplift of Pile | No. | 1
4M4 |  | Deleted
4M5 |  | Deleted
4N | Lighting, small power, air conditioning and Ventilation
4N1 | Indoor Lighting (LED type), small power, air conditioning and Ventilation and emergency DC lighting required for bay extension work for control building and local control houses |  | Deleted
4N2 | Lighting (LED type) for ouside building required for bay extension work for security, roadway, switchyard and emergency DC lighting |  | lot | 1
4O | Fibre Optic Multiplexer Equipment and PLC Equipment for Communication and Protection
4O1 | Extension of Indoor Fibre Optic Multipexer Equipment |  | lot | 1
4O2 | PABX Card & telephone set |  | Deleted
4O3 | Under ground optical fiber cable, armoured, 48 core including Outdoor termination box,indoor MDF & pigtail cables |  | lot | 1
4O4 | Extension of PDH & SDH and 48 Core ODF with necessary connection work and testing shall be installed. |  | lot | 1
Total Price (for Extension works at Comilla(N) SS) carried to Summary of Price Schedule
Total Price in words (for Extension works at Comilla(N) SS)............................................................................................................................................................................

## Schedule B5
Schedule B5: Grand Summary
Total price
|  | Foreign Currency | Local Currency
|  | (in……….) | (in BDT)
New 230/132/33 kV Substation at KACHUA
Schedule No. B1: | Plant & Equipment (including Mandatory Spare Parts) Supplied from Abroad
Schedule No.B2: | Plant & Equipment (including Mandatory Spare Parts) Supplied from within the Employer’s Country
Schedule No. B3: | Design Services
Schedule No. B4: | Installation and Other Services
Schedule No. B7: | EMP Implementation Cost |  | 261000
New 230/132/33 kV Substation at KACHUA
Grand Total
New 132/33 kV Substation at LAKSHAM
Schedule No. B1: | Plant & Equipment (including Mandatory Spare Parts) Supplied from Abroad
Schedule No.B2: | Plant & Equipment (including Mandatory Spare Parts) Supplied from within the Employer’s Country
Schedule No. B3: | Design Services
Schedule No. B4: | Installation and Other Services
Schedule No. B7: | EMP Implementation Cost |  | 261000
New 132/33 kV Substation at LAKSHAM
Grand Total
New 132/33 kV Substation at Muradnagar
Schedule No. B1: | Plant & Equipment (including Mandatory Spare Parts) Supplied from Abroad
Schedule No.B2: | Plant & Equipment (including Mandatory Spare Parts) Supplied from within the Employer’s Country
Schedule No. B3: | Design Services
Schedule No. B4: | Installation and Other Services
Schedule No. B7: | EMP Implementation Cost |  | 261000
New 132/33 kV Substation at Muradnagar
Grand Total
New 132/33 kV Substation at Chandina
Schedule No. B1: | Plant & Equipment (including Mandatory Spare Parts) Supplied from Abroad
Schedule No.B2: | Plant & Equipment (including Mandatory Spare Parts) Supplied from within the Employer’s Country
Schedule No. B3: | Design Services
Schedule No. B4: | Installation and Other Services
Schedule No. B7: | EMP Implementation Cost |  | 261000
New 132/33 kV Substation at Chandina
Grand Total
New 132/33 kV Substation at Laxmipur
Schedule No. B1: | Plant & Equipment (including Mandatory Spare Parts) Supplied from Abroad
Schedule No.B2: | Plant & Equipment (including Mandatory Spare Parts) Supplied from within the Employer’s Country
Schedule No. B3: | Design Services
Schedule No. B4: | Installation and Other Services
Schedule No. B7: | EMP Implementation Cost |  | 261000
New 132/33 kV Substation at Laxmipur
Grand Total
New 132/33 kV Substation at Kosba
Schedule No. B1: | Plant & Equipment (including Mandatory Spare Parts) Supplied from Abroad
Schedule No.B2: | Plant & Equipment (including Mandatory Spare Parts) Supplied from within the Employer’s Country
Schedule No. B3: | Design Services
Schedule No. B4: | Installation and Other Services
Schedule No. B7: | EMP Implementation Cost |  | 261000
New 132/33 kV Substation at Kosba
Subtotal - to Schedule 5 - Grand Total
Extension of 230kV Bays at GAZARIA 230/132 kV GIS Substation
Schedule No. B1: | Plant & Equipment (including Mandatory Spare Parts) Supplied from Abroad
Schedule No.B2: | Plant & Equipment (including Mandatory Spare Parts) Supplied from within the Employer’s Country
Schedule No. B3: | Design Services
Schedule No. B4: | Installation and Other Services
Extension of 230kV Bays at GAZARIA 230/132 kV GIS Substation
Grand Total
Extension of 132kV Bays at existing COMILLA NORTH 230/132 kV AIS Substation
Schedule No. B1: | Plant & Equipment (including Mandatory Spare Parts) Supplied from Abroad
Schedule No.B2: | Plant & Equipment (including Mandatory Spare Parts) Supplied from within the Employer’s Country
Schedule No. B3: | Design Services
Schedule No. B4: | Installation and Other Services
Extension of 132kV Bays at existing COMILLA NORTH 230/132 kV AIS Substation
Grand Total
GRAND GRAND Total

## Schedule B6
Schedule B6: Recommended Spare Parts
No | Description | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
|  |  |  | Unit Price | Total Price | Unit Price | Total Price
|  |  | (1) | (2) | (3)=(1)x(2) | (4) | (5)=(1)x(4)

## Schedule B7
Schedule B7: EMP Implementation Cost
New 230/132/33 kV Substation at KACHUA
Description of item | Qty | Rate | Amount
EM-01 Establishment of labor camp (1 male shed, 1 female shed - 12 ft x 30 ft each) with living arrangement, drinking water facilities, cooking arrangement, mosquito net,, waste bin etc. as per Engineer-in-charge. | 2 | 20000 | 40000
EM-02 Dust suppression measures by water spraying throughout the construction period in and around the subproject site, uncovered aggregates and loose materials such as stockpiles of the sands, excavated earth etc. daily or as per requirements (lump sum) as per Engineer-in-charge. | LS |  | 5000
EM-03 To provide water supply facilities in the camp site ,1nos. of tube well as per Engineer-in-charge. | 1 | 15000 | 15000
EM-04 Sanitation facilities (at the camp site): 2nos. of the toilets preferably portable toilets (1 no. for women and 1nos. for men) as per Engineer-in-charge. | 2 | 15000 | 30000
EM-05 Installation of cautionary sign in term of health and safety signs as required as per Engineer-in-charge. | LS | 16000 | 16000
EM-06 Providing PPEs like hand gloves, spectacles for eye protection, helmets, masks, visible jacket, ear plug, safety boots for at least 30 person (25 for workers and 5 for visitor) and one first aid box with necessary medicine as per Engineer-in-charge. | LS | 20000 | 20000
EM-07 Wastes disposal facility during the construction period; collection, transportation, and providing 4 bin to be provided where 2 for organic and 2 for inorganic waste as per Engineer-in-charge | LS | 20000 | 20000
EM-08 Tree plantation for ecological enhancement work preferably local fruits, flowers, medicinal and ornamental trees- 50 nos. trees (Lum sum) as per Engineer-in-charge | 50 | 400 | 20000
EM-9 Awareness documents (signs/ posters) for effective use of water source and proper waste management, Lum sum basis) as per Engineer-in-charge. | LS | 5000 | 5000
EM-10 Noise level measurement. It can be measured from the preapproved public institute/ university 2 times during construction as per Engineer-in-charge. | LS | 20000 | 20000
EM-11 Air quality (SPM, PM10)) measurement- It can be measured from the pre-approved public institute/ university 2 times during construction as per Engineer-in-charge | LS | 40000 | 40000
EM-12 Water quality water (PH, turbidity, hardness, Cl, TDS, Mn, As, Fe,one for ground water and one for surface TC,FC)- by any recognized laboratory as per Engineer-incharge. | LS | 30000 | 30000
New 132/33 kV Substation at Laksham
Description of item | Qty | Rate | Amount
EM-01 Establishment of labor camp (1 male shed, 1 female shed - 12 ft x 30 ft each) with living arrangement, drinking water facilities, cooking arrangement, mosquito net,, waste bin etc. as per Engineer-in-charge. | 2 | 20000 | 40000
EM-02 Dust suppression measures by water spraying throughout the construction period in and around the subproject site, uncovered aggregates and loose materials such as stockpiles of the sands, excavated earth etc. daily or as per requirements (lump sum) as per Engineer-in-charge. | LS |  | 5000
EM-03 To provide water supply facilities in the camp site ,1nos. of tube well as per Engineer-in-charge. | 1 | 15000 | 15000
EM-04 Sanitation facilities (at the camp site): 2nos. of the toilets preferably portable toilets (1 no. for women and 1nos. for men) as per Engineer-in-charge. | 2 | 15000 | 30000
EM-05 Installation of cautionary sign in term of health and safety signs as required as per Engineer-in-charge. | LS | 16000 | 16000
EM-06 Providing PPEs like hand gloves, spectacles for eye protection, helmets, masks, visible jacket, ear plug, safety boots for at least 30 person (25 for workers and 5 for visitor) and one first aid box with necessary medicine as per Engineer-in-charge. | LS | 20000 | 20000
EM-07 Wastes disposal facility during the construction period; collection, transportation, and providing 4 bin to be provided where 2 for organic and 2 for inorganic waste as per Engineer-in-charge | LS | 20000 | 20000
EM-08 Tree plantation for ecological enhancement work preferably local fruits, flowers, medicinal and ornamental trees- 50 nos. trees (Lum sum) as per Engineer-in-charge | 50 | 400 | 20000
EM-9 Awareness documents (signs/ posters) for effective use of water source and proper waste management, Lum sum basis) as per Engineer-in-charge. | LS | 5000 | 5000
EM-10 Noise level measurement. It can be measured from the preapproved public institute/ university 2 times during construction as per Engineer-in-charge. | LS | 20000 | 20000
EM-11 Air quality (SPM, PM10)) measurement- It can be measured from the pre-approved public institute/ university 2 times during construction as per Engineer-in-charge | LS | 40000 | 40000
EM-12 Water quality water (PH, turbidity, hardness, Cl, TDS, Mn, As, Fe,one for ground water and one for surface TC,FC)- by any recognized laboratory as per Engineer-incharge. | LS | 30000 | 30000
New132/33 kV Substation at Muradnagar
Description of item | Qty | Rate | Amount
EM-01 Establishment of labor camp (1 male shed, 1 female shed - 12 ft x 30 ft each) with living arrangement, drinking water facilities, cooking arrangement, mosquito net,, waste bin etc. as per Engineer-in-charge. | 2 | 20000 | 40000
EM-02 Dust suppression measures by water spraying throughout the construction period in and around the subproject site, uncovered aggregates and loose materials such as stockpiles of the sands, excavated earth etc. daily or as per requirements (lump sum) as per Engineer-in-charge. | LS |  | 5000
EM-03 To provide water supply facilities in the camp site ,1nos. of tube well as per Engineer-in-charge. | 1 | 15000 | 15000
EM-04 Sanitation facilities (at the camp site): 2nos. of the toilets preferably portable toilets (1 no. for women and 1nos. for men) as per Engineer-in-charge. | 2 | 15000 | 30000
EM-05 Installation of cautionary sign in term of health and safety signs as required as per Engineer-in-charge. | LS | 16000 | 16000
EM-06 Providing PPEs like hand gloves, spectacles for eye protection, helmets, masks, visible jacket, ear plug, safety boots for at least 30 person (25 for workers and 5 for visitor) and one first aid box with necessary medicine as per Engineer-in-charge. | LS | 20000 | 20000
EM-07 Wastes disposal facility during the construction period; collection, transportation, and providing 4 bin to be provided where 2 for organic and 2 for inorganic waste as per Engineer-in-charge | LS | 20000 | 20000
EM-08 Tree plantation for ecological enhancement work preferably local fruits, flowers, medicinal and ornamental trees- 50 nos. trees (Lum sum) as per Engineer-in-charge | 50 | 400 | 20000
EM-9 Awareness documents (signs/ posters) for effective use of water source and proper waste management, Lum sum basis) as per Engineer-in-charge. | LS | 5000 | 5000
EM-10 Noise level measurement. It can be measured from the preapproved public institute/ university 2 times during construction as per Engineer-in-charge. | LS | 20000 | 20000
EM-11 Air quality (SPM, PM10)) measurement- It can be measured from the pre-approved public institute/ university 2 times during construction as per Engineer-in-charge | LS | 40000 | 40000
EM-12 Water quality water (PH, turbidity, hardness, Cl, TDS, Mn, As, Fe,one for ground water and one for surface TC,FC)- by any recognized laboratory as per Engineer-incharge. | LS | 30000 | 30000
New 132/33 kV Substation at Chandina
Description of item | Qty | Rate | Amount
EM-01 Establishment of labor camp (1 male shed, 1 female shed - 12 ft x 30 ft each) with living arrangement, drinking water facilities, cooking arrangement, mosquito net,, waste bin etc. as per Engineer-in-charge. | 2 | 20000 | 40000
EM-02 Dust suppression measures by water spraying throughout the construction period in and around the subproject site, uncovered aggregates and loose materials such as stockpiles of the sands, excavated earth etc. daily or as per requirements (lump sum) as per Engineer-in-charge. | LS |  | 5000
EM-03 To provide water supply facilities in the camp site ,1nos. of tube well as per Engineer-in-charge. | 1 | 15000 | 15000
EM-04 Sanitation facilities (at the camp site): 2nos. of the toilets preferably portable toilets (1 no. for women and 1nos. for men) as per Engineer-in-charge. | 2 | 15000 | 30000
EM-05 Installation of cautionary sign in term of health and safety signs as required as per Engineer-in-charge. | LS | 16000 | 16000
EM-06 Providing PPEs like hand gloves, spectacles for eye protection, helmets, masks, visible jacket, ear plug, safety boots for at least 30 person (25 for workers and 5 for visitor) and one first aid box with necessary medicine as per Engineer-in-charge. | LS | 20000 | 20000
EM-07 Wastes disposal facility during the construction period; collection, transportation, and providing 4 bin to be provided where 2 for organic and 2 for inorganic waste as per Engineer-in-charge | LS | 20000 | 20000
EM-08 Tree plantation for ecological enhancement work preferably local fruits, flowers, medicinal and ornamental trees- 50 nos. trees (Lum sum) as per Engineer-in-charge | 50 | 400 | 20000
EM-9 Awareness documents (signs/ posters) for effective use of water source and proper waste management, Lum sum basis) as per Engineer-in-charge. | LS | 5000 | 5000
EM-10 Noise level measurement. It can be measured from the preapproved public institute/ university 2 times during construction as per Engineer-in-charge. | LS | 20000 | 20000
EM-11 Air quality (SPM, PM10)) measurement- It can be measured from the pre-approved public institute/ university 2 times during construction as per Engineer-in-charge | LS | 40000 | 40000
EM-12 Water quality water (PH, turbidity, hardness, Cl, TDS, Mn, As, Fe,one for ground water and one for surface TC,FC)- by any recognized laboratory as per Engineer-incharge. | LS | 30000 | 30000
New 132/33 kV Substation at Laxmipur
Description of item | Qty | Rate | Amount
EM-01 Establishment of labor camp (1 male shed, 1 female shed - 12 ft x 30 ft each) with living arrangement, drinking water facilities, cooking arrangement, mosquito net,, waste bin etc. as per Engineer-in-charge. | 2 | 20000 | 40000
EM-02 Dust suppression measures by water spraying throughout the construction period in and around the subproject site, uncovered aggregates and loose materials such as stockpiles of the sands, excavated earth etc. daily or as per requirements (lump sum) as per Engineer-in-charge. | LS |  | 5000
EM-03 To provide water supply facilities in the camp site ,1nos. of tube well as per Engineer-in-charge. | 1 | 15000 | 15000
EM-04 Sanitation facilities (at the camp site): 2nos. of the toilets preferably portable toilets (1 no. for women and 1nos. for men) as per Engineer-in-charge. | 2 | 15000 | 30000
EM-05 Installation of cautionary sign in term of health and safety signs as required as per Engineer-in-charge. | LS | 16000 | 16000
EM-06 Providing PPEs like hand gloves, spectacles for eye protection, helmets, masks, visible jacket, ear plug, safety boots for at least 30 person (25 for workers and 5 for visitor) and one first aid box with necessary medicine as per Engineer-in-charge. | LS | 20000 | 20000
EM-07 Wastes disposal facility during the construction period; collection, transportation, and providing 4 bin to be provided where 2 for organic and 2 for inorganic waste as per Engineer-in-charge | LS | 20000 | 20000
EM-08 Tree plantation for ecological enhancement work preferably local fruits, flowers, medicinal and ornamental trees- 50 nos. trees (Lum sum) as per Engineer-in-charge | 50 | 400 | 20000
EM-9 Awareness documents (signs/ posters) for effective use of water source and proper waste management, Lum sum basis) as per Engineer-in-charge. | LS | 5000 | 5000
EM-10 Noise level measurement. It can be measured from the preapproved public institute/ university 2 times during construction as per Engineer-in-charge. | LS | 20000 | 20000
EM-11 Air quality (SPM, PM10)) measurement- It can be measured from the pre-approved public institute/ university 2 times during construction as per Engineer-in-charge | LS | 40000 | 40000
EM-12 Water quality water (PH, turbidity, hardness, Cl, TDS, Mn, As, Fe,one for ground water and one for surface TC,FC)- by any recognized laboratory as per Engineer-incharge. | LS | 30000 | 30000
New 132/33 kV Substation at Kosba
Description of item | Qty | Rate | Amount
EM-01 Establishment of labor camp (1 male shed, 1 female shed - 12 ft x 30 ft each) with living arrangement, drinking water facilities, cooking arrangement, mosquito net,, waste bin etc. as per Engineer-in-charge. | 2 | 20000 | 40000
EM-02 Dust suppression measures by water spraying throughout the construction period in and around the subproject site, uncovered aggregates and loose materials such as stockpiles of the sands, excavated earth etc. daily or as per requirements (lump sum) as per Engineer-in-charge. | LS |  | 5000
EM-03 To provide water supply facilities in the camp site ,1nos. of tube well as per Engineer-in-charge. | 1 | 15000 | 15000
EM-04 Sanitation facilities (at the camp site): 2nos. of the toilets preferably portable toilets (1 no. for women and 1nos. for men) as per Engineer-in-charge. | 2 | 15000 | 30000
EM-05 Installation of cautionary sign in term of health and safety signs as required as per Engineer-in-charge. | LS | 16000 | 16000
EM-06 Providing PPEs like hand gloves, spectacles for eye protection, helmets, masks, visible jacket, ear plug, safety boots for at least 30 person (25 for workers and 5 for visitor) and one first aid box with necessary medicine as per Engineer-in-charge. | LS | 20000 | 20000
EM-07 Wastes disposal facility during the construction period; collection, transportation, and providing 4 bin to be provided where 2 for organic and 2 for inorganic waste as per Engineer-in-charge | LS | 20000 | 20000
EM-08 Tree plantation for ecological enhancement work preferably local fruits, flowers, medicinal and ornamental trees- 50 nos. trees (Lum sum) as per Engineer-in-charge | 50 | 400 | 20000
EM-9 Awareness documents (signs/ posters) for effective use of water source and proper waste management, Lum sum basis) as per Engineer-in-charge. | LS | 5000 | 5000
EM-10 Noise level measurement. It can be measured from the preapproved public institute/ university 2 times during construction as per Engineer-in-charge. | LS | 20000 | 20000
EM-11 Air quality (SPM, PM10)) measurement- It can be measured from the pre-approved public institute/ university 2 times during construction as per Engineer-in-charge | LS | 40000 | 40000
EM-12 Water quality water (PH, turbidity, hardness, Cl, TDS, Mn, As, Fe,one for ground water and one for surface TC,FC)- by any recognized laboratory as per Engineer-incharge. | LS | 30000 | 30000
New 132/33 kV Substation at Kosba
Description of item | Qty | Rate | Amount
EM-01 Establishment of labor camp (1 male shed, 1 female shed - 12 ft x 30 ft each) with living arrangement, drinking water facilities, cooking arrangement, mosquito net,, waste bin etc. as per Engineer-in-charge. | 2 | 20000 | 40000
EM-02 Dust suppression measures by water spraying throughout the construction period in and around the subproject site, uncovered aggregates and loose materials such as stockpiles of the sands, excavated earth etc. daily or as per requirements (lump sum) as per Engineer-in-charge. | LS |  | 5000
EM-03 To provide water supply facilities in the camp site ,1nos. of tube well as per Engineer-in-charge. | 1 | 15000 | 15000
EM-04 Sanitation facilities (at the camp site): 2nos. of the toilets preferably portable toilets (1 no. for women and 1nos. for men) as per Engineer-in-charge. | 2 | 15000 | 30000
EM-05 Installation of cautionary sign in term of health and safety signs as required as per Engineer-in-charge. | LS | 16000 | 16000
EM-06 Providing PPEs like hand gloves, spectacles for eye protection, helmets, masks, visible jacket, ear plug, safety boots for at least 30 person (25 for workers and 5 for visitor) and one first aid box with necessary medicine as per Engineer-in-charge. | LS | 20000 | 20000
EM-07 Wastes disposal facility during the construction period; collection, transportation, and providing 4 bin to be provided where 2 for organic and 2 for inorganic waste as per Engineer-in-charge | LS | 20000 | 20000
EM-08 Tree plantation for ecological enhancement work preferably local fruits, flowers, medicinal and ornamental trees- 50 nos. trees (Lum sum) as per Engineer-in-charge | 50 | 400 | 20000
EM-9 Awareness documents (signs/ posters) for effective use of water source and proper waste management, Lum sum basis) as per Engineer-in-charge. | LS | 5000 | 5000
EM-10 Noise level measurement. It can be measured from the preapproved public institute/ university 2 times during construction as per Engineer-in-charge. | LS | 20000 | 20000
EM-11 Air quality (SPM, PM10)) measurement- It can be measured from the pre-approved public institute/ university 2 times during construction as per Engineer-in-charge | LS | 40000 | 40000
EM-12 Water quality water (PH, turbidity, hardness, Cl, TDS, Mn, As, Fe,one for ground water and one for surface TC,FC)- by any recognized laboratory as per Engineer-incharge. | LS | 30000 | 30000

## Code
Country of Origin
Item | Country | Code