## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:July 2021
Sl. | Items | Current Month |  | Current Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2021-07-01 |  | 2021-06-01 |  | 2020-07-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 13525 | 2021-07-15 | 13014 | 2021-06-02 | 12552 | 26/07/20 | 13792 | 2021-04-27
|  |  | 21:00 |  | 21:00 |  | 22:00 |  | 20:00
2 | Minimum Generation (MW) | 6682 | 2021-07-29 | 7369 | 2021-06-18 | 7092.1 | 31/07/20 | - | -
|  |  | 1:00 |  | 9:00 |  | 8:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 13525 | 2021-07-15 | 13014 | 2021-06-02 | 12536 | 26/07/20 | 13792 | 2021-04-27
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 20:00
4 | Maximum Day Peak Generation (MW) | 11549 | 2021-07-15 | 9351 | 2021-06-01 | 10525.4 | 26/07/20 | 11773 | 2021-04-27
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 13525 | 2021-07-15 | 13014 | 2021-06-02 | 12536 | 26/07/20 | 14097 | 2021-04-27
|  |  | 21:00 |  | 19:00 |  | 21:00 |  | 19:00
6 | Average Generation (MW) at Evening Peak | 11656.2903 |  | 11972.1667 |  | 11474.9032 |  | 12676.7 | 2021-04-27
7 | Average Generation (MW) at Day Peak | 9260.4516 |  | 10113.8333 |  | 9424.8087 |  | 10379.6667 | 2021-04-27
8 | Maximum Power Import from India, BIPTC (MW) | 907 | 2021-07-01 | 933 | 2021-04-29 18:00 | 951 | 13/07/2020 | 956 | 27/3/2019
|  |  | 0:30 |  | 18:00 |  | 2:30 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 172 | 2021-07-10 | 187 | 2021-04-18 | 174 | 27/07/2020 | 194 | 12/06/19
|  |  | 23:00 |  | 18:00 |  | 23:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 0 | - | 0 | - | - | - | 1459 | 04/05/2010
|  |  | - |  | - |  |  |  | 20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 13792 | 2021-04-27
|  | - | - | - | - | - | - |  | 20:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | - | 0 | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | 0 |  | 0 |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 1852.5058 |  | 1824.666 |  | 3547.5075 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 113.9022 |  | 133.138 |  | 100.2925
22 | Net Generation of BPDB (MKWH) | 1738.6035 |  | 1691.528 |  | 3447.2149
23 | Net Generation of IPP (MKWH) | 4403.448 |  | 4415.8372 |  | 2424.5663
24 | Net Generation of REB (MKWH) | 129.0256 |  | 133.1241 |  | 150.4311
24 | Net Generation of Rental Power Plant (MKWH) | 427.9978 |  | 485.0104 |  | 531.8624
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 6699.0748 |  | 6725.4996 |  | 6554.0747 |  | 7072.7704 | April'21
26 | Energy Generation by Gas (MKWH) | 4815.0058 |  | 4718.5487 |  | 4349.8373 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 290.9346 |  | 291.9991 |  | 314.162 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1187.2509 |  | 1394.2185 |  | 1406.9164 |  | 1679.4648 | Sep-20
29 | Energy Generation by Hydro (MKWH) | 61.0975 |  | 17.4436 |  | 90.7677 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 16.6657 |  | 15.602 |  | 4.1688 |  | 22.56 | 2019-09-16
31 | Energy Generation by Coal (MKWH) | 442.0225 |  | 420.8257 |  | 488.515 |  | 627.4399 | April'21
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 659.2349 |  | 711.7673 |  | 769.1694 |  | 775.9511 | August-20
33 | Monthly Load Factor (%) | 74.2573 |  | 78.1871 |  | 79.4923 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:July 2021
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 13525 | 2021-07-15 | 21:00
Generation Period
| Dhaka | MW | 4565
| Chattogram | MW | 1319
| Cumilla | MW | 1262
| Mymensingh | MW | 1042
| Sylhet | MW | 535
a) | Total supply in East zone | MW | 8723
| Khulna | MW | 1599
| Barisal | MW | 398
| Rajshahi | MW | 1386
| Rangpur | MW | 783
b) | Total supply in West zone | MW | 4166
c) | Total supply in both zone ( a+b) | MW | 12889
Ref: | 27.21.0000.603.16.087.20.417 | Date: 18/07/2021
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:July 2021
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 850 | 2021-07-30 | 18:30
| b) Ishurdi end | MW | 228 | 2021-07-07 | 17:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 675 | 2021-07-01 | 15:00
| b) Ishurdi end | MW | 280 | 2021-07-30 | 19:30
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 42.94
| b) Ishurdi end | MKWH | 21.11
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 20.48
| b) Ishurdi end | MKWH | 41.68
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 400 | 2021-07-24 | 19:30
| b)Serajganj end | MW | 280 | 2021-07-01 | 14:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 260 | 2021-07-01 | 15:00
| b)Sirajganj end | MW | 360 | 2021-07-30 | 20:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 6.19 | 2021-07-31
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 6.14 | 2021-07-31
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 80.06
| b)Sirajganj end | MKWH | 12.56
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 12.36
| b)Sirajganj end | MKWH | 80.35
30 | Transmission loss of EWI /NO-2 | % | -0.078
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month:July 2021
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Manikganj | 132/33 kV Transformers- T2 | 2021-07-01 12:04 | 2021-07-01 13:30 | 1:26 | E/O | Due to spark on LT side of T-2 | 0 | 0 | No interruption
Dhamrai | 132/33 kV Transformers- T2 | 2021-07-01 15:16 | 2021-07-01 18:21 | 3:05 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformers- T2 | 2021-07-01 15:52 | 2021-07-01 15:52 | 0:00 | E/O | Due to sparking at LT cable near LT bushing. | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformers- GT-3 | 2021-07-02 08:50 | 2021-07-02 10:52 | 2:02 | E/O | Due to showing PRD | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer T-03 | 2021-07-02 15:45 | 2021-07-02 16:05 | 0:20 | T | Tripped showing Diff relay | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformers- T2 | 2021-07-04 06:46 | 2021-07-04 10:18 | 3:32 | E/O | Due to oil leakage from bushing of T2 | 0 | 0 | No interruption
Saver | 132/33 kV Transformers- T1 and T2 | 2021-07-04 14:54 | 2021-07-04 15:13 | 0:19 | E/O | Due to 33 kV B/C fault | 137 | 43.3833 | Power interruption
Keraniganj | 132/33 kV Transformers- T1 | 2021-07-05 07:21 | 2021-07-05 07:32 | 0:11 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Satmosjid | 132/33 kV Transformers- T2 | 2021-07-05 10:53 | 2021-07-05 12:59 | 2:06 | T | Tripped showing TC-PRV trip, lockout | 0 | 0 | No interruption
Tongi | 230/132 kV transformer T-1 | 2021-07-05 11:33 | 2021-07-05 11:55 | 0:22 | T | Due to OLTC trip,main protection trip. | 0 | 0 | No interruption
Tongi | 230/132 kV transformer T-3 | 2021-07-05 13:02 | 2021-07-05 15:20 | 2:18 | T | Due to HT Y-phase jumper flashing. | 0 | 0 | No interruption
Tongi | 230/132 kV transformer T-1 | 2021-07-05 16:28 | 2021-07-05 19:14 | 2:46 | T | Due to OLTC trip. | 0 | 0 | No interruption
Kaliakoir | 230/132 kV New transformer T | 2021-07-07 11:57 | 2021-07-07 12:41 | 0:44 | T | Tripped showing PRD | 100 | 73.3333 | Power interruption
Tangail | 132/33 kV Transformers- T1 | 2021-07-08 12:50 | 2021-07-08 14:30 | 1:40 | T | Tripped showing PRD,Bhouchaltz relay | 0 | 0 | No interruption
Bhulta | 132/33 kV Transformers- T2 | 2021-07-08 20:33 | 2021-07-08 20:57 | 0:24 | T | Tripped showing O/C relay | 60 | 24 | Power interruption
Tongi | 132/33 kV Transformers- T1 and T2 | 2021-07-09 13:44 | 2021-07-09 13:58 | 0:14 | T | Due to 33 kV feeder fault | 35 | 8.1667 | Power interruption
Jamalpur | 132/33 kV Transformers- T1 | 2021-07-12 12:22 | 2021-07-12 13:32 | 1:10 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformers- T3 | 2021-07-12 15:44 | 2021-07-12 18:10 | 2:26 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Nawabganj | 132/33 kV Transformers- T1 | 2021-07-13 08:27 | 2021-07-13 09:08 | 0:41 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Nawabganj | 132/33 kV Transformers- T2 | 2021-07-13 09:11 | 2021-07-13 09:37 | 0:26 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Netrokona | 132/33 kV Transformers- T3 | 2021-07-13 08:10 | 2021-07-13 10:35 | 2:25 | E/O | Due to red-hot maint | 28 | 67.6667 | Power interruption
Netrokona | 132/33 kV Transformers- T4 | 2021-07-13 10:37 | 2021-07-13 12:55 | 2:18 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Satmosjid | 132/33 kV Transformers- T2 | 2021-07-13 12:04 | 2021-07-13 13:33 | 1:29 | T | Tripped showing 86 TCSR relay | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformers- T1, T2 | 2021-07-14 08:17 | 2021-07-14 11:46 | 3:29 | T | Tripped showing O/C relay | 80 | 278.6667 | Power interruption
Maniknagar | 132/33 kV Transformers- T1, T2 | 2021-07-15 21:03 | 2021-07-15 21:05 | 0:02 | T | Tripped showing O/C relay | 93 | 3.1 | Power interruption
Aminbazar | 230/132 kV transformer T03 | 2021-07-16 15:13 | 2021-07-16 16:22 | 1:09 | T | Tripped showing Gen. trip,oil purify alarm | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformers- T3 | 2021-07-17 08:58 | 2021-07-17 16:48 | 7:50 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformers- T2 | 2021-07-18 09:22 | 2021-07-18 13:43 | 4:21 | E/O | Due to oil leakage | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformers- T1 | 2021-07-20 08:26 | 2021-07-20 10:22 | 1:56 | E/O | Due to red-hot maint | 10 | 19.3333 | Power interruption
Mymensingh | 132/33 kV Transformers- T2 | 2021-07-20 10:48 | 2021-07-21 00:32 | 13:44 | E/O | Due to Y,LT bushing clamp temperature high | 0 | 0 | No interruption
Keraniganj | 132/33 kV Transformers- T1 & 33 kV Bus | 2021-07-20 13:49 | 2021-07-20 15:37 | 1:48 | E/O | Due to red-hot maint | 5 | 9 | Power interruption
Kishoreganj | 132/33 kV Transformers- T3 & 33 kV Bu | 2021-07-23 00:01 | 2021-07-23 00:35 | 0:34 | E/O | Due to red-hot maint | 20 | 11.3333 | Power interruption
Satmosjid | 132/33 kV Transformers- T2 | 2021-07-24 08:50 | 2021-07-24 11:17 | 2:27 | T | Tripped showing L/O relay | 0 | 0 | No interruption
Nawabganj | 33 kV Bus | 2021-07-30 08:17 | 2021-07-30 09:24 | 1:07 | E/O | Due to red-hot maint | 28 | 31.2667 | Power interruption
Madanganj | 132/33 kV Transformers- T1 & T2 | 2021-07-31 16:00 | 2021-07-31 22:10 | 6:10 | T | Tripped showing O/C relay at 33 kV end | 0 | 0 | No interruption
Madanganj | 132/33 kV Transformers- T1 & T3 | 2021-07-31 16:00 | 2021-07-31 16:40 | 0:40 | T | Tripped showing O/C relay at 33 kV end | 0 | 0 | No interruption
|  |  | Total : | 77:41 |  | Unserved Energy: |  | 569.25
Dhaka (South) Grid Circle :
Norsingdi | 132/33 kv transformers T-2 | 2021-07-16 00:53 | 2021-07-16 01:30 | 0:37 | T | Tripped showing bhuchaltz relay | 0 | 0 | No interruption
Hasnabad | 132/33 kv transformers T-1, T-5 | 2021-07-23 13:29 | 2021-07-23 13:48 | 0:19 | T | Tripped showing 33 kV Pangaon feeder fault | 50 | 15.8333 | Power interruption
|  |  | Total : | 0:56 |  | Unserved Energy: |  | 15.8333
Chattogram Grid Circle :
Halishahar | 132/33 kv transformers T-1, T-2 & T-3 | 2021-07-05 14:59 | 2021-07-05 15:22 | 0:23 | T | Tripped showing O/C relay | 85 | 32.5833 | Power interruption
Cox's Bazar | 132/33 kv transformers T-3 | 2021-07-08 18:00 | 2021-07-08 18:30 | 0:30 | E/O | Due to oil leakage maintenance | 0 | 0 | No interruption
Dohazari | 132/33 kV Transformers- T2 with 33 kV Bus-2 | 2021-07-10 07:56 | 2021-07-10 08:52 | 0:56 | E/O | Due to red-hot maint | 22 | 20.5333 | Power interruption
Chowmuhoni | 132/33 kv transformers T-3 | 2021-07-12 06:38 | 2021-07-12 07:20 | 0:42 | T | Due to operating PRD | 40 | 28 | Power interruption
Madunaghat | 132/33 kv transformers T-1 | 2021-07-12 11:51 | 2021-07-12 13:05 | 1:14 | E/O | Due to red-hot maint | 18 | 22.2 | Power interruption
Madunaghat | 132/33 kv transformers T1,T-2 | 2021-07-27 10:56 | 2021-07-27 11:22 | 0:26 | T | Due to heavy flashing at 33 kV Bus | 0 | 0 | No interruption
Bakulia | 132/33 kV transformer T3 | 2021-07-27 20:40 | 2021-07-27 21:38 | 0:58 | E/O | Due to red-hot maint | 29 | 28.0333 | Power interruption
Cox'sbazar | 132/33 kv transformers T1 & T-2 | 2021-07-28 23:29 | 2021-07-29 00:02 | 0:33 | T | Due to of 33 kV feeder fault | 40 | 22 | Power interruption
Hathazari | 230/132 kV transformer MT-4 | 2021-07-31 10:15 | 2021-07-31 11:43 | 1:28 | T | Due to due to O2TC trouble, mechanical | 0 | 0 | No interruption
|  |  | Total : | 7:10 |  | Unserved Energy: |  | 153.35
Cumilla Grid Circle :
Feni | 132/33 kv transformers T-1 | 2021-07-01 15:10 | 2021-07-01 16:42 | 1:32 | E/O | Due to red-hot maint | 15 | 23 | Power interruption
Chaddogram | 132/33 kv transformers T-2 | 2021-07-01 15:29 | 2021-07-01 18:07 | 2:38 | E/O | Due to Buchholz alarm. | 0 | 0 | No interruption
Comilla(N) | 132/33 kv transformers T-4 | 2021-07-11 12:19 | 2021-07-11 13:12 | 0:53 | E/O | Due to red-hot maint | 0 | 0 | No interruption
B.Baria | 132/33 kv transformers T-1 | 2021-07-11 20:58 | 2021-07-12 00:28 | 3:30 | T | Tripped showing SF6,Lockout , O/C,E/F relay | 0 | 0 | No interruption
B.Baria | 132/33 kv transformers T2 | 2021-07-11 20:58 | 2021-07-11 21:19 | 0:21 | T | Tripped showing SF6,Lockout , O/C,E/F relay | 150 | 52.5 | Power interruption
Sunamganj | 132/33 kv transformers T1 | 2021-07-13 09:35 | 2021-07-13 10:05 | 0:30 | T | Tripped showing B phase E/F relay | 0 | 0 | No interruption
Sunamganj | 132/33 kv transformers T3 | 2021-07-13 09:35 | 2021-07-13 10:17 | 0:42 | T | Tripped showing B phase E/F relay | 0 | 0 | No interruption
Chandpur | 132/33 kV transformers T-1, T-2 and T-3 | 2021-07-18 19:44 | 2021-07-18 19:58 | 0:14 | T | Tripped showing 33 kV Matlab feeder loop fault | 30 | 7 | Power interruption
Chatak | 132/33 kV transformer T-2 | 2021-07-19 02:15 | 2021-07-19 02:22 | 0:07 | T | Tripped showing 33 kV feeder fault | 0 | 0 | No interruption
Shahjibazar | 132/33 kV transformers T-4, T6 | 2021-07-19 11:11 | 2021-07-19 12:16 | 1:05 | T | Tripped showing Madhabpur-1 PBS feeder fault | 20 | 21.6667 | Power interruption
Sylhet | 132/33 kv transformers T1 | 2021-07-22 01:45 | 2021-07-22 02:36 | 0:51 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
Shahjibazar | 132/33 kv transformers T3 | 2021-07-31 18:54 | 2021-07-31 19:35 | 0:41 | T | Tripped showing O/C & E/F relay | 16 | 10.9333 | Power interruption
|  |  | Total : | 13:04 |  |  |  | 115.1
Khulna Grid Circle :
Satkhira | 132/33 kV Transformer-T1,T2 | 2021-07-01 14:59 | 2021-07-01 15:30 | 0:31 | T | Tripped showing O/C,E/F relay | 40 | 20.6667 | Power interruption
Barishal | 132/33 kV Transformer-T2 | 2021-07-05 07:12 | 2021-07-05 07:54 | 0:42 | E/O | Due to red-hot maint | 12 | 8.4 | Power interruption
Barishal(S) | 132/33 kV Transformer-T2 | 2021-07-07 11:38 | 2021-07-07 12:36 | 0:58 | E/O | Due to red-hot maint | 30 | 29 | Power interruption
Faridpur | 132/33 kV Transformer-T2 | 2021-07-08 08:46 | 2021-07-08 10:26 | 1:40 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Mongla | 132/33 kV Transformer-T2 | 2021-07-09 10:58 | 2021-07-09 11:56 | 0:58 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Bottail | 132/33 kV Transformer-T2 | 2021-07-12 07:45 | 2021-07-12 08:55 | 1:10 | E/O | Due to red-hot maint | 40 | 46.6667 | Power interruption
Jashore | 132/33 kV Transformer-T1 & 33 kV Bus | 2021-07-14 08:17 | 2021-07-14 08:24 | 0:07 | T | Tripped showing E/F relays at 33 kV end | 40 | 4.6667 | Power interruption
Mongla | 132/33 kV Transformer-T1,T2 | 2021-07-16 07:10 | 2021-07-16 07:36 | 0:26 | T | Tripped showing E/F relay | 36 | 15.6 | Power interruption
Madaripur | 33 kV Bus-2 | 2021-07-22 11:35 | 2021-07-22 13:27 | 1:52 | E/O | Due to red-hot maint | 15 | 28 | Power interruption
Chuadanga | 132/33 kV Transformer-T2 | 2021-07-23 07:01 | 2021-07-23 08:01 | 1:00 | E/O | Due to R-phase clamp | 35 | 35 | Power interruption
Faridpur | 132/33 kV Transformer-T2 & 33 kV Bus | 2021-07-23 07:19 | 2021-07-23 08:28 | 1:09 | E/O | Due to tear of 33 kV B-phase CT loop | 50 | 57.5 | Power interruption
Patuakhali | 132/33 kV Transformer-T1 | 2021-07-24 20:55 | 2021-07-24 23:32 | 2:37 | T | Due to tear of 33 kV B-phase CT loop | 0 | 0 | No interruption
Patuakhali | 132/33 kV Transformer-T2 | 2021-07-24 20:55 | 2021-07-24 21:12 | 0:17 | T | Due to tear of 33 kV B-phase CT loop | 20 | 5.6667 | Power interruption
Barishal(N) | 132/33 kV Transformer-T4 and T5 | 2021-07-26 16:09 | 2021-07-26 17:30 | 1:21 | T | Due to tear LT bus PT Y-phase burst | 32 | 43.2 | Power interruption
Barishal(S) | 132/33 kV Transformer-T1 and T2 | 2021-07-28 00:15 | 2021-07-28 00:36 | 0:21 | T | Due to 33 kV WZPDCL feeder fault | 32 | 11.2 | Power interruption
Mongla | 132/33 kV Transformer-T1 and T2 | 2021-07-28 21:56 | 2021-07-29 00:10 | 2:14 | T | Due to of 33 kV feeder fault | 0 | 0 | No interruption
Mongla | 132/33 kV Transformer-T1 and T2 | 2021-07-29 00:15 | 2021-07-29 02:48 | 2:33 | T | Due to of 33 kV feeder fault | 16 | 40.8 | Power interruption
Magura | 132/33 kV Transformer-T1 | 2021-07-30 09:54 | 2021-07-30 11:40 | 1:46 | T | Due to oil temperature high | 0 | 0 | No interruption
|  |  | Total : | 21:42 |  | Unserved Energy: |  | 346.3667
HVDC Grid Circle : Nil
Nil
|  |  | Total : | 0:00 |  |  |  | 0
Bogura Grid Circle:
B.Pukuria | 132/33 kV Transformer-T3 | 2021-07-01 00:43 | 2021-07-01 01:02 | 0:19 | T | Tripped showing no relay | 0 | 0 | No interruption
B.Pukuria | 132/33 kV Transformer-T4 | 2021-07-01 12:48 | 2021-07-01 14:20 | 1:32 | T | Tripped showing lock out relay | 0 | 0 | No interruption
B.Pukuria | 132/33 kV Transformer-T3 | 2021-07-02 08:54 | 2021-07-02 10:02 | 1:08 | T | Tripped showing lock out relay | 0 | 0 | No interruption
B.Pukuria | 132/33 kV Transformer-T3 | 2021-07-02 10:43 | 2021-07-02 12:49 | 2:06 | T | Tripped showing lock out relay | 0 | 0 | No interruption
Natore | 132/33 kV transformer T1 & T2 | 2021-07-03 16:29 | 2021-07-03 16:44 | 0:15 | T | Tripped showing O/C,E/F & lock out relay | 42 | 10.5 | Power interruption
Palashbari | 33 kV Bus section-2 | 2021-07-05 08:38 | 2021-07-05 09:25 | 0:47 | E/O | Due to red-hot maint | 20 | 15.6667 | Power interruption
Rangpur | 132/33 kV Transformer-T2 | 2021-07-07 11:07 | 2021-07-07 12:05 | 0:58 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Bogura(Old) | 132/33 kV Transformer-T3 with 33 kV Bus section | 2021-07-07 16:18 | 2021-07-07 17:15 | 0:57 | E/O | Due to red-hot maint | 22 | 20.9 | Power interruption
Shajadpur | 132/33 kV transformer T1 | 2021-07-08 11:05 | 2021-07-08 14:07 | 3:02 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Barapukuria | 33 kV Bus & 132/33 kV T3 & T4 transformers | 2021-07-09 11:05 | 2021-07-09 13:38 | 2:33 | E/O | Due to red-hot maint | 30 | 76.5 | Power interruption
Purbasadipur | 132/33 kV Transformer-T3 | 2021-07-16 20:01 | 2021-07-16 20:25 | 0:24 | T | Due to shetabganj NESCO feeder fault | 0 | 0 | No interruption
Pabna | 132/33 kV transformer T1 & T2 | 2021-07-17 12:05 | 2021-07-17 12:28 | 0:23 | T | Due to showing O/C, E/F relay | 94 | 36.0333 | Power interruption
Sirajganj | 132/33 kV Transformer-T4 | 2021-07-19 07:43 | 2021-07-19 10:27 | 2:44 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Barapukuria | 132/33 kV Transformer-T3 | 2021-07-20 14:25 | 2021-07-20 15:03 | 0:38 | T | Tripped showing L/O, O/C and E/F relays | 0 | 0 | No interruption
Ishwardi | 230/132 kV Transformer-T3 | 2021-07-27 08:15 | 2021-07-27 11:12 | 2:57 | T | Tripped showing OLTC | 0 | 0 | No interruption
|  |  | Total : | 20:43 |  |  |  | 159.6
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 141:16 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month:July 2021
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks | b
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Manikganj | Manikganj-Kabirpur 132 kV Ckt-2 | 2021-07-01 12:04 | 2021-07-01 13:30 | 1:26 | E/O | Due to spark on LT side of T-2 | 0 | 0 | No interruption
Kabirpur | Kabirpur-Tongi 132 kV Ckt-2 | 2021-07-04 06:45 | 2021-07-04 06:55 | 0:10 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Manikganj | Manikganj-Kabirpur 132 kV Ckt-2 | 2021-07-04 06:46 | 2021-07-04 10:18 | 3:32 | E/O | due to oil leakage from bushing of T2 | 0 | 0 | No interruption
Ashuganj(S) | Ashuganj(S)-Ghorasal 230 kV Ckt-2 | 2021-07-05 00:51 | 2021-07-05 02:04 | 1:13 | T | Tripped showing dist relay | 0 | 0 | No interruption
Ghorasal(AIS) | Ghorasal(AIS)-Ghorasal(GIS) 230 kV Ckt-1 | 2021-07-05 00:51 | 2021-07-05 02:38 | 1:47 | T | Due to red hot maintenance | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-2 | 2021-07-06 21:02 | 2021-07-06 21:18 | 0:16 | T | Tripped showing dist relay | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamrai 132 kV Ckt-1 | 2021-07-06 19:40 | 2021-07-06 20:50 | 1:10 | T | Due to Diff. relay | 103 | 120.1667 | Power interruption
Kaliakoir | Kaliakoir-Dhamrai 132 kV Ckt-2 | 2021-07-06 20:22 | 2021-07-06 20:26 | 0:04 | T | Due to Diff. relay | 96 | 6.4 | Power interruption
Keraniganj | Keraniganj-Hasnabad 230 kV Ckt-1 | 2021-07-07 09:42 | 2021-07-07 17:54 | 8:12 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV Ckt-3 | 2021-07-09 00:15 | 2021-07-09 00:39 | 0:24 | E/O | Due to mid CB gas pressure problem | 0 | 0 | No interruption
Agargaon | Agargaon-Cantonment 132 kV Ckt-1 | 2021-07-09 18:30 | 2021-07-09 18:30 | 0:00 | T | Tripped showing Diff. B-phase relay | 0 | 0 | No interruption
Mymensing | Mymensing-Netrokona 132 kV Ckt-1 | 2021-07-09 21:52 | 2021-07-10 00:13 | 2:21 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Shyampur | Shyampur-Hasnabad 230 kV Ckt | 2021-07-12 09:37 | 2021-07-12 15:06 | 5:29 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV Ckt-2 | 2021-07-13 15:15 | 2021-07-13 15:40 | 0:25 | T | Tripped showing dist, O/C relay | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ishurdi 230 kV Ckt-1 | 2021-07-15 13:33 | 2021-07-15 14:25 | 0:52 | T | Tripped showing dist relay | 0 | 0 | No interruption
Ghorasal | Ghorasal GIS-Ghorasal(O) 230 kV Ckt-1 | 2021-07-15 13:50 | 2021-07-15 14:20 | 0:30 | T | Tripped showing pick up & SOTF relay | 0 | 0 | No interruption
Manikganj | Manikganj-Kabirpur 132 kV Ckt-2 | 2021-07-18 09:22 | 2021-07-18 13:43 | 4:21 | E/O | Due to oil leakage | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV Ckt-1 | 2021-07-19 16:32 | 2021-07-19 16:46 | 0:14 | T | Tripped showing no relay | 0 | 0 | No interruption
Mymensing | Mymensing-Kishorganj 132 kV Ckt-2 | 2021-07-23 13:50 | 2021-07-23 13:57 | 0:07 | T | Tripped showing dist relay | 0 | 0 | No interruption
Ghorasal | Ghorasal-Norsingdi 132 kV Ckt-1 | 2021-07-24 04:15 | 2021-07-24 05:30 | 1:15 | T | Tripped showing showing E/F relay | 0 | 0 | No interruption
Kodda | Kodda-Joydevpur 132 kV Ckt-1 | 2021-07-24 01:37 | 2021-07-24 07:21 | 5:44 | T | Tripped showing showing E/F relay | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-1 | 2021-07-27 08:50 | 2021-07-27 09:11 | 0:21 | T | Tripped showing dist relay | 0 | 0 | No interruption
Aminbazar | Aminbazar-manikganj-162 MW P/S 132 kV Ckt-2 | 2021-07-30 19:33 | 2021-07-30 20:30 | 0:57 | T | Tripped showing dist relay | 0 | 0 | No interruption
|  |  | Total : | 23:00 |  | Unserved Energy: |  | 126.5667
Dhaka (South) Grid Circle :
Hasnabad | Hasnabad-Keraniganj 230 kV Ckt-1 | 2021-07-03 22:49 | 2021-07-03 22:49 | 0:00 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Maniknagar 230 kV Ckt-2 | 2021-07-14 16:28 | 2021-07-14 17:58 | 1:30 | E/O | Due to spark at CT | 0 | 0 | No interruption
|  |  | Total : | 1:30 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Bakulia | Bakulia-Khulshi 132 kV Ckt-1 | 2021-07-06 18:58 | 2021-07-06 19:10 | 0:12 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Khulshi | Khulshi-Madunaghat 132 kV Ckt-1 | 2021-07-11 11:00 | 2021-07-11 11:24 | 0:24 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Hathazari | Hathazari -Kaptai 132 kV Ckt-1 | 2021-07-11 21:30 | 2021-07-11 21:58 | 0:28 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Dohazari | Dohazari-Cox's Bazar 132 kV Ckt-2 | 2021-07-13 10:14 | 2021-07-13 11:19 | 1:05 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV Ckt-1 | 2021-07-15 09:09 | 2021-07-15 09:51 | 0:42 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
AKSM | AKSM-Hathazari 230 kV Ckt | 2021-07-17 05:20 | 2021-07-17 07:23 | 2:03 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Khulshi | Khulshi-AKSM 132 kV Ckt | 2021-07-17 11:21 | 2021-07-17 12:44 | 1:23 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Bakulia | Bakulia-Khulshi 132 kV Ckt-1 | 2021-07-18 21:33 | 2021-07-18 22:36 | 1:03 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-2 | 2021-07-26 19:45 | 2021-07-26 20:34 | 0:49 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-2 | 2021-07-26 21:40 | 2021-07-26 22:35 | 0:55 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-2 | 2021-07-27 03:01 | 2021-07-27 03:01 | 0:00 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-2 | 2021-07-29 00:03 | 2021-07-29 00:23 | 0:20 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-2 | 2021-07-30 11:26 | 2021-07-30 11:40 | 0:14 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 9:38 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Ashuganj | Ashuganj-Ashuganj(S) 230 kV Ckt-2 | 2021-07-04 13:00 | 2021-07-04 13:00 | 0:00 | T | Tripped showing Diff relay. | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sreemangal 132 kV Ckt-2 | 2021-07-08 13:19 | 2021-07-08 13:38 | 0:19 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Sylhet | Sylhet-Chattak 132 kV Ckt-2 | 2021-07-13 00:01 | 2021-07-13 00:16 | 0:15 | T | Tripped showing Dist. relay | 33 | 8.25 | Power interruption
Tripura | Tripura-Cumilla 132 kV both Ckts | 2021-07-17 13:41 | 2021-07-17 14:19 | 0:38 | T | Due to CT burst of Laksham REB feeder | 96 | 60.8 | Power interruption
B.Baria | B.Baria-Shahzibazar 132 kV Ckt-2 | 2021-07-22 13:41 | 2021-07-22 19:56 | 6:15 | T | Tripped showing SOTF relay | 0 | 0 | No interruption
B.Baria | B.Baria-Shahzibazar 132 kV Ckt-3 | 2021-07-22 20:14 | 2021-07-22 20:14 | 0:00 | T | Tripped showing SOTF relay | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Kulaura 132 kV Ckt-2 | 2021-07-26 14:18 | 2021-07-26 15:13 | 0:55 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV Ckt-1 | 2021-07-29 11:27 | 2021-07-29 11:40 | 0:13 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
|  |  | Total : | 8:35 |  | Unserved Energy: |  | 69.05
Khulna Grid Circle :
Bottail | Bottail-Jhenaidah 132 kV Ckt-1 | 2021-07-02 00:05 | 2021-07-02 05:58 | 5:53 | T | Tripped showing Dist. Z1,E/F relay | 0 | 0 | No interruption
Khulna© | Khulna©-Khulna(S) 132 kV Ckt-2 | 2021-07-06 07:34 | 2021-07-06 07:34 | 0:00 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV Ckt-2 | 2021-07-07 14:29 | 2021-07-07 14:47 | 0:18 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Khulna© | Khulna©-Khulna-225 MW P/S 132 kV Ckt-2 | 2021-07-26 09:18 | 2021-07-26 10:37 | 1:19 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Barishal(S) | Barishal South-(Barguna)-Patuakhali 132 kV Ckt | 2021-07-28 01:32 | 2021-07-28 09:07 | 7:35 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Faridpur | Faridpur-Gopalganj(N) 132 kV Ckt-1 | 2021-07-29 21:35 | 2021-07-29 21:46 | 0:11 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Faridpur | Faridpur-Gopalganj(N) 132 kV Ckt-2 | 2021-07-29 21:35 | 2021-07-29 21:47 | 0:12 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
|  |  | Total : | 15:28 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Nill
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Polashbari | Polashbari-Mahasthangar 132 kV Ckt-1 | 2021-07-12 10:40 | 2021-07-12 10:53 | 0:13 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Polashbari | Polashbari-Rangpur 132 kV Ckt-2 | 2021-07-12 10:40 | 2021-07-12 10:48 | 0:08 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Sirajganj | Sirajganj-Shahjadpur 132 kV Ckt | 2021-07-12 10:07 | 2021-07-12 10:22 | 0:15 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Sirajganj | Sirajganj-Shahjadpur 132 kV Ckt | 2021-07-12 11:23 | 2021-07-12 11:23 | 0:00 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Baghabari | Baghabari-Shahjadpur 132 kV Ckt-1 | 2021-07-18 09:39 | 2021-07-18 10:03 | 0:24 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Rajshahi(O) | Rajshahi(O)-Natore 132 kV Ckt-2 | 2021-07-19 19:15 | 2021-07-19 19:15 | 0:00 | T | Tripped showing Dist. Z2 relay | 0 | 0 | No interruption
Sirajganj | Sirajganj-Baghabari 132 kV Ckt | 2021-07-27 17:29 | 2021-07-27 19:20 | 1:51 | T | Tripped showing Dist. & SOTF | 0 | 0 | No interruption
|  |  | Total : | 2:51 |  | Unserved Energy: |  | 0
Others :Nil
Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 61:02 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:July 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Saver | 33 kV Bus-B | 2021-07-04 13:28 | 2021-07-04 15:13 | 1:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishorganj | 132/33 kv transformers T-1 | 2021-07-05 08:52 | 2021-07-05 11:20 | 2:28 | S/O | Due to 33 kV loop maint. | 0 | 0 | No interruption
Kaliakoir | 230 kV Bus-2 | 2021-07-06 08:29 | 2021-07-06 17:34 | 9:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | 400 kV Bus-1 & 2 | 2021-07-07 12:20 | 2021-07-07 12:20 | 0:00 | S/O | Due to Project work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-1 | 2021-07-08 06:24 | 2021-07-08 06:24 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | 132 kV Bus-1 | 2021-07-08 10:47 | 2021-07-08 10:47 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | 230 kV Bus-2 | 2021-07-08 13:57 | 2021-07-08 17:19 | 3:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kv transformers T-1 | 2021-07-09 06:39 | 2021-07-09 06:39 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Maniknagar | 132/33 kV transformer T2 | 2021-07-09 11:02 | 2021-07-09 15:50 | 4:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Saver | Bus-B & 132/33 kV transformer T3 | 2021-07-09 09:23 | 2021-07-09 17:45 | 8:22 | S/O | Due to 33 kV Bus coupler maint | 0 | 0 | No interruption
Savar | 33 kV Bus-B | 2021-07-10 09:44 | 2021-07-10 18:45 | 9:01 | S/O | Due to D/W work | 0 | 0 | No interruption
Bhaluka | 132/33 kv transformers T-1 | 2021-07-11 09:13 | 2021-07-11 12:46 | 3:33 | S/O | Due to D/W work | 15 | 53.25 | Power interruption
Savar | 33 kV Bus-B | 2021-07-12 10:30 | 2021-07-12 16:42 | 6:12 | S/O | Due to D/W work | 0 | 0 | No interruption
Sherpur | 132/33 kv transformers T-1 | 2021-07-13 07:52 | 2021-07-13 07:52 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur | 132/33 kv transformers T-1 with 33 kV bus | 2021-07-13 08:10 | 2021-07-13 09:44 | 1:34 | S/O | Due to C/M work | 12 | 18.8 | Power interruption
Aminbazar | 230/132 kV transformers T-2 | 2021-07-13 09:23 | 2021-07-13 17:30 | 8:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur | 132/33 kv transformers T-3 | 2021-07-13 10:25 | 2021-07-13 12:07 | 1:42 | S/O | Due to C/M work | 12 | 20.4 | Power interruption
Jamalpur | 132/33 kv transformers T-3 | 2021-07-13 09:25 | 2021-07-13 12:20 | 2:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Nawabganj | 33 kV full bus | 2021-07-14 07:08 | 2021-07-14 09:10 | 2:02 | S/O | Due to C/M work | 32 | 65.0667 | Power interruption
Aminbazar | 230/132 kV transformers T-3 | 2021-07-14 09:12 | 2021-07-14 17:59 | 8:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kv transformers T-3 | 2021-07-14 08:45 | 2021-07-14 09:55 | 1:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Satmosjid | 132/33 kV transformer T2 | 2021-07-14 09:33 | 2021-07-14 12:06 | 2:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV transformer T2 | 2021-07-15 07:52 | 2021-07-15 13:42 | 5:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | 132 kV main Bus | 2021-07-17 10:53 | 2021-07-17 15:01 | 4:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 132/33 kv transformers T-3 | 2021-07-17 09:53 | 2021-07-17 12:44 | 2:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | 132 kV reserve Bus | 2021-07-18 08:42 | 2021-07-18 18:40 | 9:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | 132 kV Bus-1 | 2021-07-18 13:45 | 2021-07-18 20:15 | 6:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | 132 kV reserve Bus | 2021-07-19 08:49 | 2021-07-19 11:45 | 2:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensing | 132/33 kV transformer T2 | 2021-07-19 10:35 | 2021-07-19 12:43 | 2:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensing | 132/33 kV transformer T3 | 2021-07-20 10:48 | 2021-07-21 00:32 | 13:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV transformer T3 | 2021-07-26 11:49 | 2021-07-26 13:33 | 1:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishorganj | 132/33 kV transformer T3 | 2021-07-27 07:08 | 2021-07-27 09:53 | 2:45 | S/O | Due to C/M work | 30 | 82.5 | Power interruption
Jamalpur | 132/33 kV transformer T4 | 2021-07-27 08:54 | 2021-07-27 16:24 | 7:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV transformer T2 | 2021-07-27 10:58 | 2021-07-27 14:15 | 3:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T4 | 2021-07-28 19:11 | 2021-07-28 20:03 | 0:52 | S/O | Due to C/M work | 20 | 17.3333 | Power interruption
Netrokona | 132 kV main Bus | 2021-07-29 07:59 | 2021-07-29 11:16 | 3:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Netrokona | 132/33 kV transformer T4 | 2021-07-29 07:53 | 2021-07-29 11:36 | 3:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Nawabganj | 132/33 kV transformer T1 | 2021-07-29 20:11 | 2021-07-29 20:11 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Valuka | 33 kV bus section-1 | 2021-07-30 07:53 | 2021-07-30 09:22 | 1:29 | S/O | Due to C/M work | 21 | 31.15 | Power interruption
Kabirpur | 132 kV reserve Bus | 2021-07-30 14:23 | 2021-07-30 17:02 | 2:39 | S/O | Due to C/M work | 22 | 58.3 | Power interruption
Kabirpur | 132/33 kV transformer T1 | 2021-07-30 14:16 | 2021-07-30 17:11 | 2:55 | S/O | Due to C/M work | 23 | 67.0833 | Power interruption
Tangail | 132/33 kV transformer T1 | 2021-07-31 09:08 | 2021-07-31 14:30 | 5:22 | S/O | Due to C/M work | 24 | 128.8 | Power interruption
|  |  | Total : | 161:04 |  | Unserved Energy: |  | 542.6833
Dhaka (South) Grid Circle :
Haripur | 230 kV Bus-1 | 2021-07-07 07:39 | 2021-07-07 07:39 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Hathazari | 132 kV main Bus-1 | 2021-07-02 10:55 | 2021-07-02 15:20 | 4:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | 230/132 kV transformer MT-04 | 2021-07-03 07:11 | 2021-07-03 07:11 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | 132 kV main Bus | 2021-07-03 07:27 | 2021-07-03 07:27 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Halishahar | 33 kV Bus under 132/33 kV T-2 transformer | 2021-07-06 15:56 | 2021-07-06 16:03 | 0:07 | S/O | Due to 33kV tunnel feeder loop stringing work | 22 | 2.5667 | Power interruption
Halishahar | 132 kV Bus | 2021-07-07 04:46 | 2021-07-07 06:52 | 2:06 | S/O | Due to C/M work | 55 | 115.5 | Power interruption
Madunaghat | 132/33 kv transformers T-1 | 2021-07-08 07:13 | 2021-07-08 07:13 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
BSRM | 230/132 kV transformer T |  | 2021-07-08 15:59 |  | S/O | After maintenance | 0 | 0 | No interruption
Bakulia | 132/33 kv transformers T-3 | 2021-07-10 07:35 | 2021-07-10 07:35 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | 132/33 kV transformer T2 with 33 kV bus | 2021-07-13 10:14 | 2021-07-13 11:19 | 1:05 | S/O | Due to C/M work | 20 | 21.6667 | Power interruption
Cox's Bazar | 132/33 kv transformers T-3 | 2021-07-17 15:15 | 2021-07-17 16:21 | 1:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | 132/33 kv transformers T-2 | 2021-07-18 06:13 | 2021-07-18 06:13 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Halishahar | 132/33 kv transformers T-1 | 2021-07-28 19:26 | 2021-07-28 20:28 | 1:02 | S/O | Due to C/M work | 0 | 0 | No interruption
BSRM | 230/132 kV transformer T0-2 | 2021-07-31 14:29 | 2021-07-31 14:29 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 9:51 |  | Unserved Energy : |  | 139.7333
Cumilla Grid Circle :
B. Baria | 132/33 kV transformer T1 | 2021-07-12 16:46 | 2021-07-12 18:04 | 1:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhandaria | 132/33 kV transformer T1 | 2021-07-17 10:32 | 2021-07-17 13:21 | 2:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Comilla(S) | 132/33 kV transformer T2 |  | 2021-07-18 09:15 |  | S/O | After maintenance | 0 | 0 | No interruption
Patonga | 132/33 kv transformers T1 | 2021-07-19 14:40 | 2021-07-19 18:12 | 3:32 | S/O | Due to Diff maintenance work | 0 | 0 | No interruption
Patonga | 132 kV main Bus | 2021-07-19 16:32 | 2021-07-19 17:12 | 0:40 | S/O | Due to D/W work | 0 | 0 | No interruption
Chandpur | 132/33 kv transformers T1 | 2021-07-20 07:02 | 2021-07-20 07:02 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | 132/33 kv transformers T2 | 2021-07-23 07:17 | 2021-07-23 08:50 | 1:33 | S/O | Due to C/M work | 38 | 58.9 | Power interruption
Ashuganj | 132/33 kv transformers T2 | 2021-07-24 11:36 | 2021-07-24 18:18 | 6:42 | S/O | Due to energy meter test | 0 | 0 | No interruption
Cumilla(N) | 132/33 kv transformers T3 | 2021-07-26 07:47 | 2021-07-26 08:40 | 0:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | 132/33 kv transformers Av | 2021-07-28 09:24 | 2021-07-28 18:12 | 8:48 | S/O | Due to energy meter maintenance | 0 | 0 | No interruption
|  |  | Total : | 26:15 |  | Unserved Energy : |  | 58.9
Khulna Grid Circle :
Bhandaria | 132/33 kV both transformers along with 33 kV Bus | 2021-07-02 19:40 | 2021-07-02 19:50 | 0:10 | S/O | Due to fuse change of auxiliary X-former | 0 | 0 | No interruption
Gallamari | 132/33 kV Transformer-GT-1 | 2021-07-03 11:49 | 2021-07-03 14:09 | 2:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Gallamari | 132 kV full Bus | 2021-07-04 13:27 | 2021-07-04 13:27 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Goalpara | 132 kV Bus-A | 2021-07-05 10:30 | 2021-07-05 12:30 | 2:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T1 | 2021-07-05 07:40 | 2021-07-05 09:41 | 2:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T2 | 2021-07-10 08:21 | 2021-07-10 10:29 | 2:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj | 400 kV S/S capacitor bank | 2021-07-10 23:30 | 2021-07-10 23:30 | 0:00 | S/O | Due to 132 kV B-phase LA burst | 0 | 0 | No interruption
Gallamari | 132/33 kV Transformer-T1 |  | 2021-07-14 16:46 |  | S/O | After maintenance | 0 | 0 | No interruption
Gallamari | 132/33 kV Transformer-T2 |  | 2021-07-14 16:47 |  | S/O | After maintenance | 0 | 0 | No interruption
Rajbari | 132/33 kV Transformer-T1 | 2021-07-16 06:35 | 2021-07-16 06:35 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Bheramara | 132/33 kV Transformer-T2 | 2021-07-18 08:30 | 2021-07-18 09:39 | 1:09 | S/O | Due to GK project work. | 0 | 0 | No interruption
Barishal(N) | 132/33 kV Transformer-T4 | 2021-07-19 10:00 | 2021-07-19 10:54 | 0:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Patuakhali | 132/33 kV Transformer-T1 | 2021-07-19 11:41 | 2021-07-19 12:42 | 1:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Barisal | 132/33 kV Transformer-T2 | 2021-07-24 12:24 | 2021-07-24 13:44 | 1:20 | S/O | Due to C/M work | 20 | 26.6667 | Power interruption
Bagethat | 132/33 kV Transformer-T1 | 2021-07-26 07:05 | 2021-07-26 08:25 | 1:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T2 | 2021-07-28 08:33 | 2021-07-28 09:04 | 0:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T3 | 2021-07-28 09:50 | 2021-07-28 12:58 | 3:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenaidah(N) | 132 kV Bus & 230/132 kV transformer |  | 2021-07-28 12:33 |  | S/O | After maintenance | 0 | 0 | No interruption
Jhenaidah(N) | 230/132 kV transformer T01 |  | 2021-07-28 19:43 |  | S/O | After maintenance | 0 | 0 | No interruption
Barisal | 132/33 kV Transformer-T2 | 2021-07-29 09:05 | 2021-07-29 10:08 | 1:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T1 | 2021-07-30 09:25 | 2021-07-30 10:55 | 1:30 | S/O | Due to C/M work | 16 | 24 | Power interruption
|  |  | Total : | 20:35 |  | Unserved Energy : |  | 50.6667
HVDC Grid Circle :Nil
|  |  | Total : | 0:00 |  | Unserved Energy : |  | 0
Bogura Grid Circle:
Barapukuria | 132/33 kV Transformer-T4 | 2021-07-05 12:12 | 2021-07-05 15:12 | 3:00 | S/O | Due to 33 kV bus maint. | 20 | 60 | Power interruption
Sirajganj | 132/33 kV Transformer-T3 | 2021-07-08 09:49 | 2021-07-08 14:03 | 4:14 | S/O | Due to 33 kV incomer loop cut | 0 | 0 | No interruption
Natore | 33 kV Bus-1 & 2 | 2021-07-09 05:40 | 2021-07-09 07:43 | 2:03 | S/O | Due to 33 kV loop change | 60 | 123 | Power interruption
Bogura | 132/33 kV Transformer-T1 | 2021-07-12 07:12 | 2021-07-12 08:54 | 1:42 | S/O | Due to 33 kV loop change | 32 | 54.4 | Power interruption
Natore | 132/33 kV Transformer-T2 | 2021-07-16 05:31 | 2021-07-16 08:25 | 2:54 | S/O | Due to PBS maintenance work | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T3 | 2021-07-16 06:03 | 2021-07-16 09:37 | 3:34 | S/O | Due to PBS maintenance work | 40 | 142.6667 | Power interruption
Panchagar | 132 kV full bus | 2021-07-16 07:49 | 2021-07-16 08:58 | 1:09 | S/O | Due to D/W work | 40 | 46 | Power interruption
Ishurdi | 230/132 kV transformer T02 | 2021-07-16 09:12 | 2021-07-16 11:33 | 2:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Pabna | 132/33 kV Transformer-T2 its 33 kV Bus | 2021-07-18 12:50 | 2021-07-18 14:37 | 1:47 | S/O | Due to maintenance work | 0 | 0 | No interruption
Rajshahi(O) | 132 kV Bus | 2021-07-25 05:07 | 2021-07-25 07:30 | 2:23 | S/O | Due to C/M work | 100 | 238.3333 | Power interruption
Purbasadipur | 33 kV Bus & 132/33 kV transformer T1 | 2021-07-28 08:15 | 2021-07-28 10:12 | 1:57 | S/O | Due to C/M work | 30 | 58.5 | Power interruption
Niamatpur | 132/33 kV Transformer-T2 | 2021-07-28 19:29 | 2021-07-28 21:03 | 1:34 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 28:38 |  | Unserved Energy : |  | 722.9
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 246:23 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/5 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:July 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | Tongi-Bashundhara 132 kv Ckt-1 | 2021-07-01 06:59 | 2021-07-01 06:59 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Bosila 132 kV Ckt |  | 2021-07-01 16:12 |  | S/O | After maintenance | 0 | 0 | No interruption
Maniknagar | Maniknagar-Narinda 132 kV Ckt-2 | 2021-07-02 11:45 | 2021-07-02 17:04 | 5:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV Ckt-1 | 2021-07-02 08:42 | 2021-07-02 17:25 | 8:43 | S/O | Due to D/W work | 0 | 0 | No interruption
Manikganj P.P | Manikganj P.P.-Savar 132 kV Ckt-2 | 2021-07-02 11:11 | 2021-07-02 14:39 | 3:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV Ckt-1 & 2 | 2021-07-03 08:28 | 2021-07-03 18:25 | 9:57 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-1 | 2021-07-04 11:02 | 2021-07-04 19:20 | 8:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV Ckt-1 & 2 | 2021-07-04 08:24 | 2021-07-04 17:34 | 9:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-1 | 2021-07-04 08:55 | 2021-07-04 20:54 | 11:59 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-1 | 2021-07-04 20:09 | 2021-07-04 21:06 | 0:57 | S/O | Due to newly installed CT ration correction | 25 | 23.75 | Power interruption
Rampura | Rampura-Mogbazar 132 kV Ckt-2 | 2021-07-05 07:39 | 2021-07-05 07:39 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-1 | 2021-07-05 06:38 | 2021-07-05 06:38 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Ullon 132 kV Ckt-2 | 2021-07-05 08:36 | 2021-07-05 13:04 | 4:28 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-1 | 2021-07-06 07:41 | 2021-07-06 07:41 | 0:00 | S/O | Due to maint work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamrai 132 kV Ckt-2 |  | 2021-07-06 18:20 |  | S/O | After maintenance | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamrai 132 kV Ckt-2 | 2021-07-06 19:27 | 2021-07-06 19:45 | 0:18 | S/O | Due to testing purpose | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-1 | 2021-07-07 06:58 | 2021-07-07 06:58 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Manikganj P.P. | Manikganj P.P.-Savar 132 kV Ckt-2 | 2021-07-07 13:11 | 2021-07-07 16:41 | 3:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-2 | 2021-07-08 10:55 | 2021-07-08 17:58 | 7:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Hasnabad 230 kV Ckt-1 | 2021-07-08 11:12 | 2021-07-08 15:57 | 4:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Manikganj P/P | Manikganj P/P-Aminbazar 132 kV Ckt-1 | 2021-07-08 11:37 | 2021-07-08 17:38 | 6:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-1 | 2021-07-09 06:48 | 2021-07-09 06:48 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Narinda 132 kV Ckt-2 | 2021-07-09 11:02 | 2021-07-09 15:50 | 4:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-1 | 2021-07-10 09:04 | 2021-07-10 21:37 | 12:33 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-1 | 2021-07-11 07:41 | 2021-07-11 07:41 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj PP 132 kV Ckt-2 | 2021-07-11 09:35 | 2021-07-11 13:13 | 3:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-1 | 2021-07-12 07:25 | 2021-07-12 07:25 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Aurahati | Aurahati-Keraniganj 132 kV Ckt | 2021-07-12 10:05 | 2021-07-12 13:50 | 3:45 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Bhaluka 132 kV Ckt-1 | 2021-07-12 10:25 | 2021-07-12 15:47 | 5:22 | S/O | Due to D/W work | 0 | 0 | No interruption
Kodda S/S | Gazipur 100 MW-Kodda 132 kV Ckt | 2021-07-12 11:14 | 2021-07-12 18:24 | 7:10 | S/O | Due to Bus bar protection test. | 0 | 0 | No interruption
Kodda | Kodda-Rajendrapur 132 kV Ckt-1 | 2021-07-12 12:15 | 2021-07-12 21:10 | 8:55 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV Ckt-1 | 2021-07-13 08:21 | 2021-07-13 10:42 | 2:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Bhaluka 132 kV Ckt-2 | 2021-07-13 09:43 | 2021-07-13 15:16 | 5:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Kodda | Kodda-Rajendrapur 132 kV Ckt-1 | 2021-07-13 10:26 | 2021-07-13 13:29 | 3:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Kodda | Kodda-RPCL 100 MW 132 kV Ckt | 2021-07-13 10:20 | 2021-07-13 13:15 | 2:55 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrokona 132 kV Ckt-1 | 2021-07-14 09:07 | 2021-07-14 13:27 | 4:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Kodda | Kodda-Rajendrapur 132 kV Ckt-1 | 2021-07-14 10:46 | 2021-07-14 15:46 | 5:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensing | Mymensing-Netrokona 132 kV Ckt-1 | 2021-07-14 09:07 | 2021-07-14 13:27 | 4:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-1 | 2021-07-14 08:25 | 2021-07-14 17:58 | 9:33 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensing | Mymensing-Netrokona 132 kV Ckt-2 | 2021-07-15 09:17 | 2021-07-15 17:51 | 8:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Agargaon | Agargaon-Cantonment 132 kV Ckt-1 |  | 2021-07-15 16:53 |  | S/O | After maintenance | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj PP 132 kV Ckt-1 | 2021-07-16 09:13 | 2021-07-16 23:46 | 14:33 | S/O | Due to D/W work | 0 | 0 | No interruption
Agargaon | Agargaon-Cantonment 132 kV Ckt-1 | 2021-07-17 09:13 | 2021-07-16 16:53 |  | S/O | After maintenance | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj PP 132 kV Ckt-2 | 2021-07-17 08:39 | 2021-07-17 17:57 | 9:18 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV Ckt-1 | 2021-07-18 08:45 | 2021-07-18 19:24 | 10:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV Ckt-1 | 2021-07-19 12:22 | 2021-07-19 16:39 | 4:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV Ckt-2 | 2021-07-19 08:50 | 2021-07-19 12:21 | 3:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV Ckt-2 | 2021-07-25 10:44 | 2021-07-25 15:03 | 4:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV Ckt-1 | 2021-07-26 13:40 | 2021-07-26 17:08 | 3:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensing | Mymensing-Netrokona 132 kV Ckt-1 | 2021-07-28 08:27 | 2021-07-28 17:57 | 9:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensing | Mymensing-Netrokona 132 kV Ckt-2 | 2021-07-29 07:59 | 2021-07-29 11:16 | 3:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensing | Mymensing-Netrokona 132 kV Ckt-1 |  | 2021-07-29 15:25 |  | S/O | After maintenance | 0 | 0 | No interruption
Mymensing | Mymensing-Netrokona 132 kV Ckt-2 | 2021-07-31 08:11 | 2021-07-31 13:26 | 5:15 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 243:53 |  | Unserved Energy: |  | 23.75
Dhaka (South) Grid Circle :
Siddhirganj | Siddhirganj-Haripur 230 kV Ckt-1 | 2021-07-09 07:50 | 2021-07-09 10:50 | 3:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Maniknagar 230 kV Ckt-2 | 2021-07-14 12:25 | 2021-07-14 16:24 | 3:59 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 432:08 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-1 | 2021-07-02 16:14 | 2021-07-02 18:02 | 1:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-1 | 2021-07-03 06:58 | 2021-07-03 06:58 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-2 | 2021-07-03 07:01 | 2021-07-03 07:01 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV Ckt-2 | 2021-07-04 10:17 | 2021-07-04 11:53 | 1:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-2 |  | 2021-07-06 18:14 |  | S/O | After maintenance | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-1 | 2021-07-08 06:08 | 2021-07-08 06:08 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Madunaghat 132 kV Ckt-2 | 2021-07-10 10:11 | 2021-07-10 11:49 | 1:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Cox'sbazar | Cox'sbazar-Dohazari 132 kV Ckt | 2021-07-15 07:18 | 2021-07-15 07:18 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Matarbari-Cox's Bazar 132 kV Ckt-1 |  | 2021-07-15 16:39 |  | S/O | After maintenance | 0 | 0 | No interruption
Halishahar | Halishahar-Juldah 132 kV Ckt | 2021-07-16 06:13 | 2021-07-16 06:13 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Baraulia | Baraulia-KSRM 132 kV Ckt | 2021-07-30 10:15 | 2021-07-30 12:54 | 2:39 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 7:41 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Ashuganj | Ashuganj-Ashuganj(S) 230 kV Ckt-2 |  | 2021-07-04 08:47 |  | S/O | After mainteneance | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ashuganj(S) 230 kV Ckt-1 | 2021-07-04 09:12 | 2021-07-04 13:19 | 4:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Baroierhat | Baroierhat-PHP 132 kV Ckt-1 | 2021-07-04 08:35 | 2021-07-04 17:46 | 9:11 | S/O | Due to C/M work | 20 | 183.6667 | Power interruption
Feni | Feni-PHP 132 kV Ckt-1 | 2021-07-04 08:35 | 2021-07-04 17:46 | 9:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandpur S/S | Chandpur S/S-Chandpur Desh 132 kV Ckt-1 |  | 2021-07-15 18:14 |  | S/O | After mainteneance | 0 | 0 | No interruption
Chandpur S/S | Chandpur S/S-Chandpur Desh 132 kV Ckt-2 |  | 2021-07-15 18:16 |  | S/O | After mainteneance | 0 | 0 | No interruption
Chandpur | Chandpur-Kochua 132 kV Ckt-2 | 2021-07-16 09:13 | 2021-07-16 10:53 | 1:40 | S/O | Due to D/W work | 0 | 0 | No interruption
Chandpur | Chandpur-Kochua 132 kV Ckt-1 | 2021-07-16 10:58 | 2021-07-16 12:51 | 1:53 | S/O | Due to D/W work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-B.Baria 132 kV Ckt-2 |  | 2021-07-24 18:35 |  | S/O | After mainteneance | 0 | 0 | No interruption
|  |  | Total : | 26:02 |  | Unserved Energy: |  | 183.6667
Khulna Grid Circle :
Bagherhat | Bagherhat-Bhandaria 132 kV Ckt | 2021-07-12 10:43 | 2021-07-12 12:20 | 1:37 | S/O | Due to tree trimming. | 0 | 0 | No interruption
Gopalganj S/S | Gopalganj S/S-Gopalganj P/S 132 kV Ckt | 2021-07-13 13:54 | 2021-07-13 15:09 | 1:15 | S/O | Due to isolator maint | 0 | 0 | No interruption
Faridpur | Faridpur-Rajbari-Bheramara 132 kV Ckt-1 | 2021-07-16 06:19 | 2021-07-16 06:19 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Faridpur | Faridpur-Gopalganj 132 kV Ckt-2 | 2021-07-17 07:17 | 2021-07-17 07:17 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bheramara | Bheramara-Khulna(S) 230 kV Ckt-1 | 2021-07-19 09:35 | 2021-07-19 19:21 | 9:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Barishal(S) | Barishal(S)-Barishal(N) 132 kV Ckt-2 | 2021-07-20 22:42 | 2021-07-20 23:27 | 0:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Bheramara | Bheramara-GK 132 kV Ckt-1 | 2021-07-25 11:21 | 2021-07-25 12:57 | 1:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenaidah | Jhenaidah-Chuadanga 132 kV Ckt | 2021-07-28 08:12 | 2021-07-28 19:50 | 11:38 | S/O | Due to D/W work | 60 | 698 | Power interruption
Jhenaidah | Jhenaidah(O)-Jhenaidah(N) 132 kV Ckt |  | 2021-07-28 12:33 |  | S/O | After mainteneance | 0 | 0 | No interruption
Khulna(south) | Khulna(south)-Bheramara HVDC 230 kV Ckt-1 |  | 2021-07-28 19:20 |  | S/O | After mainteneance | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV Ckt | 2021-07-29 11:23 | 2021-07-29 11:46 | 0:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Goalpara | Goalpara-Khulna 225 MW P/P 132 kV Ckt | 2021-07-29 13:05 | 2021-07-29 16:10 | 3:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Bheramara | Bheramara-Bheramara 410 MW P/P 132 kV Ckt | 2021-07-29 15:30 | 2021-07-29 15:30 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bottail | Bottail-Jhenaidah(old) 132 kV Ckt-2 | 2021-07-30 08:04 | 2021-07-30 10:53 | 2:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Bottail | Bottail-Jhenaidah(old) 132 kV Ckt-1 | 2021-07-30 11:23 | 2021-07-30 12:53 | 1:30 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 32:47 |  | Unserved Energy: |  | 698
HVDC Grid Circle :
HVDC | HVDC-Khulna(S) 230 kV Ckt-1 | 2021-07-28 07:15 | 2021-07-28 07:15 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 1396
Bogura Grid Circle :
Rajlanka P.P | Rajlanka P.P.-Natore 132 kV Ckt | 2021-07-02 11:01 | 2021-07-02 16:10 | 5:09 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV Ckt-1 | 2021-07-09 06:35 | 2021-07-09 06:35 | 0:00 | S/O | Due to OPGW work. | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV Ckt-2 | 2021-07-10 06:24 | 2021-07-10 06:24 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV Ckt-1 | 2021-07-10 14:08 | 2021-07-10 16:55 | 2:47 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura | Bogura-Sherpur 132 kV Ckt-2 | 2021-07-12 09:20 | 2021-07-12 09:52 | 0:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Shahjadpur 132 kV Ckt | 2021-07-12 13:32 | 2021-07-12 15:15 | 1:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Polashbari | Polashbari-Mahasthangar 132 kV Ckt-1 | 2021-07-12 14:40 | 2021-07-12 15:50 | 1:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Sherpur 132 kV Ckt-1 | 2021-07-13 10:35 | 2021-07-13 11:37 | 1:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Natore 132 kV Ckt-2 |  | 2021-07-20 13:42 |  | S/O | After mainteneance | 0 | 0 | No interruption
Rangpur | Rangpur-Kurigram 132 kV Ckt | 2021-07-31 14:11 | 2021-07-31 15:36 | 1:25 | S/O | Due to new capacitor bank installation | 46 | 65.1667 | Power interruption
|  |  | Total : | 13:48 |  | Unserved Energy: |  | 65.1667
Others :
Nill
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 756:19 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:July 2021
| Area | Previous Month (June' 2021) |  |  |  | Current Month (July' 2021)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 37 | 15 | 115 | 167 | 34 | 25 | 95 | 154
2 | Dhaka (South) Grid Circle. | 10 | 1 | 23 | 34 | 2 | 2 | 3 | 7
3 | Chattogram Grid Circle. | 18 | 7 | 29 | 54 | 15 | 7 | 24 | 46
4 | Cumilla Grid Circle. | 29 | 2 | 26 | 57 | 16 | 4 | 19 | 39
5 | Khulna Grid Circle. | 23 | 7 | 34 | 64 | 15 | 10 | 36 | 61
6 | HVDC Grid Circle | 1 | 0 | 4 | 5 | 0 | 0 | 1 | 1
7 | Bogura Grid Circle. | 19 | 19 | 35 | 73 | 16 | 6 | 22 | 44
8 | Others | Total number of Total: 0; Total number of Total: 0
9 | Total | 137 | 51 | 266 | 454 | 98 | 54 | 200 | 352
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:July 2021
| Area | Previous Month (June 2021) |  |  |  | Current Month (July' 2021)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 210.42 | 945.83 | 1686.47 | 2842.72 | 513.84 | 181.98 | 566.43 | 1262.25
2 | Dhaka (South) Grid Circle. | 547.5 | 0 | 0 | 547.5 | 15.8333 | 0 | 0 | 15.8333
3 | Chattogram Grid Circle. | 258.3 | 57.84 | 1059.3 | 1375.44 | 82.58 | 70.76 | 139.7333 | 293.0733
4 | Cumilla Grid Circle. | 230.91 | 0 | 122.71 | 353.62 | 161.15 | 23 | 242.57 | 426.72
5 | Khulna Grid Circle. | 188.87 | 111.47 | 472.02 | 772.36 | 141.8 | 204.57 | 748.67 | 1095.04
6 | HVDC Grid Circle | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Bogura Grid Circle. | 152.49 | 362.38 | 200.3 | 715.17 | 46.53 | 113.07 | 788.07 | 947.67
8 | Others | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Total | 1588.49 | 1477.52 | 3540.8 | 6606.81 | 961.7333 | 593.38 | 2485.4733 | 4040.5867
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:July 2021
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 11 | 10 | 21 | 4 | 3 | 14 | 1111.93
2 | Dhaka (South) | 5031.6 | 1 | 0 | 1 | 1 | 0 | 0 | 15.8333
3 | Chattogram | 2042 | 6 | 3 | 9 | 2 | 4 | 3 | 293.08
4 | Khulna | 2434 | 13 | 2 | 15 | 4 | 4 | 7 | 397.04
5 | HVDC | 5954.3 | - | - | - | - | - | - | 0
6 | Bogura | 3145.6 | 5 | 7 | 12 | 2 | 2 | 8 | 882.5
7 | Cumilla | 2981 | 5 | 1 | 6 | 2 | 1 | 3 | 174
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 2874.3833
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.86%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.95%
4 | Khulna | 99.89%
5 | HVDC | 100% | [6 empty] | Executive Engineer
6 | Bogura | 99.93% | [6 empty] | Information Management Division
7 | Cumilla | 99.94% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:July 2021
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 2 | 1 | 3 | 1 | 1 | 1 | 150.32
2 | Dhaka (South) | 990.29 |  | - | - | - | - | - | - | -
3 | Chattogram | 917 | - | - | - | - | - | - | - | -
4 | Khulna | 1238.4 | - | - | 1 | 1 | - | - | 1 | 698 | -
5 | HVDC | 1325 | 501 | - | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - | - | 1 | - | - | - | 1 | 65.1667
7 | Cumilla | 1648.16 | - | 2 | 1 | 3 | 1 | 1 | 1 | 252.72
8 | Others | - |  | - | - | - | - | - | - | -
| Total | 10176.6215 | 501 | [6 empty] | 1166.2067
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.94%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.97%
4 | Khulna | 99.98%
5 | Bheramara (HVDC) | 100% | [7 empty] | Executive Engineer
6 | Bogura | 99.99% | [7 empty] | Information Management Division
7 | Cumilla | 99.98% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:July 2021
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2021-07-18 | 24 | - | 19 | 23hr57 min |  |  | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:July 2021
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Saver | 1 | 0:19 | 137 | 43.3833 | Due to 33 kV B/C fault
Bhulta | 1 | 0:24 | 60 | 24 | Due to Tripping of 132/33 kV Transformers- T2
Tongi | 1 | 0:14 | 35 | 8.1667 | Due to 33 kV feeder fault
Netrokona | 1 | 2:25 | 28 | 67.6667 | Due to red-hot maint
Kishoreganj | 3 | 3:29 | 80 | 278.6667 | Due to Tripping of 132/33 kV Transformer-T1,T2
|  | 0:34 | 20 | 11.3333 | Due to red-hot maint
|  | 2:45 | 30 | 82.5 | Due to S/D of 132/33 kV Transformer-T3
Maniknagar | 1 | 0:02 | 93 | 3.1 | Due to Tripping of 132/33 kV Transformer-T1,T2
Keraniganj | 1 | 1:48 | 5 | 9 | Due to red-hot maint
Nawabganj | 2 | 1:07 | 28 | 31.2667 | Due to red-hot maint
|  | 2:02 | 32 | 65.0667 | Due to S/D of 33 kV full bus
Valuka | 2 | 3:33 | 15 | 53.25 | Due to S/D of 132/33 kV T1 transformer
|  | 1:29 | 21 | 31.15 | Due to S/D 33 kV bus section-1
Sherpur | 3 | 1:34 | 12 | 18.8 | Due to S/D of 132/33 kV Transformer-T3
|  | 1:42 | 12 | 20.4 | Due to S/D 132/33 kv transformers T-1 with 33 kV bus
|  | 1:56 | 10 | 19.3333 | Due to red-hot maint
Jamalpur | 1 | 0:52 | 20 | 17.3333 | Due to S/D 132/33 kV transformer T4
Kabirpur | 3 | 2:39 | 22 | 58.3 | Due to S/D 132 kV reserve Bus
|  | 2:55 | 23 | 67.0833 | Due to S/D 132/33 kV transformer T1
|  | 0:57 | 25 | 23.75 | Due to newly installed CT ration correction
Tangail | 1 | 5:22 | 24 | 128.8 | Due to S/D 132/33 kV transformer T2
Hasnabad | 1 | 0:19 | 50 | 15.8333 | Due to Tripping of 132/33 kv transformers T-1, T-5
Kaliakoir | 3 | 1:10 | 103 | 120.1667 | Due to Tripping of Kaliakoir-Dhamrai 132 kV Ckt-1
|  | 0:04 | 96 | 6.4 | Due to Tripping of Kaliakoir-Dhamrai 132 kV Ckt-2
|  | 0:44 | 100 | 73.3333 | Due to tripping of 230/132 kV New transformer T
Dohazari | 2 | 1:05 | 20 | 21.6667 | Due to S/D 132/33 kV transformer T2 with 33 kV bus
|  | 0:56 | 22 | 20.5333 | Due to red-hot maint
Chowmuhoni | 1 | 0:42 | 40 | 28 | Due to operating PRD
Madunaghat | 1 | 1:14 | 18 | 22.2 | Due to red-hot maint
Bakulia | 1 | 0:58 | 29 | 28.0333 | Due to red-hot maint
Cox'sbazar | 1 | 0:33 | 40 | 22 | Due to tripping of 132/33 kV transformers T1 & T-2
Halishahar | 3 | 0:07 | 22 | 2.5667 | Due to S/D 33 kV Bus under 132/33 kV T-2 transformer
|  | 2:06 | 55 | 115.5 | Due to S/D of 132 kV Bus
|  | 0:23 | 85 | 32.5833 | Due to Tripping of 132/33 kv transformers T-1, T-2 & T-3
Sylhet | 2 | 0:15 | 33 | 8.25 | Due to Tripping of Sylhet-Chattak 132 kV Ckt-2
|  | 1:33 | 38 | 58.9 | Due to S/D of 132/33 kv transformers T2
Baroierhat | 1 | 9:11 | 20 | 183.6667 | Due to S/D of Baroierhat-PHP 132 kV Ckt-1
Feni | 1 | 1:32 | 15 | 23 | Due to red-hot maint
B.Baria | 1 | 0:21 | 150 | 52.5 | Due to Tripping of 132/33 kv transformers T2
Chandpur | 1 | 0:14 | 30 | 7 | Due to Tripping of 132/33 kV transformers T-1, T-2 and T-3
Shahjibazar | 2 | 1:05 | 20 | 21.6667 | Due to Tripping of 132/33 kV transformers T-4, T6
|  | 0:41 | 16 | 10.9333 | Due to Tripping of 132/33 kv transformers T3
Tripura | 1 | 0:38 | 96 | 60.8 | Due to Tripping of Tripura-Cumilla 132 kV both Ckts
Satkhira | 1 | 0:31 | 40 | 20.6667 | Due to Tripping of 132/33 kV Transformer-T1,T2
Barishal | 1 | 0:42 | 12 | 8.4 | Due to red-hot maint
Barishal(S) | 1 | 0:58 | 30 | 29 | Due to red-hot maint
Bottail | 1 | 1:10 | 40 | 46.6667 | Due to red-hot maint
Jashore | 1 | 0:07 | 40 | 4.6667 | Due to Tripping of 132/33 kV Transformer-T1 & 33 kV Bus
Mongla | 2 | 0:26 | 36 | 15.6 | Due to Tripping of 132/33 kV Transformer-T1,T2
|  | 2:33 | 16 | 40.8 | Due to Tripping of 132/33 kV Transformer-T1 and T2
Madaripur | 1 | 1:52 | 15 | 28 | Due to red-hot maint
Chuadanga | 1 | 1:00 | 35 | 35 | Due to R-phase clamp
Faridpur | 1 | 1:09 | 50 | 57.5 | Due to tear of 33 kV B-phase CT loop
Patuakhali | 1 | 0:17 | 20 | 5.6667 | Due to tear of 33 kV B-phase CT loop
Barishal(N) | 1 | 1:21 | 32 | 43.2 | Due to tear LT bus PT Y-phase burst
Barishal(S) | 1 | 0:21 | 32 | 11.2 | Due to 33 kV WZPDCL feeder fault
Barisal | 1 | 1:20 | 20 | 26.6667 | Due to S/D of 132/33 kV Transformer-T2
Bagethat | 1 | 1:30 | 16 | 24 | Due to S/D of 132/33 kV Transformer-T1
Jhenaidah | 1 | 11:38 | 60 | 698 | Due to S/D of Jhenaidah-Chuadanga 132 kV Ckt
Palashbari | 1 | 0:47 | 20 | 15.6667 | Due to red-hot maint
Bogura(Old) | 1 | 0:57 | 22 | 20.9 | Due to red-hot maint
Barapukuria | 2 | 2:33 | 30 | 76.5 | Due to red-hot maint
|  | 3:00 | 20 | 60 | Due to 33 kV bus maint.
Pabna | 1 | 0:23 | 94 | 36.0333 | Due to Tripping of 132/33 kV transformer T1 & T2
Rangpur | 1 | 1:25 | 46 | 65.1667 | Due to S/D of Rangpur-Kurigram 132 kV Ckt
Natore | 3 | 0:15 | 42 | 10.5 | Due to Tripping of 132/33 kV transformer T1 & T2
|  | 2:03 | 60 | 123 | Due to S/D of 132/33 kV Transformer-T3
|  | 3:34 | 40 | 142.6667 | Due to PBS maintenance work
Bogura | 1 | 1:42 | 32 | 54.4 | Due to 33 kV loop change
Panchagar | 1 | 1:09 | 40 | 46 | Due to S/D of 132 kV full bus
Rajshahi(O) | 1 | 2:23 | 100 | 238.3333 | Due to S/D of 132 kV Bus
Purbasadipur | 1 | 1:57 | 30 | 58.5 | Due to S/D of 33 kV Bus & 132/33 kV transformer T1
| Total Unserved energy : |  |  | 4040.5833 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: July'2021
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 132 | 15 | 2021-07-01 | 16:00
2 | Munsiganj | 108 | 12 | 2021-07-01 | 23:00
3 | Sonargaon | 81 | 7 | 2021-07-01 | 22:00
4 | Shyampur | 198 | 15 | 2021-07-01 | 0:00
5 | Bhulta | 202 | 11 | 2021-07-01 | 0:00
6 | Madanganj | 61 | 13 | 2021-07-01 | 12:00
7 | Shitalakhya | 136 | 13 | 2021-07-01 | 13:00
8 | Rahim steel | 27 | 7 | 2021-07-01 | 0:00
9 | Matuail | 66 | 4 | 2021-07-01 | 8:00
10 | Ghorasal | 81 | 5 | 2021-07-01 | 22:00
11 | Narsingdi | 186 | 15 | 2021-07-01 | 21:00
12 | Haripur (SBU) | 123 | 11 | 2021-07-01 | 13:00
13 | Sreenagar | 45 | 21 | 2021-07-01 | 19:30
14 | Ullon | 80 | 11 | 2021-07-01 | 0:00
15 | Hasnabad | 88 | 3 | 2021-07-01 | 19:00
16 | Magbazar | 92 | 19 | 2021-07-01 | 12:00
17 | Maniknagar | 76 | 18 | 2021-07-01 | 13:00
18 | Bangabhaban | 14 | 14 | 2021-07-01 | 14:00
19 | Narinda | 64 | 5 | 2021-07-01 | 22:00
20 | Dhanmondi | 199 | 15 | 2021-07-01 | 15:00
21 | Lalbag | 97 | 15 | 2021-07-01 | 13:00
22 | Madartek | 76 | 11 | 2021-07-01 | 23:00
23 | Dhaka University | 34 | 15 | 2021-07-01 | 12:00
24 | Aftabnagar | 11 | 15 | 2021-07-01 | 19:00
25 | Fatullah | 57 | 13 | 2021-07-01 | 0:00
26 | Nawabganj | 56 | 11 | 2021-07-01 | 22:00
27 | Mirpur | 140 | 15 | 2021-07-01 | 19:30
28 | Kalyanpur | 132 | 14 | 2021-07-01 | 19:00
29 | Gulshan | 106 | 15 | 2021-07-01 | 13:00
30 | Uttara | 102 | 11 | 2021-07-01 | 19:30
31 | Uttara(new) | 41 | 15 | 2021-07-01 | 14:00
32 | Kamrangirchar | 87 | 13 | 2021-07-01 | 13:00
33 | Savar | 173 | 6 | 2021-07-01 | 13:00
34 | Bhasantec | 133 | 18 | 2021-07-01 | 13:00
35 | Agargaon | 86 | 15 | 2021-07-01 | 13:00
36 | Satmosjid | 112 | 12 | 2021-07-01 | 24:00
37 | Tongi | 119 | 15 | 2021-07-01 | 11:00
38 | Kabirpur | 256 | 6 | 2021-07-01 | 15:00
39 | Basundhara | 251 | 15 | 2021-07-01 | 15:00
40 | Manikganj | 92 | 12 | 2021-07-01 | 19:30
41 | Joydevpur | 179 | 12 | 2021-07-01 | 19:30
42 | New Tongi | 125 | 6 | 2021-07-01 | 12:00
43 | Kodda | 348 | 5 | 2021-07-01 | 19:00
44 | Dhamrai | 116 | 15 | 2021-07-01 | 19:30
45 | Rajendrapur | 112 | 17 | 2021-07-01 | 19:30
46 | Valuka | 136 | 17 | 2021-07-01 | 15:00
47 | Tangail | 235 | 16 | 2021-07-01 | 21:00
48 | Mymensing | 222 | 14 | 2021-07-01 | 20:00
49 | Kishorganj | 158 | 21 | 2021-07-01 | 21:00
50 | Netrokona | 136 | 27 | 2021-07-01 | 20:00
51 | Jamalpur | 158 | 10 | 2021-07-01 | 21:00
52 | Sherpur | 138 | 26 | 2021-07-01 | 22:00
53 | Srimongal | 64 | 26 | 2021-07-01 | 22:00
Page: 2/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: July'2021
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
54 | Shahjibazar | 118 | 9 | 2021-07-01 | 23:00
56 | Fenchuganj | 50 | 12 | 2021-07-01 | 19:00
57 | Kulawara | 50 | 27 | 2021-07-01 | 19:00
58 | Sylhet | 136 | 15 | 2021-07-01 | 19:00
59 | Chatak | 34 | 12 | 2021-07-01 | 21:00
60 | Sunamganj | 55 | 12 | 2021-07-01 | 21:00
61 | Bianibazar | 77 | 22 | 2021-07-01 | 19:30
62 | Cumilla (S) | 172 | 10 | 2021-07-01 | 23:00
63 | Cumilla(N) | 157 | 15 | 2021-07-01 | 20:00
64 | Chandpur | 93 | 21 | 2021-07-01 | 23:00
65 | Feni | 132 | 22 | 2021-07-01 | 21:00
66 | Chowmuhani | 233 | 21 | 2021-07-01 | 21:00
67 | Ashuganj | 57 | 6 | 2021-07-01 | 21:00
68 | Daudkandi | 164 | 14 | 2021-07-01 | 23:00
69 | B.Baria | 180 | 15 | 2021-07-01 | 21:00
70 | Ramganj | 100 | 21 | 2021-07-01 | 19:00
71 | Chaddagram | 63 | 26 | 2021-07-01 | 23:00
72 | PHP | 9 | 26 | 2021-07-01 | 9:00
73 | Kochua | 72 | 18 | 2021-07-01 | 22:00
74 | Madanhat | 69 | 21 | 2021-07-01 | 19:00
75 | Hathazari | 97 | 15 | 2021-07-01 | 20:00
76 | Khulshi | 220 | 15 | 2021-07-01 | 10:00
77 | Halishahar | 123 | 15 | 2021-07-01 | 8:00
78 | Baraulia | 154 | 16 | 2021-07-01 | 1:00
79 | Sikalbaha | 39 | 12 | 2021-07-01 | 18:00
80 | Dohazari | 98 | 11 | 2021-07-01 | 19:00
81 | Cox'sbazar | 105 | 18 | 2021-07-01 | 20:00
82 | Chandraghona | 34 | 21 | 2021-07-01 | 19:30
83 | Kaptai | 4.5 | 9 | 2021-07-01 | 19:00
84 | A. Khaer Stl. | 10 | 1 | 2021-07-01 | 12:00
85 | Bakulia | 111 | 12 | 2021-07-01 | 15:00
86 | Julda | 24 | 7 | 2021-07-01 | 12:00
87 | TK chemical | 35 | 21 | 2021-07-01 | 21:00
88 | Modern Steel | 0 | 1 | 2021-07-01 | #N/A
89 | Shahmirpur | 33 | 6 | 2021-07-01 | 0:00
90 | Khagrachhari | 30 | 12 | 2021-07-01 | 4:00
91 | Matarbari | 42.5 | 21 | 2021-07-01 | 21:00
92 | Baroiar Hat | 60 | 21 | 2021-07-01 | 21:00
93 | Rangamati | 18 | 24 | 2021-07-01 | 14:00
94 | Abul Khair 230 | 167 | 16 | 2021-07-01 | 10:00
95 | BSRM | 165 | 18 | 2021-07-01 | 19:30
96 | GPH Ispat | 96 | 8 | 2021-07-01 | 13:00
97 | Goalpara | 39 | 13 | 2021-07-01 | 13:00
98 | Central s/s | 120 | 12 | 2021-07-01 | 22:00
99 | Noapara | 59 | 17 | 2021-07-01 | 20:00
100 | Jashore | 127 | 15 | 2021-07-01 | 21:00
101 | Benapol | 74 | 18 | 2021-07-01 | 19:30
101 | Jhenidah | 120 | 16 | 2021-07-01 | 19:30
102 | Bottail | 144 | 16 | 2021-07-01 | 20:00
Page: 3/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: July'2021
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
103 | G.K Project | 61 | 18 | 2021-07-01 | 22:00
104 | Faridpur | 154 | 15 | 2021-07-01 | 23:00
105 | Madaripur | 117 | 21 | 2021-07-01 | 23:00
106 | Sariatpur | 82 | 21 | 2021-07-01 | 22:00
107 | Gopalganj | 102 | 17 | 2021-07-01 | 22:00
108 | Bagerhat | 109 | 17 | 2021-07-01 | 21:00
109 | Mongla | 42 | 4 | 2021-07-01 | 14:00
110 | Satkhira | 114 | 18 | 2021-07-01 | 21:00
111 | Gallamari | 56 | 9 | 2021-07-01 | 22:00
112 | Magura | 60 | 25 | 2021-07-01 | 20:00
113 | Norail | 95 | 9 | 2021-07-01 | 22:00
114 | Chuadanga | 101 | 28 | 2021-07-01 | 21:00
115 | Borguna | 47 | 9 | 2021-07-01 | 21:00
116 | Barsal(N) | 100 | 24 | 2021-07-01 | 21:00
117 | Barsal(S) | 118 | 19 | 2021-07-01 | 23:00
118 | Patuakhali | 129 | 21 | 2021-07-01 | 22:00
119 | Bhandaria | 60 | 19 | 2021-07-01 | 22:00
120 | Borhan Uddin | 49 | 19 | 2021-07-01 | 22:00
121 | Ishurdi | 72 | 12 | 2021-07-01 | 1:00
122 | Ruppur Paromanobik | 4 | 6 | 2021-07-01 | 17:00
123 | Natore | 140 | 18 | 2021-07-01 | 21:00
124 | Bogura | 171 | 13 | 2021-07-01 | 1:00
125 | Naogaon | 123 | 9 | 2021-07-01 | 23:00
126 | Rajshahi | 163 | 17 | 2021-07-01 | 21:00
127 | Rajshahi New | 20 | 14 | 2021-07-01 | 1:00
128 | C.Nawabganj | 78 | 15 | 2021-07-01 | 20:00
129 | Amnura | 60 | 16 | 2021-07-01 | 20:00
130 | Pabna | 110 | 5 | 2021-07-01 | 21:00
131 | Shahjadpur | 105 | 14 | 2021-07-01 | 21:00
132 | Serajganj | 114 | 14 | 2021-07-01 | 21:00
133 | Niyamatpur | 88 | 16 | 2021-07-01 | 20:00
134 | Joypurhat | 66 | 17 | 2021-07-01 | 21:00
135 | Sherpur(Bogura) | 62 | 16 | 2021-07-01 | 19:30
136 | Mohastangar | 78 | 16 | 2021-07-01 | 21:00
137 | Bangura | 36 | 16 | 2021-07-01 | 21:00
138 | Rangpur | 142 | 21 | 2021-07-01 | 19:30
139 | Lalmonirhat | 48 | 9 | 2021-07-01 | 19:30
140 | Saidpur | 110 | 15 | 2021-07-01 | 20:00
141 | Purbasadipur | 115 | 13 | 2021-07-01 | 23:00
142 | Thakurgaon | 92 | 25 | 2021-07-01 | 20:00
143 | Palshbari | 126 | 26 | 2021-07-01 | 20:00
144 | Barapukuria | 58 | 12 | 2021-07-01 | 21:00
145 | Panchugar | 59 | 24 | 2021-07-01 | 21:00
146 | Joldhaka | 68 | 21 | 2021-07-01 | 22:00
147 | Kurigram | 64 | 20 | 2021-07-01 | 20:00
148 | Mitha Pukur | 52 | 12 | 2021-07-01 | 2:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:July 2021
Area | MW | Date | Hour | Remarks
Dhaka | 5023 | 18.07.2021 | 7:00
Chattogram | 1423 | 14.07.2021 | 23:00
Khulna | 1636 | 17.07.2021 | 22:00
Rajshahi | 1417 | 16.07.2021 | 21:00
Cumilla | 1280 | 22.07.2021 | 23:00
Mymensingh | 1086 | 16.07.2021 | 21:00
Sylhet | 539 | 26.07.2021 | 22:00
Barisal | 421 | 19.07.2021 | 23:00
Rangpur | 838 | 25.07.2021 | 22:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: July'2021
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 407 | 30 | 2021-07-01 | 1:00 | 394 | 3 | 2021-07-01 | 15:00
2 | Bheramara | 400 | 407 | 3 | 2021-07-01 | 2:00 | 391 | 10 | 2021-07-01 | 23:00
3 | Ashuganj(N) | 400 | 393 | 15 | 2021-07-01 | 6:00 | 375 | 21 | 2021-07-01 | 16:00
4 | Payra | 400 | 418 | 20 | 2021-07-01 | 7:00 | 397 | 10 | 2021-07-01 | 1:00
5 | Kaliakoir | 400 | 399 | 24 | 2021-07-01 | 7:00 | 377 | 4 | 2021-07-01 | 12:00
6 | Bhulta | 400 | 389 | 9 | 2021-07-01 | 14:00 | 367 | 1 | 2021-07-01 | 14:15
7 | Gopalganj | 400 | 416 | 29 | 2021-07-01 | 15:00 | 380 | 10 | 2021-07-01 | 21:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 244 | 25 | 2021-07-01 | 20:00 | 227 | 2 | 2021-07-01 | 10:00
2 | Ishurdi | 230 | 251 | 15 | 2021-07-01 | 14:00 | 224 | 5 | 2021-07-01 | 20:00
3 | Ashuganj | 230 | 240 | 6 | 2021-07-01 | 19:00 | 223 | 6 | 2021-07-01 | 8:00
4 | Serajganj | 230 | 233 | 15 | 2021-07-01 | 17:00 | 222 | 13 | 2021-07-01 | 22:00
5 | Baghabari | 230 | 234 | 2 | 2021-07-01 | 3:00 | 224 | 14 | 2021-07-01 | 19:00
6 | Barapukuria | 230 | 237 | 2 | 2021-07-01 | 6:00 | 221 | 29 | 2021-07-01 | 21:00
7 | Bogura | 230 | 227 | 23 | 2021-07-01 | 19:00 | 210 | 14 | 2021-07-01 | 21:00
8 | Rajshahi | 230 | 237 | 4 | 2021-07-01 | 18:00 | 218 | 31 | 2021-07-01 | 12:00
9 | Khulna South | 230 | 240 | 27 | 2021-07-01 | 9:00 | 188 | 19 | 2021-07-01 | 13:00
10 | Rampura | 230 | 230 | 9 | 2021-07-01 | 19:30 | 221 | 1 | 2021-07-01 | 15:00
11 | Haripur | 230 | 232 | 30 | 2021-07-01 | 8:00 | 219 | 1 | 2021-07-01 | 10:00
12 | Hasnabad | 230 | 231 | 9 | 2021-07-01 | 10:00 | 218 | 1 | 2021-07-01 | 9:00
13 | Shyampur | 230 | 229 | 4 | 2021-07-01 | 21:00 | 220 | 1 | 2021-07-01 | 10:00
14 | Aminbazar | 230 | 230 | 27 | 2021-07-01 | 1:00 | 216 | 1 | 2021-07-01 | 2:00
15 | Tongi | 230 | 230 | 19 | 2021-07-01 | 18:00 | 127 | 17 | 2021-07-01 | 13:00
16 | Comilla (N) | 230 | 233 | 4 | 2021-07-01 | 16:00 | 219 | 1 | 2021-07-01 | 11:00
17 | Hathazari | 230 | 228 | 30 | 2021-07-01 | 2:00 | 212 | 1 | 2021-07-01 | 9:00
18 | Megnaghat | 230 | 237 | 30 | 2021-07-01 | 7:00 | 223 | 3 | 2021-07-01 | 11:00
19 | Fenchuganj | 230 | 242 | 2 | 2021-07-01 | 12:00 | 232 | 3 | 2021-07-01 | 3:00
20 | Siddhirganj | 230 | 237 | 2 | 2021-07-01 | 18:30 | 222 | 1 | 2021-07-01 | 9:00 |  | 7345
21 | Maniknagar | 230 | 232 | 29 | 2021-07-01 | 8:00 | 220 | 1 | 2021-07-01 | 11:00
22 | Old Airport | 230 | 230 | 29 | 2021-07-01 | 11:00 | 215 | 3 | 2021-07-01 | 15:00
23 | Barisal | 230 | 251 | 23 | 2021-07-01 | 2:00 | 215 | 5 | 2021-07-01 | 17:00
24 | Bhola 225 MW | 230 | 251 | 23 | 2021-07-01 | 3:00 | 215 | 5 | 2021-07-01 | 17:00
25 | AKSML | 230 | 230 | 30 | 2021-07-01 | 2:00 | 213 | 1 | 2021-07-01 | 9:00
26 | BSRM | 230 | 230 | 27 | 2021-07-01 | 18:30 | 214 | 1 | 2021-07-01 | 9:00
27 | Bibiyana | 230 | 241 | 30 | 2021-07-01 | 9:00 | 232 | 3 | 2021-07-01 | 13:00
28 | Bhulta | 230 | 236 | 29 | 2021-07-01 | 18:30 | 221 | 1 | 2021-07-01 | 15:00
29 | Ashuganj (S) | 230 | 232 | 0 | 2021-07-01 | 12:00 | 228 | 1 | 2021-07-01 | 11:00
30 | Kaliakoir | 230 | 230 | 29 | 2021-07-01 | 23:00 | 212 | 13 | 2021-07-01 | 8:00
31 | GPH | 230 | 229 | 10 | 2021-07-01 | 4:00 | 213 | 1 | 2021-07-01 | 9:00
132 kV Substation
1 | Siddhirganj | 132 | 136 | 29 | 2021-07-01 | 0.33333 | 127 | 1 | 2021-07-01 | 0.375
2 | Munsiganj | 132 | 137 | 19 | 2021-07-01 | 0.79167 | 126 | 1 | 2021-07-01 | 0.5
3 | Sonargaon | 132 | 137 | 3 | 2021-07-01 | 0.54167 | 126 | 1 | 2021-07-01 | 0.45833
4 | Shyampur | 132 | 139 | 29 | 2021-07-01 | 0.33333 | 129 | 1 | 2021-07-01 | 0.41667
5 | Bhulta | 132 | 132 | 15 | 2021-07-01 | 0.41667 | 120 | 1 | 2021-07-01 | 0.41667
6 | Madanganj | 132 | 136 | 21 | 2021-07-01 | 0.8125 | 125 | 1 | 2021-07-01 | 0.41667
7 | Shitalakhya | 132 | 144 | 11 | 2021-07-01 | 0.8125 | 127 | 12 | 2021-07-01 | 0.041667
8 | Rahim Steal | 132 | 136 | 29 | 2021-07-01 | 0.29167 | 127 | 1 | 2021-07-01 | 0.5
9 | Matuail | 132 | 136 | 29 | 2021-07-01 | 0.33333 | 127 | 1 | 2021-07-01 | 0.375
10 | Ghorasal | 132 | 140 | 29 | 2021-07-01 | 0.33333 | 134 | 1 | 2021-07-01 | 0.625
11 | Narsinghdi | 132 | 136 | 2 | 2021-07-01 | 0.41667 | 123 | 21 | 2021-07-01 | 0.875
12 | Haripur (SBU) | 132 | 136 | 19 | 2021-07-01 | 0.79167 | 126 | 4 | 2021-07-01 | 0.5
13 | Sreenagar | 132 | - |  | - | - | - | - | - | -
14 | Ullon | 132 | 136 | 1 | 2021-07-01 | 0.79167 | 128 | 18 | 2021-07-01 | 0.41667
15 | Hasnabad | 132 | 140 | 9 | 2021-07-01 | 0.79167 | 130 | 1 | 2021-07-01 | 0.41667
16 | Magbazar | 132 | 138 | 2 | 2021-07-01 | 0.75 | 123 | 10 | 2021-07-01 | 0.45833
17 | Maniknagar | 132 | 138 | 9 | 2021-07-01 | 0.8125 | 130 | 14 | 2021-07-01 | 0.66667
18 | Bangabhaban | 132 | 138 | 9 | 2021-07-01 | 0.8125 | 130 | 14 | 2021-07-01 | 0.66667
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: July'2021
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
19 | Narinda | 132 | 138 | 9 | 2021-07-01 | 0.8125 | 130 | 14 | 2021-07-01 | 0.66667
20 | Dhanmondi | 132 | 136 | 25 | 2021-07-01 | 0.29167 | 127 | 1 | 2021-07-01 | 0.45833
21 | Lalbag | 132 | 141 | 9 | 2021-07-01 | 0.8125 | 129 | 3 | 2021-07-01 | 0.45833
22 | Madartek | 132 | 137 | 2 | 2021-07-01 | 0.77083 | 128 | 18 | 2021-07-01 | 0.45833
23 | Dhaka University | 132 | - | - | - | - | - | - | - | -
24 | Aftabnagar | 132 | 137 | 2 | 2021-07-01 | 0.20833 | 128 | 18 | 2021-07-01 | 0.45833
25 | Fatullah | 132 | 139 | 29 | 2021-07-01 | 0.33333 | 129 | 1 | 2021-07-01 | 0.45833
26 | Nawabganj | 133 | 132 | 9 | 2021-07-01 | 0.8125 | 122 | 3 | 2021-07-01 | 0.625
27 | Mirpur | 132 | 139 | 29 | 2021-07-01 | 0.95833 | 125 | 1 | 2021-07-01 | 0.95833
28 | Kalyanpur | 132 | 140 | 29 | 2021-07-01 | 0 | 128 | 1 | 2021-07-01 | 0.625
29 | Gulshan | 132 | 137 | 2 | 2021-07-01 | 0.79167 | 127 | 18 | 2021-07-01 | 0.5
30 | Uttara | 132 | 138 | 20 | 2021-07-01 | 0.041667 | 127 | 1 | 2021-07-01 | 0.5
31 | Uttara(New) | 132 | 139 | 29 | 2021-07-01 | 0.54167 | 126 | 1 | 2021-07-01 | 0.5
32 | Kamrangirchar | 132 | 141 | 9 | 2021-07-01 | 0.8125 | 129 | 3 | 2021-07-01 | 0.66667
33 | Savar | 132 | 138 | 14 | 2021-07-01 | 0.041667 | 125 | 3 | 2021-07-01 | 0.45833
34 | Bhasantec | 132 | 139 | 16 | 2021-07-01 | 0.041667 | 128 | 3 | 2021-07-01 | 0.625
35 | Agargaon | 132 | 141 | 19 | 2021-07-01 | 0.041667 | 129 | 3 | 2021-07-01 | 0.625
36 | Satmosjid | 132 | 138 | 20 | 2021-07-01 | 0.33333 | 129 | 3 | 2021-07-01 | 0.625
37 | Tongi | 132 | 142 | 29 | 2021-07-01 | 23:00 | 129 | 1 | 2021-07-01 | 0.54167
38 | Kabirpur | 132 | 142 | 29 | 2021-07-01 | 8:00 | 127 | 4 | 2021-07-01 | 0.5
39 | Basundhara | 132 | 139 | 16 | 2021-07-01 | 18:30 | 127 | 3 | 2021-07-01 | 0.5
40 | Manikganj | 132 | 142 | 22 | 2021-07-01 | 18:00 | 126 | 12 | 2021-07-01 | 9:00
41 | Joydevpur | 132 | 141 | 7 | 2021-07-01 | 0 | 127 | 4 | 2021-07-01 | 0.375
42 | New Tongi | 132 | 140 | 9 | 2021-07-01 | 0.83333 | 131 | 18 | 2021-07-01 | 10:00
43 | Kodda | 132 | 138 | 16 | 2021-07-01 | 1:00 | 124 | 12 | 2021-07-01 | 10:00
44 | Dhamrai | 132 | 135 | 2 | 2021-07-01 | 6.00 | 126 | 4 | 2021-07-01 | 0.625
45 | Rajendrapur | 132 | 139 | 22 | 2021-07-01 | 22:00 | 119 | 12 | 2021-07-01 | 15:00
46 | Valuka | 132 | 130 | 28 | 2021-07-01 | 0.77083 | 108 | 10 | 2021-07-01 | 0.95833
47 | Tangail | 132 | 137 | 29 | 2021-07-01 | 0.33333 | 120 | 12 | 2021-07-01 | 0.875
48 | Mymensing | 132 | 132 | 17 | 2021-07-01 | 0.33333 | 113 | 4 | 2021-07-01 | 0.91667
49 | Kishorganj | 132 | 133 | 1 | 2021-07-01 | 0.91667 | 112 | 6 | 2021-07-01 | 0.91667
50 | Netrokona | 132 | 130 | 17 | 2021-07-01 | 0.29167 | 107 | 21 | 2021-07-01 | 0.83333
51 | Jamalpur | 132 | 138 | 19 | 2021-07-01 | 0.29167 | 117 | 24 | 2021-07-01 | 0.54167
52 | Sherpur | 132 | 137 | 5 | 2021-07-01 | 0.79167 | 113 | 29 | 2021-07-01 | 0.75
53 | Srimongal | 132 | 140 | 2 | 2021-07-01 | 0.375 | 130 | 21 | 2021-07-01 | 0.79167
54 | Shahjibazar | 132 | 138 | 15 | 2021-07-01 | 0.29167 | 127 | 21 | 2021-07-01 | 0.79167
55 | Fenchuganj | 132 | 139 | 1 | 2021-07-01 | 0.8125 | 132 | 23 | 2021-07-01 | 0.91667
56 | Khulawara | 132 | 137 | 1 | 2021-07-01 | 0.77083 | 131 | 26 | 2021-07-01 | 0.91667
57 | Sylhet | 132 | 136 | 1 | 2021-07-01 | 0.41667 | 123 | 21 | 2021-07-01 | 0.33333
58 | Chattak | 132 | 137 | 13 | 2021-07-01 | 0.041667 | 126 | 26 | 2021-07-01 | 0.95833
59 | Sunamganj | 132 | 137 | 13 | 2021-07-01 | 0.041667 | 118 | 9 | 2021-07-01 | 0.5
60 | Biani Bazar | 132 | 136 | 2 | 2021-07-01 | 0.29167 | 125 | 26 | 2021-07-01 | 0.91667
61 | Comilla(South) | 132 | 132 | 22 | 2021-07-01 | 0.041667 | 121 | 15 | 2021-07-01 | 0.95833
62 | Comilla (North) | 132 | 139 | 1 | 2021-07-01 | 0.77083 | 123 | 4 | 2021-07-01 | 0.041667
63 | Chandpur | 132 | 140 | 29 | 2021-07-01 | 0.95833 | 123 | 3 | 2021-07-01 | 0.95833
64 | Feni | 132 | 139 | 1 | 2021-07-01 | 0.77083 | 123 | 1 | 2021-07-01 | 0.45833
65 | Chowmuhani | 132 | 137 | 1 | 2021-07-01 | 0.8125 | 120 | 21 | 2021-07-01 | 0.91667
66 | Ashuganj | 132 | 140 | 1 | 2021-07-01 | 0.083333 | 132 | 18 | 2021-07-01 | 0.95833
67 | Daudkandi | 132 | 138 | 14 | 2021-07-01 | 0.8125 | 124 | 4 | 2021-07-01 | 1899-12-31
68 | Brahminbaria | 132 | 136 | 2 | 2021-07-01 | 0.25 | 125 | 21 | 2021-07-01 | 0.79167
69 | Ramganj | 132 | 139 | 7 | 2021-07-01 | 0.45833 | 116 | 2 | 2021-07-01 | 0.16667
70 | Chaddagram | 132 | 138 | 8 | 2021-07-01 | 0.77083 | 125 | 1 | 2021-07-01 | 0.58333
71 | PHP | 132 | 137 | 8 | 2021-07-01 | 0.77083 | 0 | 4 | 2021-07-01 | 0.33333
72 | Kochua | 132 | 138 | 16 | 2021-07-01 | 0.79167 | 123 | 3 | 2021-07-01 | 0
73 | Madanhat | 132 | 136 | 30 | 2021-07-01 | 0.79167 | 127 | 1 | 2021-07-01 | 0.41667
74 | Hathazari | 132 | 135 | 19 | 2021-07-01 | 0.83333 | 126 | 1 | 2021-07-01 | 0.375
75 | Khulshi | 132 | 133 | 19 | 2021-07-01 | 0.83333 | 124 | 1 | 2021-07-01 | 0.375
76 | Halishahar | 132 | 135 | 19 | 2021-07-01 | 0.8125 | 123 | 24 | 2021-07-01 | 0.54167
77 | Baraulia | 132 | 139 | 24 | 2021-07-01 | 0.25 | 124 | 1 | 2021-07-01 | 0.45833
78 | Sikalbaha | 132 | 136 | 19 | 2021-07-01 | 0.8125 | 124 | 24 | 2021-07-01 | 0.54167
79 | Dohazari | 132 | 132 | 1 | 2021-07-01 | 0.25 | 122 | 20 | 2021-07-01 | 0.70833
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: July'2021
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
80 | Cox'sbazar | 132 | 127 | 27 | 2021-07-01 | 0.29167 | 107 | 15 | 2021-07-01 | 0.66667
81 | Chandraghona | 132 | 135 | 19 | 2021-07-01 | 0.8125 | 126 | 1 | 2021-07-01 | 0.58333
82 | Kaptai | 132 | 135 | 28 | 2021-07-01 | 0.79167 | 127 | 4 | 2021-07-01 | 0.45833
83 | A. Khaer Stl. | 132 | 133 | 27 | 2021-07-01 | 0.875 | 125 | 1 | 2021-07-01 | 0.45833
84 | Bakulia | 132 | 136 | 30 | 2021-07-01 | 0.8125 | 124 | 23 | 2021-07-01 | 0.54167
85 | Julda | 132 | 136 | 27 | 2021-07-01 | 0.77083 | 125 | 1 | 2021-07-01 | 0.54167
86 | TK Chemical | 132 | 136 | 20 | 2021-07-01 | 0.8125 | 125 | 23 | 2021-07-01 | 0.54167
87 | Modern Steel | - | - | - | - | - | - | - | - | -
88 | Shahmirpur | 132 | 136 | 29 | 2021-07-01 | 0.91667 | 123 | 24 | 2021-07-01 | 0.54167
89 | Khagrachhari | 132 | 133 | 19 | 2021-07-01 | 0.8125 | 119 | 25 | 2021-07-01 | 0.58333
90 | Matarbari | 132 | 130 | 2 | 2021-07-01 | 0.75 | 102 | 1 | 2021-07-01 | 0.95833
91 | Baroiar Hat | 132 | 137 | 8 | 2021-07-01 | 0.77083 | 123 | 21 | 2021-07-01 | 0.91667
92 | Rangamati | 132 | 134 | 19 | 2021-07-01 | 0.8125 | 125 | 1 | 2021-07-01 | 0.58333
93 | Goalpara | 132 | 140 | 1 | 2021-07-01 | 0.625 | 114 | 19 | 2021-07-01 | 0.54167
94 | Khulna Central | 132 | 141 | 29 | 2021-07-01 | 0.77083 | 113 | 19 | 2021-07-01 | 0.54167
95 | Noapara | 132 | 140 | 29 | 2021-07-01 | 0.77083 | 110 | 19 | 2021-07-01 | 0.54167
96 | Jessore | 132 | 139 | 29 | 2021-07-01 | 0.70833 | 108 | 19 | 2021-07-01 | 0.54167
97 | Benapol | 132 | 139 | 29 | 2021-07-01 | 0.77083 | 109 | 15 | 2021-07-01 | 0.8125
98 | Jhenida | 132 | 135 | 29 | 2021-07-01 | 0.41667 | 105 | 5 | 2021-07-01 | 0.875
99 | Bottail | 132 | 136 | 2 | 2021-07-01 | 0.66667 | 119 | 11 | 2021-07-01 | 0.91667
100 | G.K Project | 132 | 140 | 7 | 2021-07-01 | 0.66667 | 124 | 2 | 2021-07-01 | 0.95833
101 | Faridpur | 132 | 140 | 2 | 2021-07-01 | 0.45833 | 120 | 23 | 2021-07-01 | 0.041667
102 | Madaripur | 132 | 145 | 29 | 2021-07-01 | 0.41667 | 128 | 5 | 2021-07-01 | 0.91667
103 | Sariatpur | 132 | 144 | 29 | 2021-07-01 | 0.33333 | 126 | 5 | 2021-07-01 | 0.91667
104 | Gopalganj | 132 | 148 | 29 | 2021-07-01 | 0.41667 | 128 | 5 | 2021-07-01 | 0.875
105 | Bagerhat | 132 | 140 | 29 | 2021-07-01 | 0.66667 | 110 | 19 | 2021-07-01 | 0.54167
106 | Mongla | 132 | 139 | 29 | 2021-07-01 | 0.25 | 110 | 19 | 2021-07-01 | 0.54167
107 | Satkhira | 132 | 140 | 8 | 2021-07-01 | 0.77083 | 110 | 19 | 2021-07-01 | 0.54167
108 | Gallamari | 132 | 141 | 2 | 2021-07-01 | 0.25 | 122 | 4 | 2021-07-01 | 0.5
109 | Magura | 132 | 136 | 29 | 2021-07-01 | 0.70833 | 102 | 5 | 2021-07-01 | 0.83333
110 | Norail | 132 | 134 | 2 | 2021-07-01 | 0.625 | 100 | 21 | 2021-07-01 | 0.875
111 | Chuadanga | 132 | 137 | 29 | 2021-07-01 | 0.625 | 93 | 5 | 2021-07-01 | 0.875
112 | Borguna | 132 | 144 | 29 | 2021-07-01 | 0.375 | 124 | 5 | 2021-07-01 | 0.875
113 | Barisal(N) | 132 | 145 | 29 | 2021-07-01 | 0.70833 | 118 | 29 | 2021-07-01 | 0.95833
114 | Barisal(S) | 132 | 143 | 29 | 2021-07-01 | 0.33333 | 126 | 5 | 2021-07-01 | 0.875
115 | Patuakhali | 132 | 143 | 29 | 2021-07-01 | 0.29167 | 122 | 5 | 2021-07-01 | 0.875
116 | Bhandaria | 132 | 148 | 1 | 2021-07-01 | 0.70833 | 121 | 5 | 2021-07-01 | 0.91667
117 | Ishurdi | 132 | 138 | 8 | 2021-07-01 | 0.77083 | 128 | 29 | 2021-07-01 | 0.041667
118 | Ruppur paromanobik | 132 | 137 | 2 | 2021-07-01 | 0.375 | 127 | 29 | 2021-07-01 | 0.041667
118 | Natore | 132 | 136 | 8 | 2021-07-01 | 0.77083 | 125 | 27 | 2021-07-01 | 0.54167
119 | Bogra | 132 | 136 | 23 | 2021-07-01 | 0.79167 | 120 | 19 | 2021-07-01 | 0.875
120 | Noagaon | 132 | 131 | 2 | 2021-07-01 | 0.20833 | 114 | 16 | 2021-07-01 | 0.875
121 | Rajshahi | 132 | 134 | 6 | 2021-07-01 | 0.75 | 123 | 25 | 2021-07-01 | 0.58333
122 | Rajshahi New | 132 | 135 | 3 | 2021-07-01 | 0.75 | 122 | 24 | 2021-07-01 | 0.083333
123 | C.Nawabganj | 132 | 136 | 6 | 2021-07-01 | 0.77083 | 120 | 25 | 2021-07-01 | 0.58333
124 | Amnura | 132 | 136 | 6 | 2021-07-01 | 0.77083 | 118 | 22 | 2021-07-01 | 0.083333
125 | Pabna | 132 | 136 | 2 | 2021-07-01 | 0.25 | 126 | 31 | 2021-07-01 | 0.83333
126 | Shahjadpur | 132 | 140 | 1 | 2021-07-01 | 0.041667 | 130 | 21 | 2021-07-01 | 0.91667
127 | Serajganj | 132 | 135 | 9 | 2021-07-01 | 0.77083 | 125 | 9 | 2021-07-01 | 0.875
128 | Niyamatpur | 132 | 130 | 6 | 2021-07-01 | 0.75 | 107 | 16 | 2021-07-01 | 0.875
129 | Joypurhat | 132 | 132 | 2 | 2021-07-01 | 0.45833 | 111 | 16 | 2021-07-01 | 0.875
130 | Sherpur(Bogura) | 132 | 136 | 23 | 2021-07-01 | 0.8125 | 122 | 14 | 2021-07-01 | 0.875
132 | Mohastangor | 132 | 137 | 4 | 2021-07-01 | 0.45833 | 120 | 13 | 2021-07-01 | 0.875
133 | Bangura | 132 | 138 | 2 | 2021-07-01 | 0.45833 | 129 | 16 | 2021-07-01 | 0.875
134 | Rangpur | 132 | 134 | 23 | 2021-07-01 | 0.041667 | 108 | 28 | 2021-07-01 | 0.58333
135 | Lalmonirhat | 132 | 131 | 2 | 2021-07-01 | 0.41667 | 111 | 28 | 2021-07-01 | 0.58333
136 | Saidpur | 132 | 133 | 2 | 2021-07-01 | 0.45833 | 110 | 10 | 2021-07-01 | 0.875
137 | Purbasadipur | 132 | 131 | 2 | 2021-07-01 | 0.25 | 104 | 29 | 2021-07-01 | 0.875
138 | Thakurgaon | 132 | 132 | 2 | 2021-07-01 | 0.29167 | 102 | 12 | 2021-07-01 | 0.8125
139 | Palashbari | 132 | 131 | 2 | 2021-07-01 | 0.41667 | 115 | 9 | 2021-07-01 | 0.875
140 | Barapukuria | 132 | 137 | 2 | 2021-07-01 | 0.25 | 121 | 29 | 2021-07-01 | 0.875
141 | Panchagar | 132 | 132 | 21 | 2021-07-01 | 0.375 | 100 | 9 | 2021-07-01 | 0.875
142 | Joldhaka | 132 | 131 | 2 | 2021-07-01 | 0.20833 | 100 | 29 | 2021-07-01 | 0.875
143 | Kurigram | 132 | 131 | 31 | 2021-07-01 | 0.70833 | 105 | 28 | 2021-07-01 | 0.58333
144 | Mithapukur | 132 | 133 | 3 | 2021-07-01 | 0.79167 | 114 | 28 | 2021-07-01 | 0.58333
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
Page: 1/1 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:July 2021
Name of the | Auto transformer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 0 | 0 | S/D
Hasnabad | TR2 | 225 | 142 | 420 | 16/07/21 | 9:00
| TR3 | 225 | 140 | 420
| TR1 | 225 | 150 | 460
Tongi | TR2 | 225 | 150 | 460 | 13/07/21 | 11:00
| TR3 | 225 | 150 | 460
Haripur | TR1 | 225 | 82 | 220
| TR2 | 225 | 82 | 220 | 13/07/21 | 4:00
| TR3 | 225 | 82 | 220
| TR1 | 225 | 179 | 480
Rampura | TR2 | 225 | 179 | 480 | 15/07/2021 | 15:00
| TR3 | 225 | 179 | 480
Keraniganj | ATR1 | 300 | 51 | 144 |  | 23:00
| ATR2 | 300 | 51 | 144 | 21/07/2021
| ATR3 | 300 | 51 | 144
| TR1 | 225 | 134 | 390
Aminbazar | TR2 | 225 | 134 | 390 | 2021-03-07 | 15:00
| TR3 | 225 | 142 | 406
Agargaon | TR1 | 300 | 155 | 438 | 18/07/21 | 13:00
| TR2 | 300 | 155 | 438
Maniknagar | TR1 | 300 | 123 | 350 | 15/07/21 | 16:00
| TR2 | 300 | 123 | 350
Cumilla (N) | TR1 | 225 | 178 | 507 | 2021-01-07 | 11:00
| TR2 | 225 | 174 | 493
Fenchuganj | AT2 | 300 | 233 | 615 | 2021-09-06 | 21:00
| MT1 | 150 | 92 | 250 | 25/07/21
Hathazari | MT2 | 150 | 92 | 250 |  | 18:00
| MT3 | 150 | 92 | 250
| MT4 | 150 | 92 | 250
| TR1 | 225 | 118 | 310
Ishurdi | TR2 | 225 | 118 | 310 | 29/07/21 | 23:00
| TR3 | 225 | 118 | 310
Khulna(S) | TR1 | 225 | 124 | 340
| TR2 | 225 | 124 | 340 | 18/07/21 | 19:30
| TR3 | 300 | 158 | 440
Bogura | TR1 | 225 | 121 | 366
| TR2 | 225 | 121 | 366 | 17/07/21 | 7:00
| TR3 | 225 | 166 | 482
Baghabari | TR1 | 300 | 170 | 460 | 14/07/21 | 21:00
| TR2 | 225 | 128 | 350
Rajshahi | ATR-01 | 300 | 114 | 306 | 27/07/21 | 14:00
| ATR-02 | 300 | 114 | 306
Barapukuria | TR1 | 225 | 162 | 800 |  |  | Due to unavailability of 230 kV side meters
| TR2 | 225 | 171 | 850 | 25/07/21 | 21:00 | 132 kV current is being provided
| TR6 | 300 | 222 | 1115
Bheramara | Transformer-1 | 225 | 132 | 346 | 29/07/21 | 23:00
| Transformer-2 | 225 | 132 | 346
Shyampur | ATR-01 | 300 | 103 | 338 | 17/07/21 | 10:00
| ATR-02 | 300 | 103 | 338
Kaliakoir | TR1 | 300 | 120 | 340 | 15:07/21 | 21:00
QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:July 2021
Name of the | Transformer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps (400 kV side) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 276 | 420 | 19/07/21 | 9:15
| TR2(400/230 kV) | 520 | 279.5 | 424
| TR1(400/132 kV) | 325 | 278.3 | 469 | 2021-08-07 | 19:30
| TR2(400/132 kV) | 325 | 277.3 | 466
Bibiyana | ICT1(400/230 kV) | 520 | 190 | 275 | 24/07/21 | 21:13
| ICT2(400/230kV) | 520 | 185 | 277
Bhulta | ATR1(400/230 kV) | 520 | 184 | 346 | 13/07/21 | 17:23
| ATR2(400/230kV) | 520 | 184 | 346
Ashuganj(N) | GSUT1 | 567 | 371 | 609 | 17/07/21 | 7:59
Gopalganj | ATR1(400/138 kV) | 325 | 299 | 458 | 2021-09-07 | 22:00
| ATR2(400/138kV) | 325 | 299 | 458
Payra | GSUT1 | 270 | 202 | 906 | 2021-09-07 | 22:27
| GSUT2 | 270 | 201 | 887
| GSUT3 | 270 | 202 | 889
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.
270

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:July 2021 | [6 empty] | (For Evening Peak) | [7 empty] | Month:July 2021 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2021-07-01 | 10097 | 10097 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-01 | 8476 | 8476 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-02 | 9942 | 9942 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-02 | 7379 | 7379 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-03 | 11515 | 11515 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-03 | 9422 | 9422 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-04 | 11704 | 11704 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-04 | 9453 | 9453 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-05 | 12477 | 12477 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-05 | 10231 | 10231 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-06 | 12433 | 12433 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-06 | 10488 | 10488 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-07 | 11698 | 11698 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-07 | 10165 | 10165 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-08 | 12358 | 12358 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-08 | 10115 | 10115 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-09 | 12113 | 12113 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-09 | 9162 | 9162 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-10 | 12898 | 12898 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-10 | 10100 | 10100 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-11 | 12900 | 12900 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-11 | 10745 | 10745 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-12 | 13022 | 13022 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-12 | 11176 | 11176 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-13 | 12838 | 12838 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-13 | 10278 | 10278 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-14 | 13077 | 13077 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-14 | 10846 | 10846 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-15 | 13525 | 13525 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-15 | 11549 | 11549 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-16 | 12830 | 12830 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-16 | 10643 | 10643 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-17 | 13056 | 13056 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-17 | 10670 | 10670 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-18 | 12953 | 12953 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-18 | 11210 | 11210 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-19 | 11940 | 11940 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-19 | 10232 | 10232 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-20 | 10960 | 10960 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-20 | 8011 | 8011 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-21 | 11298 | 11298 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-21 | 7208 | 7208 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-22 | 10908 | 10908 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-22 | 8576 | 8576 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-23 | 10303 | 10303 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-23 | 7507 | 7507 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-24 | 10620 | 10620 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-24 | 7609 | 7609 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-25 | 11285 | 11285 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-25 | 8451 | 8451 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-26 | 11354 | 11354 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-26 | 9002 | 9002 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-27 | 10551 | 10551 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-27 | 8473 | 8473 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-28 | 10400 | 10400 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-28 | 8068 | 8068 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-29 | 9309 | 9309 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-29 | 6782 | 6782 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-30 | 10204 | 10204 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-30 | 7206 | 7206 | - | - | - | - | - | - | - | - | - | - | - | -
2021-07-31 | 10777 | 10777 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-07-31 | 7841 | 7841 | - | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:July 2021
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 13525 | 2021-07-15 | 21:00
2 | Maximum Day Peak Genaration | MW | 11549 | 2021-07-15 | 12:00
3 | Maximum Evening Peak Demand | MW | 13525 | 2021-07-15 | 21:00
4 | Minimum Generation | MW | 6682 | 2021-07-29 | 1:00
5 | Average of the daily evening peak Genaration | MW | 11656.2903
6 | Average of the daily day peak Genaration | MW | 9260.4516
7 | Maximum load shed | MW | 0 | - | -
8 | Minimum load shed | MW | 0 | - | -
9 | Total nos. of load shed days | Day | 0
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 0
11 | Total Generation | MkWh | 7472.212
12 | Total Generation by BPDB | MkWh | 1852.5058 | % of total Gen. | 24.79%
13 | Total Generation by IPP | MkWh | 2024.123 | '' | 27.09%
14 | A) Total Generation by Generation Companies | MkWh | 2379.325 | '' | 31.84%
| B) Total Generation by REB | MkWh | 129.0256 | " | 1.727%
| C) Total Generation by RENTAL | MkWh | 427.9978 | " | 5.728%
| D) Total Imported from India (BIPTC) | MkWh | 576.0289 | " | 7.709%
| E) Total Imported from Tripura, India (A.C) | MkWh | 83.2061 | " | 1.114%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4815.0058 | % of total Gen. | 64.44%
| B) Oil | MkWh | 1478.1855 | '' | 19.78%
| C) Hydro | MkWh | 61.0975 | '' | 0.8177%
| D) Solar | MkWh | 16.6657 | '' | 0.223%
| E) Coal | MkWh | 442.0225 | '' | 5.916%
| F) BIPTC (Import from India) | MkWh | 576.0289 | '' | 7.709%
| G) A.C (Import from Tripura, India) | MkWh | 83.2061 | '' | 1.114%
16 | Maximun of the daily total Generation . | MkWh | 287.5106 | 2021-07-15
17 | Monthly Load factor | % | 74.2573
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 21629.8605
| A) Gas | M.Taka | 4967.5383
| B) Liquid fuel | M.Taka | 11118.425
| C) Coal | M.Taka | 2086.511
| D) BIPTC (Import from India) | M.Taka | 2851.5998
| E) Tripura(Import from India) | M.Taka | 605.7864
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 915.9376 | 2021-07-08
| A) Gas | M.Taka | 171.2928 | 2021-07-20
| B) Liquid fuel | M.Taka | 681.8483 | 2021-07-08
| C) Coal | M.Taka | 82.9334 | 2021-07-15
| D) BIPTC (Import from India) | M.Taka | 101.8034 | 2021-07-13
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 3.1648
| B) Excluding Hydro & Solar | Taka/kWhR | 3.1978
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 88.83 | 31/7/2021 | 06:00
b) | Actual | FT (MSL) | 85.45 | 31/7/2021 | 06:00
22 | Peak Genaration of Jun 2021 | MW | 13014 | 2021-06-02 | 21:00
23 | Peak Demand of Jun 2021 | MW | 13014 | 24/06/20 | 22:00
24 | Maximum peak Generation recorded upto 31/07/2021 | MW | 13792 | 2021-06-02 | 20:00
25 | Maximum peak Demand recorded upto 31/07/2021 | MW | 14097 | 27/04/21 | 19:00
26 | Maximum load shed recorded upto 31/07/2021 | MW | 1459 | 04/05/2010 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.